## Power Cable Schedule
|  |  | 미배정Drum 사용(10/6) |  |  |  | DONE(10/27) | DONE |  | POWER CABLE SCHEDULE
[8 empty] | DONE 재포설 | [9 empty] | 480 | 5510 | -5030 | [8 empty] | DOC NO: CCP-W-B000-EL-353-0001 | 8 |  |  |  | 0 |  |  | 0 |  |  |  | 0
[10 empty] | PROJECT NAME: TURKISTAN TCCGT | [17 empty] | [REVISION: C01A] | ISSUE DATE: 14.10.2026
| CABLE NO. |  | Drum 재배정(9/30) SE의견에 때른 재포설필요 | 기존 DRUM NO. | DRUM NO. | LOAD NUMBER | 기존 Cable NO. | PULLING |  | S/N | CABLE |  |  | DRUM NO. | Rated Power | VOLTAGE | Power Source | LENGTH | PROCESS /SYSTEM | FROM |  |  |  | TO |  |  |  | CABLE ROUTE | REMARK | Cable Gland |  |  | Cable | Cable Lug(From) |  |  | Cable Lug(To) |  |  |  | MV KIT
[11 empty] | NUMBER | TYPE | SPEC |  | (kW) | (V) |  | (M) |  | KKS NO. | SWGR GROUP DESCRIPTION | SWGR LOCATION | T/B NUMBER | KKS NO. | LOAD DESCRIPTION | LOAD LOCATION | T/B NUMBER |  |  | Q;ty | Part No. | Range | O.D.(mm) | Q;ty | Part No. | Hole | Q;ty | Part No. | Hole |  | Q;ty | Part No.
- | - | - |  |  |  | - |  |  |  | - | - | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - |  | -
B1-SWG-64601 | -P20 | 01 |  | PE-L1-1C185-01 | PE-L1-1C185-01 | GTG-U1-001 |  | DONE | 1 | 1 | B1-SWG-64601-P2001 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-01 | 292 | 400 | N | 110 | GTG | B1-SWG-64601 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1 | 11BFA00GS001-E01 | GTG #11 LV SWGR INCMR FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1 | B164-016CT0098 → B164-016CT0099 → B164-996CT0022 → M0504 → D0531-L24 → M0510 → D0502-L24 → M0326 → B111-996BT0021 → B111-016BT0004 → B111-016BT0005 → B111-016BT0006 → B111-016BT0025 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 23
B1-SWG-64601 | -P20 | 02 |  | PE-L1-1C185-01 | PE-L1-1C185-01 |  |  | DONE | 1 | 2 | B1-SWG-64601-P2002 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-01 | 292 | 400 | N | 110 | GTG | B1-SWG-64601 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L2 | 11BFA00GS001-E01 | GTG #11 LV SWGR INCMR FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #11 | L2 | B164-016CT0098 → B164-016CT0099 → B164-996CT0022 → M0504 → D0531-L24 → M0510 → D0502-L24 → M0326 → B111-996BT0021 → B111-016BT0004 → B111-016BT0005 → B111-016BT0006 → B111-016BT0025 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 23
B1-SWG-64601 | -P20 | 03 |  | PE-L1-1C185-01 | PE-L1-1C185-01 |  |  | DONE | 1 | 3 | B1-SWG-64601-P2003 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-01 | 292 | 400 | N | 110 | GTG | B1-SWG-64601 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L3 | 11BFA00GS001-E01 | GTG #11 LV SWGR INCMR FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #11 | L3 | B164-016CT0098 → B164-016CT0099 → B164-996CT0022 → M0504 → D0531-L24 → M0510 → D0502-L24 → M0326 → B111-996BT0021 → B111-016BT0004 → B111-016BT0005 → B111-016BT0006 → B111-016BT0025 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 23
B1-SWG-64601 | -P20 | 04 |  | PE-L1-1C185-01 | PE-L1-1C185-01 |  |  | DONE | 1 | 4 | B1-SWG-64601-P2004 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-01 | 292 | 400 | N | 110 | GTG | B1-SWG-64601 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1 | 11BFA00GS001-E01 | GTG #11 LV SWGR INCMR FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1 | B164-016CT0098 → B164-016CT0099 → B164-996CT0022 → M0504 → D0531-L24 → M0510 → D0502-L24 → M0326 → B111-996BT0021 → B111-016BT0004 → B111-016BT0005 → B111-016BT0006 → B111-016BT0025 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 23
B1-SWG-64601 | -P20 | 05 |  | PE-L1-1C185-01 | PE-L1-1C185-01 |  |  | DONE | 1 | 5 | B1-SWG-64601-P2005 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-01 | 292 | 400 | N | 110 | GTG | B1-SWG-64601 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L2 | 11BFA00GS001-E01 | GTG #11 LV SWGR INCMR FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #11 | L2 | B164-016CT0098 → B164-016CT0099 → B164-996CT0022 → M0504 → D0531-L24 → M0510 → D0502-L24 → M0326 → B111-996BT0021 → B111-016BT0004 → B111-016BT0005 → B111-016BT0006 → B111-016BT0025 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 23
B1-SWG-64601 | -P20 | 06 |  | PE-L1-1C185-01 | PE-L1-1C185-01 |  |  | DONE | 1 | 6 | B1-SWG-64601-P2006 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-01 | 292 | 400 | N | 110 | GTG | B1-SWG-64601 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L3 | 11BFA00GS001-E01 | GTG #11 LV SWGR INCMR FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #11 | L3 | B164-016CT0098 → B164-016CT0099 → B164-996CT0022 → M0504 → D0531-L24 → M0510 → D0502-L24 → M0326 → B111-996BT0021 → B111-016BT0004 → B111-016BT0005 → B111-016BT0006 → B111-016BT0025 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 23
B1-SWG-64601 | -P20 | 07 |  | PE-L1-1C185-01 | PE-L1-1C185-01 |  |  | DONE | 1 | 7 | B1-SWG-64601-P2007 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-01 | 292 | 400 | N | 110 | GTG | B1-SWG-64601 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | N | 11BFA00GS001-E01 | GTG #11 LV SWGR INCMR FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #11 | N | B164-016CT0098 → B164-016CT0099 → B164-996CT0022 → M0504 → D0531-L24 → M0510 → D0502-L24 → M0326 → B111-996BT0021 → B111-016BT0004 → B111-016BT0005 → B111-016BT0006 → B111-016BT0025 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 23
B1-ESWG-64601 | -P20 | 01 |  | PE-L1-1C185-01 | PE-L1-1C185-01 | GTG-U1-002 |  |  | 1 | 8 | B1-ESWG-64601-P2001 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-01 | 146 | 400 | E | 130 | GTG | B1-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1 | 11BMA00GS001-E01 | GTG #11 STBY LV-SWGR INCM FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1 | B164-016FT0096 → B164-016FT0095 → B164-016FT0094 → B164-016FT0093 → B164-016FT0092 → B164-996FT0022 → M0504 → D0531-L32 → M0510 → D0502-L32 → M0326 → D0329-L23 → M0327 → B111-996AT0023 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 23
B1-ESWG-64601 | -P20 | 02 |  | PE-L1-1C185-01 | PE-L1-1C185-01 |  |  | DONE | 1 | 9 | B1-ESWG-64601-P2002 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-01 | 146 | 400 | E | 130 | GTG | B1-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L2 | 11BMA00GS001-E01 | GTG #11 STBY LV-SWGR INCM FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #11 | L2 | B164-016FT0096 → B164-016FT0095 → B164-016FT0094 → B164-016FT0093 → B164-016FT0092 → B164-996FT0022 → M0504 → D0531-L32 → M0510 → D0502-L32 → M0326 → D0329-L23 → M0327 → B111-996AT0023 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 23
B1-ESWG-64601 | -P20 | 03 |  | PE-L1-1C185-01 | PE-L1-1C185-01 |  |  | DONE | 1 | 10 | B1-ESWG-64601-P2003 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-01 | 146 | 400 | E | 130 | GTG | B1-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L3 | 11BMA00GS001-E01 | GTG #11 STBY LV-SWGR INCM FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #11 | L3 | B164-016FT0096 → B164-016FT0095 → B164-016FT0094 → B164-016FT0093 → B164-016FT0092 → B164-996FT0022 → M0504 → D0531-L32 → M0510 → D0502-L32 → M0326 → D0329-L23 → M0327 → B111-996AT0023 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 23
B1-ESWG-64601 | -P20 | 04 |  | PE-L1-1C95-01 | PE-L1-1C95-01 |  |  | DONE | 1 | 11 | B1-ESWG-64601-P2004 | 0.6/1kV CU/XLPE/LSZH | 1C x 95sqmm | PE-L1-1C95-01 | 146 | 400 | E | 130 | GTG | B1-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | N | 11BMA00GS001-E01 | GTG #11 STBY LV-SWGR INCM FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #11 | N | B164-016FT0096 → B164-016FT0095 → B164-016FT0094 → B164-016FT0093 → B164-016FT0092 → B164-996FT0022 → M0504 → D0531-L32 → M0510 → D0502-L32 → M0326 → D0329-L23 → M0327 → B111-996AT0023 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 17.5
B1-SWG-64301 | -P10 | 01 |  | PE-M1-3C120-01 | PE-M1-3C120-01 | GTG-U1-003 |  | DONE | 1 | 12 | B1-SWG-64301-P1001 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-01 | 2900 | 10000 | N | 110 | GTG | B1-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | 11MBJ01GT001-E01 | GTG #11 HV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #11 | U1,V1,W1 | B064-013DT0056 → B064-013DT0260 → B064-013DT0261 → B064-013DT0262 → B064-993DT0024 → M0504 → D0531-M17 → M0510 → D0502-M17 → M0326 → B161-003BC0002 → END |  |  |  |  | 55 | [7 empty] | 2 | EPKT-17C3XIH2-G56
B1-SWG-64301 | -P10 | 02 |  | PE-M1-3C120-01 | PE-M1-3C120-01 | GTG-U1-004 |  | DONE | 1 | 13 | B1-SWG-64301-P1002 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-01 | 1230 | 10000 | N | 120 | GTG | B1-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | 11MKC01GT001-E01 | GTG #11 HV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #11 | U1,V1,W1 | B064-013DT0056 → B064-013DT0260 → B064-013DT0261 → B064-013DT0262 → B064-993DT0024 → M0504 → D0531-M15 → M0510 → D0502-M15 → M0326 → D0320-M11 → M0325 → B161-003BC0006 → END |  |  |  |  | 55 |  |  | 1 |  |  |  |  | 2 | EPKT-17C3XIH2-G56
B1-SWG-64301 | -P10 | 03 |  | PE-M1-3C120-01 | PE-M1-3C120-01 | GTG-U1-005 |  | DONE | 1 | 14 | B1-SWG-64301-P1003 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-01 | 500 | 10000 | N | 130 | GTG | B1-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | 11MBN12AP001-M01 | GTG #11 INJECTION PUMP FUEL OIL | 1.1_MAIN BUILDING COMPLEX / GT #11 | U1,V1,W1 | B064-013DT0056 → B064-013DT0260 → B064-013DT0261 → B064-013DT0262 → B064-993DT0024 → M0504 → D0531-M16 → M0510 → D0502-M16 → M0326 → B161-003BC0001 → END |  |  |  |  | 55 | [7 empty] | 2 | EPKT-17C3XIH2-G56
B1-SWG-64301 | -P20 | 01 |  | PE-L1-3C4-01 | PE-L1-3C4-01 | GTG-U1-007 |  |  | 1 | 15 | B1-SWG-64301-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-01 | 0.315 | 230 | N | 140 | GTG | B1-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | L1, N, PE | 11MBN12AP001-E01 | GTG #11 INJECTION PUMP FUEL OIL SPACE HEATER | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, N, PE | B164-016AT0056 → B164-016AT0055 → B164-016AT0215 → B164-016AT0216 → B164-016AT0091 → B164-996AT0022 → M0504 → D0531-L27 → M0510 → D0502-L27 → M0326 → B161-007BC0007 → END |  |  |  |  | 13
B1-UPSP-73701 | -P20 | 01 | 재배정 | PE-L1-3C4-01 | PE-L1-3C4-13 | GTG-U1-009 |  |  | 1 | 16 | B1-UPSP-73701-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-13 | 1.19 | 230 | U | 30 | GTG | B1-UPSP-73701 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ADMIN. - BLOCK#1 - A | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | 11CRY01GW021-E01 | GTG #11 SERVER/LAN CABINET | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / SERVER ROOM | L1, N, PE | B073-016AT0013 → B073-016AT0015 → B073-016AT0011 → END |  |  |  |  | 13
B1-UPSP-64701 | -P20 | 01 |  | PE-L1-3C4-01 | PE-L1-3C4-01 | GTG-U1-011 |  |  | 1 | 17 | B1-UPSP-64701-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-01 | 0.7 | 230 | U | 120 | GTG | B1-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | 11CRU01GE001-E01 | GTG #11 POWER SUPPLY OPERATOR TERMINAL | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, N, PE | B164-006GT0201 → B164-006GT0001 → B164-006GT0002 → B164-006GT0003 → B064-006AC0008 → M0501 → D0517-L21 → M0510 → D0502-L27 → M0326 → B111-996AT0021 → B111-016AT0004 → B111-016AT0005 → B111-016AT0006 → B111-016AT0025 → END |  |  |  |  | 13
B1-SWG-64604 | -P20 | 01 |  | PE-L1-1C240-07 | PE-L1-1C240-07 | GTG-U2-001 |  | DONE | 1 | 18 | B1-SWG-64604-P2001 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-07 | 292 | 400 | N | 210 | GTG | B1-SWG-64604 | 400V SWITCHGEAR FOR GT/HRSG #2 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1 | 12BFA00GS001-E01 | GTG #12 LV SWGR INCMR FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1 | B164-016DT0110 → B164-016DT0109 → B164-016DT0108 → B164-016DT0107 → B164-996DT0024 → M0504 → D0531-L33 → M0510 → D0502-L33 → M0326 → D0320-L35 → M0325 → D0319-L22 → M0324 → D0327-L22 → M0321 → D0318-L21 → M0322 → D0328-L23 → M0323 → B111-996DT0022 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B1-SWG-64604 | -P20 | 02 |  | PE-L1-1C240-07 | PE-L1-1C240-07 |  |  | DONE | 1 | 19 | B1-SWG-64604-P2002 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-07 | 292 | 400 | N | 210 | GTG | B1-SWG-64604 | 400V SWITCHGEAR FOR GT/HRSG #2 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L2 | 12BFA00GS001-E01 | GTG #12 LV SWGR INCMR FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #12 | L2 | B164-016DT0110 → B164-016DT0109 → B164-016DT0108 → B164-016DT0107 → B164-996DT0024 → M0504 → D0531-L33 → M0510 → D0502-L33 → M0326 → D0320-L35 → M0325 → D0319-L22 → M0324 → D0327-L22 → M0321 → D0318-L21 → M0322 → D0328-L23 → M0323 → B111-996DT0022 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B1-SWG-64604 | -P20 | 03 |  | PE-L1-1C240-07 | PE-L1-1C240-07 |  |  | DONE | 1 | 20 | B1-SWG-64604-P2003 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-07 | 292 | 400 | N | 210 | GTG | B1-SWG-64604 | 400V SWITCHGEAR FOR GT/HRSG #2 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L3 | 12BFA00GS001-E01 | GTG #12 LV SWGR INCMR FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #12 | L3 | B164-016DT0110 → B164-016DT0109 → B164-016DT0108 → B164-016DT0107 → B164-996DT0024 → M0504 → D0531-L33 → M0510 → D0502-L33 → M0326 → D0320-L35 → M0325 → D0319-L22 → M0324 → D0327-L22 → M0321 → D0318-L21 → M0322 → D0328-L23 → M0323 → B111-996DT0022 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B1-SWG-64604 | -P20 | 04 |  | PE-L1-1C240-07 | PE-L1-1C240-07 |  |  | DONE | 1 | 21 | B1-SWG-64604-P2004 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-07 | 292 | 400 | N | 210 | GTG | B1-SWG-64604 | 400V SWITCHGEAR FOR GT/HRSG #2 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1 | 12BFA00GS001-E01 | GTG #12 LV SWGR INCMR FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1 | B164-016DT0110 → B164-016DT0109 → B164-016DT0108 → B164-016DT0107 → B164-996DT0024 → M0504 → D0531-L33 → M0510 → D0502-L33 → M0326 → D0320-L35 → M0325 → D0319-L22 → M0324 → D0327-L22 → M0321 → D0318-L21 → M0322 → D0328-L23 → M0323 → B111-996DT0022 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B1-SWG-64604 | -P20 | 05 |  | PE-L1-1C240-07 | PE-L1-1C240-07 |  |  | DONE | 1 | 22 | B1-SWG-64604-P2005 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-07 | 292 | 400 | N | 210 | GTG | B1-SWG-64604 | 400V SWITCHGEAR FOR GT/HRSG #2 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L2 | 12BFA00GS001-E01 | GTG #12 LV SWGR INCMR FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #12 | L2 | B164-016DT0110 → B164-016DT0109 → B164-016DT0108 → B164-016DT0107 → B164-996DT0024 → M0504 → D0531-L33 → M0510 → D0502-L33 → M0326 → D0320-L35 → M0325 → D0319-L22 → M0324 → D0327-L22 → M0321 → D0318-L21 → M0322 → D0328-L23 → M0323 → B111-996DT0022 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B1-SWG-64604 | -P20 | 06 |  | PE-L1-1C240-08 | PE-L1-1C240-08 |  |  | DONE | 1 | 23 | B1-SWG-64604-P2006 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-08 | 292 | 400 | N | 210 | GTG | B1-SWG-64604 | 400V SWITCHGEAR FOR GT/HRSG #2 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L3 | 12BFA00GS001-E01 | GTG #12 LV SWGR INCMR FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #12 | L3 | B164-016DT0110 → B164-016DT0109 → B164-016DT0108 → B164-016DT0107 → B164-996DT0024 → M0504 → D0531-L33 → M0510 → D0502-L33 → M0326 → D0320-L35 → M0325 → D0319-L22 → M0324 → D0327-L22 → M0321 → D0318-L21 → M0322 → D0328-L23 → M0323 → B111-996DT0022 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B1-SWG-64604 | -P20 | 07 |  | PE-L1-1C240-08 | PE-L1-1C240-08 |  |  | DONE | 1 | 24 | B1-SWG-64604-P2007 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-08 | 292 | 400 | N | 210 | GTG | B1-SWG-64604 | 400V SWITCHGEAR FOR GT/HRSG #2 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | N | 12BFA00GS001-E01 | GTG #12 LV SWGR INCMR FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #12 | N | B164-016DT0110 → B164-016DT0109 → B164-016DT0108 → B164-016DT0107 → B164-996DT0024 → M0504 → D0531-L33 → M0510 → D0502-L33 → M0326 → D0320-L35 → M0325 → D0319-L22 → M0324 → D0327-L22 → M0321 → D0318-L21 → M0322 → D0328-L23 → M0323 → B111-996DT0022 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B1-ESWG-64602 | -P20 | 01 |  | PE-L1-1C240-09 | PE-L1-1C240-09 | GTG-U2-002 |  | DONE | 1 | 25 | B1-ESWG-64602-P2001 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-09 | 146 | 400 | E | 220 | GTG | B1-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1 | 12BMA00GS001-E01 | GTG #12 STBY LV-SWGR INCM FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1 | B164-016AT0121 → B164-016AT0120 → B164-016AT0119 → B164-016AT0118 → B164-016AT0117 → B164-016AT0116 → B164-996AT0023 → M0504 → D0531-L34 → M0510 → D0502-L34 → M0326 → D0320-L27 → M0325 → D0319-L31 → M0324 → D0327-L31 → M0321 → D0318-L23 → M0322 → B111-996CT0021 → B111-016CT0004 → B111-016CT0003 → B111-016CT0002 → B111-016CT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B1-ESWG-64602 | -P20 | 02 |  | PE-L1-1C240-09 | PE-L1-1C240-09 |  |  | DONE | 1 | 26 | B1-ESWG-64602-P2002 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-09 | 146 | 400 | E | 220 | GTG | B1-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L2 | 12BMA00GS001-E01 | GTG #12 STBY LV-SWGR INCM FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #12 | L2 | B164-016AT0121 → B164-016AT0120 → B164-016AT0119 → B164-016AT0118 → B164-016AT0117 → B164-016AT0116 → B164-996AT0023 → M0504 → D0531-L34 → M0510 → D0502-L34 → M0326 → D0320-L27 → M0325 → D0319-L31 → M0324 → D0327-L31 → M0321 → D0318-L23 → M0322 → B111-996CT0021 → B111-016CT0004 → B111-016CT0003 → B111-016CT0002 → B111-016CT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B1-ESWG-64602 | -P20 | 03 |  | PE-L1-1C240-09 | PE-L1-1C240-09 |  |  | DONE | 1 | 27 | B1-ESWG-64602-P2003 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-09 | 146 | 400 | E | 220 | GTG | B1-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L3 | 12BMA00GS001-E01 | GTG #12 STBY LV-SWGR INCM FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #12 | L3 | B164-016AT0121 → B164-016AT0120 → B164-016AT0119 → B164-016AT0118 → B164-016AT0117 → B164-016AT0116 → B164-996AT0023 → M0504 → D0531-L34 → M0510 → D0502-L34 → M0326 → D0320-L27 → M0325 → D0319-L31 → M0324 → D0327-L31 → M0321 → D0318-L23 → M0322 → B111-996CT0021 → B111-016CT0004 → B111-016CT0003 → B111-016CT0002 → B111-016CT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B1-ESWG-64602 | -P20 | 04 |  | PE-L1-1C185-01 | PE-L1-1C185-01 |  |  | DONE | 1 | 28 | B1-ESWG-64602-P2004 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-01 | 146 | 400 | E | 220 | GTG | B1-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | N | 12BMA00GS001-E01 | GTG #12 STBY LV-SWGR INCM FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #12 | N | B164-016AT0121 → B164-016AT0120 → B164-016AT0119 → B164-016AT0118 → B164-016AT0117 → B164-016AT0116 → B164-996AT0023 → M0504 → D0531-L34 → M0510 → D0502-L34 → M0326 → D0320-L27 → M0325 → D0319-L31 → M0324 → D0327-L31 → M0321 → D0318-L23 → M0322 → B111-996CT0021 → B111-016CT0004 → B111-016CT0003 → B111-016CT0002 → B111-016CT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 23
B1-SWG-64302 | -P10 | 01 |  | PE-M1-3C120-02 | PE-M1-3C120-02 | GTG-U2-003 |  | DONE | 1 | 29 | B1-SWG-64302-P1001 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-02 | 2900 | 10000 | N | 190 | GTG | B1-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | 12MBJ01GT001-E01 | GTG #12 HV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #12 | U1,V1,W1 | B164-013AT0083 → B164-013AT0262 → B164-993AT0024 → M0504 → D0531-M13 → M0510 → D0502-M13 → M0326 → D0320-M14 → M0325 → D0319-M14 → M0324 → D0327-M14 → M0321 → D0318-M14 → M0322 → B161-003DC0002 → END |  |  |  |  | 55 | [7 empty] | 2 | EPKT-17C3XIH2-G56
B1-SWG-64302 | -P10 | 02 |  | PE-M1-3C120-02 | PE-M1-3C120-02 | GTG-U2-004 |  | DONE | 1 | 30 | B1-SWG-64302-P1002 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-02 | 1230 | 10000 | N | 170 | GTG | B1-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | 12MKC01GT001-E01 | GTG #12 HV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #12 | U1,V1,W1 | B164-013AT0083 → B164-013AT0262 → B164-993AT0024 → M0504 → D0531-M21 → M0510 → D0502-M21 → M0326 → D0320-M15 → M0325 → D0319-M13 → M0324 → D0327-M13 → M0321 → B161-003DC0006 → END |  |  |  |  | 55 | [7 empty] | 2 | EPKT-17C3XIH2-G56
B1-SWG-64302 | -P10 | 03 |  | PE-M1-3C120-03 | PE-M1-3C120-03 | GTG-U2-005 |  | DONE | 1 | 31 | B1-SWG-64302-P1003 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-03 | 500 | 10000 | N | 200 | GTG | B1-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | 12MBN12AP001-M01 | GTG #12 INJECTION PUMP FUEL OIL | 1.1_MAIN BUILDING COMPLEX / GT #12 | U1,V1,W1 | B164-013AT0083 → B164-013AT0262 → B164-993AT0024 → M0504 → D0531-M14 → M0510 → D0502-M14 → M0326 → D0320-M13 → M0325 → D0319-M15 → M0324 → D0327-M15 → M0321 → D0318-M15 → M0322 → B161-003DC0001 → END |  |  |  |  | 55 | [7 empty] | 2 | EPKT-17C3XIH2-G56
B1-SWG-64302 | -P20 | 01 |  | PE-L1-3C4-01 | PE-L1-3C4-01 | GTG-U2-007 |  | DONE | 1 | 32 | B1-SWG-64302-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-01 | 0.315 | 230 | N | 230 | GTG | B1-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | L1, N, PE | 12MBN12AP001-E01 | GTG #12 INJECTION PUMP FUEL OIL SPACE HEATER | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, N, PE | B064-016AT0075 → B064-016AT0074 → B064-016AT0073 → B064-016AT0215 → B064-016AT0214 → B064-016AT0213 → B064-016AT0032 → B064-996AT0120 → M0504 → D0531-L26 → M0510 → D0502-L34 → M0326 → D0320-L34 → M0325 → D0319-L26 → M0324 → D0327-L24 → M0321 → D0318-L24 → M0322 → B161-007DC0007 → END |  |  |  |  | 13
B1-UPSP-73702 | -P20 | 01 |  | PE-L1-3C4-01 | PE-L1-3C4-01 | GTG-U2-009 |  |  | 1 | 33 | B1-UPSP-73702-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-01 | 1.19 | 230 | U | 30 | GTG | B1-UPSP-73702 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ADMIN. - BLOCK#1 - B | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | 12CRY01GW021-E01 | GTG #12 SERVER/LAN CABINET | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / SERVER ROOM | L1, N, PE | B073-016AT0013 → B073-016AT0015 → B073-016AT0011 → END |  |  |  |  | 13
B1-UPSP-64702 | -P20 | 01 |  | PE-L1-3C6-03 | PE-L1-3C6-03 | GTG-U2-011 |  | DONE | 1 | 34 | B1-UPSP-64702-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-03 | 0.7 | 230 | U | 220 | GTG | B1-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | 12CRU01GE001-E01 | GTG #12 POWER SUPPLY OPERATOR TERMINAL | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, N, PE | B164-006HT0202 → B164-006HT0007 → B164-006HT0008 → B164-006HT0009 → B164-006HT0010 → B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0008 → M0501 → D0517-L15 → M0510 → D0502-L26 → M0326 → D0320-L26 → M0325 → D0319-L22 → M0324 → D0327-L22 → M0321 → D0318-L22 → M0322 → D0328-L31 → M0323 → B111-996CT0023 → B111-016CT0024 → END |  |  |  |  | 14.5
B2-SWG-64601 | -P20 | 01 |  | PE-L1-1C240-08 | PE-L1-1C240-08 | GTG-U3-001 |  |  | 1 | 35 | B2-SWG-64601-P2001 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-08 | 292 | 400 | N | 180 | GTG | B2-SWG-64601 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1 | 21BFA00GS001-E01 | GTG #21 LV SWGR INCMR FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1 | B264-016AT0025 → B264-016AT0026 → B264-016AT0027 → B264-016AT0028 → B264-996AT0012 → M0407 → D0302-L32 → M0302 → D0303-L32 → M0303 → D0305-L23 → M0306 → D0321-L23 → M0307 → D0306-L21 → M0308 → D0322-L23 → M0309 → B212-996BT0022 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B2-SWG-64601 | -P20 | 02 |  | PE-L1-1C240-08 | PE-L1-1C240-08 |  |  |  | 1 | 36 | B2-SWG-64601-P2002 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-08 | 292 | 400 | N | 180 | GTG | B2-SWG-64601 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L2 | 21BFA00GS001-E01 | GTG #21 LV SWGR INCMR FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #21 | L2 | B264-016AT0025 → B264-016AT0026 → B264-016AT0027 → B264-016AT0028 → B264-996AT0012 → M0407 → D0302-L32 → M0302 → D0303-L32 → M0303 → D0305-L23 → M0306 → D0321-L23 → M0307 → D0306-L21 → M0308 → D0322-L23 → M0309 → B212-996BT0022 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B2-SWG-64601 | -P20 | 03 |  | PE-L1-1C240-08 | PE-L1-1C240-08 |  |  |  | 1 | 37 | B2-SWG-64601-P2003 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-08 | 292 | 400 | N | 180 | GTG | B2-SWG-64601 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L3 | 21BFA00GS001-E01 | GTG #21 LV SWGR INCMR FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #21 | L3 | B264-016AT0025 → B264-016AT0026 → B264-016AT0027 → B264-016AT0028 → B264-996AT0012 → M0407 → D0302-L32 → M0302 → D0303-L32 → M0303 → D0305-L23 → M0306 → D0321-L23 → M0307 → D0306-L21 → M0308 → D0322-L23 → M0309 → B212-996BT0022 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B2-SWG-64601 | -P20 | 04 |  | PE-L1-1C240-08 | PE-L1-1C240-08 |  |  |  | 1 | 38 | B2-SWG-64601-P2004 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-08 | 292 | 400 | N | 180 | GTG | B2-SWG-64601 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1 | 21BFA00GS001-E01 | GTG #21 LV SWGR INCMR FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1 | B264-016AT0025 → B264-016AT0026 → B264-016AT0027 → B264-016AT0028 → B264-996AT0012 → M0407 → D0302-L32 → M0302 → D0303-L32 → M0303 → D0305-L23 → M0306 → D0321-L23 → M0307 → D0306-L21 → M0308 → D0322-L23 → M0309 → B212-996BT0022 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B2-SWG-64601 | -P20 | 05 |  | PE-L1-1C240-09 | PE-L1-1C240-09 |  |  |  | 1 | 39 | B2-SWG-64601-P2005 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-09 | 292 | 400 | N | 180 | GTG | B2-SWG-64601 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L2 | 21BFA00GS001-E01 | GTG #21 LV SWGR INCMR FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #21 | L2 | B264-016AT0025 → B264-016AT0026 → B264-016AT0027 → B264-016AT0028 → B264-996AT0012 → M0407 → D0302-L32 → M0302 → D0303-L32 → M0303 → D0305-L23 → M0306 → D0321-L23 → M0307 → D0306-L21 → M0308 → D0322-L23 → M0309 → B212-996BT0022 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B2-SWG-64601 | -P20 | 06 |  | PE-L1-1C240-09 | PE-L1-1C240-09 |  |  |  | 1 | 40 | B2-SWG-64601-P2006 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-09 | 292 | 400 | N | 180 | GTG | B2-SWG-64601 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L3 | 21BFA00GS001-E01 | GTG #21 LV SWGR INCMR FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #21 | L3 | B264-016AT0025 → B264-016AT0026 → B264-016AT0027 → B264-016AT0028 → B264-996AT0012 → M0407 → D0302-L32 → M0302 → D0303-L32 → M0303 → D0305-L23 → M0306 → D0321-L23 → M0307 → D0306-L21 → M0308 → D0322-L23 → M0309 → B212-996BT0022 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B2-SWG-64601 | -P20 | 07 |  | PE-L1-1C240-09 | PE-L1-1C240-09 |  |  |  | 1 | 41 | B2-SWG-64601-P2007 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-09 | 292 | 400 | N | 180 | GTG | B2-SWG-64601 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | N | 21BFA00GS001-E01 | GTG #21 LV SWGR INCMR FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #21 | N | B264-016AT0025 → B264-016AT0026 → B264-016AT0027 → B264-016AT0028 → B264-996AT0012 → M0407 → D0302-L32 → M0302 → D0303-L32 → M0303 → D0305-L23 → M0306 → D0321-L23 → M0307 → D0306-L21 → M0308 → D0322-L23 → M0309 → B212-996BT0022 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B2-ESWG-64601 | -P20 | 01 |  | PE-L1-1C240-10 | PE-L1-1C240-10 | GTG-U3-002 |  |  | 1 | 42 | B2-ESWG-64601-P2001 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-10 | 146 | 400 | E | 170 | GTG | B2-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1 | 21BMA00GS001-E01 | GTG #21 STBY LV-SWGR INCM FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1 | B264-016BT0030 → B264-016BT0029 → B264-996BT0012 → M0407 → D0302-L33 → M0302 → D0303-L33 → M0303 → D0305-L24 → M0306 → D0321-L24 → M0307 → D0306-L25 → M0308 → D0322-L25 → M0309 → B212-996AT0023 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B2-ESWG-64601 | -P20 | 02 |  | PE-L1-1C240-10 | PE-L1-1C240-10 |  |  |  | 1 | 43 | B2-ESWG-64601-P2002 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-10 | 146 | 400 | E | 170 | GTG | B2-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L2 | 21BMA00GS001-E01 | GTG #21 STBY LV-SWGR INCM FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #21 | L2 | B264-016BT0030 → B264-016BT0029 → B264-996BT0012 → M0407 → D0302-L33 → M0302 → D0303-L33 → M0303 → D0305-L24 → M0306 → D0321-L24 → M0307 → D0306-L25 → M0308 → D0322-L25 → M0309 → B212-996AT0023 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B2-ESWG-64601 | -P20 | 03 |  | PE-L1-1C240-10 | PE-L1-1C240-10 |  | DONE(10/12) 미포설(10/27) | DONE 미포설 | 1 | 44 | B2-ESWG-64601-P2003 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-10 | 146 | 400 | E | 170 | GTG | B2-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L3 | 21BMA00GS001-E01 | GTG #21 STBY LV-SWGR INCM FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #21 | L3 | B264-016BT0030 → B264-016BT0029 → B264-996BT0012 → M0407 → D0302-L33 → M0302 → D0303-L33 → M0303 → D0305-L24 → M0306 → D0321-L24 → M0307 → D0306-L25 → M0308 → D0322-L25 → M0309 → B212-996AT0023 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B2-ESWG-64601 | -P20 | 04 |  | PE-L1-1C185-02 | PE-L1-1C185-02 |  |  |  | 1 | 45 | B2-ESWG-64601-P2004 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-02 | 146 | 400 | E | 170 | GTG | B2-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | N | 21BMA00GS001-E01 | GTG #21 STBY LV-SWGR INCM FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #21 | N | B264-016BT0030 → B264-016BT0029 → B264-996BT0012 → M0407 → D0302-L33 → M0302 → D0303-L33 → M0303 → D0305-L24 → M0306 → D0321-L24 → M0307 → D0306-L25 → M0308 → D0322-L25 → M0309 → B212-996AT0023 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 23
B2-SWG-64301 | -P10 | 01 |  | PE-M1-3C120-18 | PE-M1-3C120-18 | GTG-U3-003 |  |  | 1 | 46 | B2-SWG-64301-P1001 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-18 | 2900 | 10000 | N | 200 | GTG | B2-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1,V1,W1 | 21MBJ01GT001-E01 | GTG #21 HV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #21 | U1,V1,W1 | B264-013JT0003 → B264-013JT0210 → B264-013JT0039 → B264-013JT0040 → B264-993JT0012 → M0407 → D0302-M11 → M0302 → D0303-M11 → M0303 → D0305-M12 → M0306 → D0321-M12 → M0307 → D0306-M17 → M0308 → B261-003DC0002 → END |  |  |  |  | 55 | [7 empty] | 2 | EPKT-17C3XIH2-G56
B2-SWG-64301 | -P10 | 02 |  | PE-M1-3C120-18 | PE-M1-3C120-18 | GTG-U3-004 |  |  | 1 | 47 | B2-SWG-64301-P1002 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-18 | 1230 | 10000 | N | 190 | GTG | B2-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1,V1,W1 | 21MKC01GT001-E01 | GTG #21 HV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #21 | U1,V1,W1 | B264-013JT0003 → B264-013JT0210 → B264-013JT0039 → B264-013JT0040 → B264-993JT0012 → M0407 → D0302-M21 → M0302 → D0303-M21 → M0303 → D0305-M11 → M0306 → D0321-M11 → M0307 → B261-003DC0006 → END |  |  |  |  | 55 | [7 empty] | 2 | EPKT-17C3XIH2-G56
B2-SWG-64301 | -P10 | 03 |  | PE-M1-3C120-19 | PE-M1-3C120-19 | GTG-U3-005 |  |  | 1 | 48 | B2-SWG-64301-P1003 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-19 | 500 | 10000 | N | 230 | GTG | B2-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1,V1,W1 | 21MBN12AP001-M01 | GTG #21 INJECTION PUMP FUEL OIL | 1.1_MAIN BUILDING COMPLEX / GT #21 | U1,V1,W1 | B264-013JT0003 → B264-013JT0210 → B264-013JT0039 → B264-013JT0040 → B264-993JT0012 → M0407 → D0302-M14 → M0302 → D0303-M14 → M0303 → D0305-M15 → M0306 → D0321-M15 → M0307 → D0306-M11 → M0308 → D0308-M11 → M0310 → B261-003DC0001 → END |  |  |  |  | 55 | [7 empty] | 2 | EPKT-17C3XIH2-G56
B2-SWG-64301 | -P20 | 01 |  | PE-L1-3C4-29 | PE-L1-3C4-29 | GTG-U3-007 |  |  | 1 | 49 | B2-SWG-64301-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-29 | 0.315 | 230 | N | 210 | GTG | B2-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | L1, N, PE | 21MBN12AP001-E01 | GTG #21 INJECTION PUMP FUEL OIL SPACE HEATER | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, N, PE | B264-016AT0008 → B264-016AT0211 → B264-016AT0212 → B264-016AT0027 → B264-016AT0028 → B264-996AT0012 → M0407 → D0302-L34 → M0302 → D0303-L34 → M0303 → D0305-L25 → M0306 → D0321-L25 → M0307 → D0306-L23 → M0308 → D0308-L23 → M0310 → B261-007DC0007 → END |  |  |  |  | 13
B2-UPSP-73701 | -P20 | 02 |  | PE-L1-3C4-29 | PE-L1-3C4-29 | GTG-U3-009 |  |  | 1 | 50 | B2-UPSP-73701-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-29 | 1.19 | 230 | U | 20 | GTG | B2-UPSP-73701 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ADMIN. - BLOCK#2 - A | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | 21CRY01GW021-E01 | GTG #21 SERVER/LAN CABINET | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / SERVER ROOM | L1, N, PE | B073-016AT0013 → END |  |  |  |  | 13
B2-UPSP-64701 | -P20 | 01 |  | PE-L1-3C6-05 | PE-L1-3C6-05 | GTG-U3-011 |  |  | 1 | 51 | B2-UPSP-64701-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-05 | 0.7 | 230 | U | 190 | GTG | B2-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | 21CRU01GE001-E01 | GTG #21 POWER SUPPLY OPERATOR TERMINAL | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, N, PE | B264-016FT0061 → B264-016FT0248 → B264-016FT0062 → B264-006AC0010 → M0407 → D0302-L26 → M0302 → D0303-L26 → M0303 → D0305-L26 → M0306 → D0321-L22 → M0307 → D0306-L22 → M0308 → D0322-L31 → M0309 → B212-996AT0021 → B212-016AT0016 → END |  |  |  |  | 14.5
B2-SWG-64604 | -P20 | 01 |  | PE-L1-1C185-01 | PE-L1-1C185-01 | GTG-U4-001 |  |  | 1 | 52 | B2-SWG-64604-P2001 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-01 | 292 | 400 | N | 110 | GTG | B2-SWG-64604 | 400V SWITCHGEAR FOR GT/HRSG #2 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1 | 22BFA00GS001-E01 | GTG #22 LV SWGR INCMR FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1 | B264-016CT0047 → B264-996CT0017 → M0407 → D0302-L33 → M0302 → D0303-L33 → M0303 → D0304-L21 → M0304 → D0307-L23 → M0305 → B212-996DT0022 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 23
B2-SWG-64604 | -P20 | 02 |  | PE-L1-1C185-02 | PE-L1-1C185-02 |  |  |  | 1 | 53 | B2-SWG-64604-P2002 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-02 | 292 | 400 | N | 110 | GTG | B2-SWG-64604 | 400V SWITCHGEAR FOR GT/HRSG #2 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L2 | 22BFA00GS001-E01 | GTG #22 LV SWGR INCMR FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #22 | L2 | B264-016CT0047 → B264-996CT0017 → M0407 → D0302-L33 → M0302 → D0303-L33 → M0303 → D0304-L21 → M0304 → D0307-L23 → M0305 → B212-996DT0022 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 23
B2-SWG-64604 | -P20 | 03 |  | PE-L1-1C185-02 | PE-L1-1C185-02 |  |  |  | 1 | 54 | B2-SWG-64604-P2003 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-02 | 292 | 400 | N | 110 | GTG | B2-SWG-64604 | 400V SWITCHGEAR FOR GT/HRSG #2 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L3 | 22BFA00GS001-E01 | GTG #22 LV SWGR INCMR FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #22 | L3 | B264-016CT0047 → B264-996CT0017 → M0407 → D0302-L33 → M0302 → D0303-L33 → M0303 → D0304-L21 → M0304 → D0307-L23 → M0305 → B212-996DT0022 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 23
B2-SWG-64604 | -P20 | 04 |  | PE-L1-1C185-02 | PE-L1-1C185-02 |  |  |  | 1 | 55 | B2-SWG-64604-P2004 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-02 | 292 | 400 | N | 110 | GTG | B2-SWG-64604 | 400V SWITCHGEAR FOR GT/HRSG #2 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1 | 22BFA00GS001-E01 | GTG #22 LV SWGR INCMR FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1 | B264-016CT0047 → B264-996CT0017 → M0407 → D0302-L33 → M0302 → D0303-L33 → M0303 → D0304-L21 → M0304 → D0307-L23 → M0305 → B212-996DT0022 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 23
B2-SWG-64604 | -P20 | 05 |  | PE-L1-1C185-02 | PE-L1-1C185-02 |  |  |  | 1 | 56 | B2-SWG-64604-P2005 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-02 | 292 | 400 | N | 110 | GTG | B2-SWG-64604 | 400V SWITCHGEAR FOR GT/HRSG #2 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L2 | 22BFA00GS001-E01 | GTG #22 LV SWGR INCMR FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #22 | L2 | B264-016CT0047 → B264-996CT0017 → M0407 → D0302-L33 → M0302 → D0303-L33 → M0303 → D0304-L21 → M0304 → D0307-L23 → M0305 → B212-996DT0022 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 23
B2-SWG-64604 | -P20 | 06 |  | PE-L1-1C185-02 | PE-L1-1C185-02 |  |  |  | 1 | 57 | B2-SWG-64604-P2006 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-02 | 292 | 400 | N | 110 | GTG | B2-SWG-64604 | 400V SWITCHGEAR FOR GT/HRSG #2 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L3 | 22BFA00GS001-E01 | GTG #22 LV SWGR INCMR FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #22 | L3 | B264-016CT0047 → B264-996CT0017 → M0407 → D0302-L33 → M0302 → D0303-L33 → M0303 → D0304-L21 → M0304 → D0307-L23 → M0305 → B212-996DT0022 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 23
B2-SWG-64604 | -P20 | 07 |  | PE-L1-1C185-03 | PE-L1-1C185-03 |  |  |  | 1 | 58 | B2-SWG-64604-P2007 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-03 | 292 | 400 | N | 110 | GTG | B2-SWG-64604 | 400V SWITCHGEAR FOR GT/HRSG #2 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | N | 22BFA00GS001-E01 | GTG #22 LV SWGR INCMR FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #22 | N | B264-016CT0047 → B264-996CT0017 → M0407 → D0302-L33 → M0302 → D0303-L33 → M0303 → D0304-L21 → M0304 → D0307-L23 → M0305 → B212-996DT0022 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 23
B2-ESWG-64602 | -P20 | 01 |  | PE-L1-1C185-03 | PE-L1-1C185-03 | GTG-U4-002 |  |  | 1 | 59 | B2-ESWG-64602-P2001 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-03 | 146 | 400 | E | 110 | GTG | B2-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1 | 22BMA00GS001-E01 | GTG #22 STBY LV-SWGR INCM FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1 | B264-016BT0049 → B264-016BT0048 → B264-996BT0013 → M0407 → D0302-L31 → M0302 → D0303-L31 → M0303 → D0304-L24 → M0304 → B212-996CT0021 → B212-016CT0004 → B212-016CT0003 → B212-016CT0002 → B212-016CT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 23
B2-ESWG-64602 | -P20 | 02 |  | PE-L1-1C185-03 | PE-L1-1C185-03 |  |  |  | 1 | 60 | B2-ESWG-64602-P2002 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-03 | 146 | 400 | E | 110 | GTG | B2-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L2 | 22BMA00GS001-E01 | GTG #22 STBY LV-SWGR INCM FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #22 | L2 | B264-016BT0049 → B264-016BT0048 → B264-996BT0013 → M0407 → D0302-L31 → M0302 → D0303-L31 → M0303 → D0304-L24 → M0304 → B212-996CT0021 → B212-016CT0004 → B212-016CT0003 → B212-016CT0002 → B212-016CT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 23
B2-ESWG-64602 | -P20 | 03 |  | PE-L1-1C185-03 | PE-L1-1C185-03 |  |  |  | 1 | 61 | B2-ESWG-64602-P2003 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-03 | 146 | 400 | E | 110 | GTG | B2-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L3 | 22BMA00GS001-E01 | GTG #22 STBY LV-SWGR INCM FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #22 | L3 | B264-016BT0049 → B264-016BT0048 → B264-996BT0013 → M0407 → D0302-L31 → M0302 → D0303-L31 → M0303 → D0304-L24 → M0304 → B212-996CT0021 → B212-016CT0004 → B212-016CT0003 → B212-016CT0002 → B212-016CT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 23
B2-ESWG-64602 | -P20 | 04 |  | PE-L1-1C185-04 | PE-L1-1C185-04 |  |  |  | 1 | 62 | B2-ESWG-64602-P2004 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-04 | 146 | 400 | E | 110 | GTG | B2-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | N | 22BMA00GS001-E01 | GTG #22 STBY LV-SWGR INCM FDR / PCC | 1.1_MAIN BUILDING COMPLEX / GT #22 | N | B264-016BT0049 → B264-016BT0048 → B264-996BT0013 → M0407 → D0302-L31 → M0302 → D0303-L31 → M0303 → D0304-L24 → M0304 → B212-996CT0021 → B212-016CT0004 → B212-016CT0003 → B212-016CT0002 → B212-016CT0001 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 17.5
B2-SWG-64302 | -P10 | 01 |  | PE-M1-3C120-19 | PE-M1-3C120-19 | GTG-U4-003 |  |  | 1 | 63 | B2-SWG-64302-P1001 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-19 | 2900 | 10000 | N | 120 | GTG | B2-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1,V1,W1 | 22MBJ01GT001-E01 | GTG #22 HV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #22 | U1,V1,W1 | B264-013KT0018 → B264-013KT0209 → B264-013KT0047 → B264-993KT0013 → M0407 → D0302-M17 → M0302 → D0303-M17 → M0303 → D0304-M11 → M0304 → B261-003BC0002 → END |  |  |  |  | 55 | [7 empty] | 2 | EPKT-17C3XIH2-G56
B2-SWG-64302 | -P10 | 02 |  | PE-M1-3C120-18 | PE-M1-3C120-18 | GTG-U4-004 |  |  | 1 | 64 | B2-SWG-64302-P1002 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-18 | 1230 | 10000 | N | 100 | GTG | B2-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1,V1,W1 | 22MKC01GT001-E01 | GTG #22 HV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #22 | U1,V1,W1 | B264-013KT0018 → B264-013KT0209 → B264-013KT0047 → B264-993KT0013 → M0407 → D0302-M15 → M0302 → D0303-M15 → M0303 → B261-003BC0006 → END |  |  |  |  | 55 | [7 empty] | 2 | EPKT-17C3XIH2-G56
B2-SWG-64302 | -P10 | 03 |  | PE-M1-3C120-19 | PE-M1-3C120-19 | GTG-U4-005 |  |  | 1 | 65 | B2-SWG-64302-P1003 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-19 | 500 | 10000 | N | 130 | GTG | B2-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1,V1,W1 | 22MBN12AP001-M01 | GTG #22 INJECTION PUMP FUEL OIL | 1.1_MAIN BUILDING COMPLEX / GT #22 | U1,V1,W1 | B264-013KT0018 → B264-013KT0209 → B264-013KT0047 → B264-993KT0013 → M0407 → D0302-M16 → M0302 → D0303-M16 → M0303 → D0304-M12 → M0304 → B261-003BC0001 → END |  |  |  |  | 55 | [7 empty] | 2 | EPKT-17C3XIH2-G56
B2-SWG-64302 | -P20 | 01 |  | PE-L1-3C4-29 | PE-L1-3C4-29 | GTG-U4-007 |  |  | 1 | 66 | B2-SWG-64302-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-29 | 0.315 | 230 | N | 140 | GTG | B2-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | L1, N, PE | 22MBN12AP001-E01 | GTG #22 INJECTION PUMP FUEL OIL SPACE HEATER | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, N, PE | B264-016AT0013 → B264-016AT0212 → B264-016AT0027 → B264-016AT0028 → B264-996AT0012 → M0407 → D0302-L27 → M0302 → D0303-L27 → M0303 → D0304-L23 → M0304 → B261-007BC0007 → END |  |  |  |  | 13
B2-UPSP-73702 | -P20 | 02 |  | PE-L1-3C4-29 | PE-L1-3C4-29 | GTG-U4-009 |  |  | 1 | 67 | B2-UPSP-73702-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-29 | 1.19 | 230 | U | 20 | GTG | B2-UPSP-73702 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ADMIN. - BLOCK#2 - B | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | 22CRY01GW021-E01 | GTG #22 SERVER/LAN CABINET | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / SERVER ROOM | L1, N, PE | B073-016AT0013 → END |  |  |  |  | 13
B2-UPSP-64702 | -P20 | 01 |  | PE-L1-3C6-05 | PE-L1-3C6-05 | GTG-U4-011 |  |  | 1 | 68 | B2-UPSP-64702-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-05 | 0.7 | 230 | U | 130 | GTG | B2-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | 22CRU01GE001-E01 | GTG #22 POWER SUPPLY OPERATOR TERMINAL | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, N, PE | B264-016FT0061 → B264-016FT0248 → B264-016FT0062 → B264-006AC0009 → M0407 → D0302-L32 → M0302 → D0303-L32 → M0303 → D0304-L22 → M0304 → D0307-L31 → M0305 → B212-996CT0023 → B212-016CT0024 → END |  |  |  |  | 14.5
B1-DCP-59701 | -P20 | 01 |  | PE-L1-2C25-01 | PE-L1-2C25-01 | STG-B1-002 |  |  | 1 | 69 | B1-DCP-59701-P2001 | 0.6/1kV CU/XLPE/LSZH | 2C x 25sqmm | PE-L1-2C25-01 | 11 | 220 | D | 30 | STG / Lubricant oil system | B1-DCP-59701 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L+, L- | B1-MS-13701 | DC STARTER EOP (MAIN) | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L+, L- | B159-006AT0014 → B159-006AT0003 → END
B1-DCP-59702 | -P20 | 01 |  | PE-L1-2C25-01 | PE-L1-2C25-01 | STG-B1-003 |  |  | 1 | 70 | B1-DCP-59702-P2001 | 0.6/1kV CU/XLPE/LSZH | 2C x 25sqmm | PE-L1-2C25-01 | 11 | 220 | D | 40 | STG / Lubricant oil system | B1-DCP-59702 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L+, L- | B1-MS-13701 | DC STARTER EOP (BACK UP) | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L+, L- | B159-006BT0005 → B159-006BT0006 → B159-006BT0019 → B159-006BT0001 → END
B1-DB-59601 | -P20 | 01 |  | PE-L1-3C4-23 | PE-L1-3C4-23 | STG-B1-004 |  |  | 1 | 71 | B1-DB-59601-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-23 | 2 | 230 | N | 30 | STG / Lubricant oil system | B1-DB-59601 | 400V-230V DIST. BOARD FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-MS-13701 | DC STARTER EOP (AUX. POWER) | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, N, PE | B159-006AT0003 → END
B1-EMCC-64601 | -P20 | 01 |  | PE-L1-5C120/70-04 | PE-L1-5C120/70-04 | STG-B1-005 | DONE(10/27) | DONE | 1 | 72 | B1-EMCC-64601-P2001 | 0.6/1kV CU/XLPE/LSZH | 4C x 120sqmm + 1C X 70sqmm | PE-L1-5C120/70-04 | 45 | 400 | E | 370 | STG | B1-EMCC-64601 | 400V EMERGENCY MCC FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B1-VSD-13601 | FRQ.CONV.TURN.GEAR POWER SUPPLY | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, L2, L3, N, PE | B164-016BT0105 → B164-016BT0104 → B164-016BT0103 → B164-016BT0102 → B164-016BT0101 → B164-016BT0100 → B164-996BT0024 → M0504 → D0531-L44 → M0510 → D0502-L24 → M0326 → D0320-L24 → M0325 → D0319-L21 → M0324 → D0327-L21 → M0321 → D0317-L21 → M0320 → D0323-L21 → M0319 → D0316-L21 → M0318 → D0315-L24 → M0315 → D0314-L24 → B159-006BT0013 → B159-006BT0024 → B159-006BT0023 → B159-006BT0022 → B159-006BT0010 → B159-006BT0018 → B159-006BT0006 → B159-006BT0019 → B159-006BT0001 → END
B1-DB-59601 | -P20 | 02 |  | PE-L1-3C4-01 | PE-L1-3C4-01 | STG-B1-006 |  |  | 1 | 73 | B1-DB-59601-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-01 | 2 | 230 | N | 30 | STG | B1-DB-59601 | 400V-230V DIST. BOARD FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-VSD-13601 | FRQ.CONV.TURN.GEAR POWER SUPPLY (AUX. POWER) | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, N, PE | B159-006AT0003 → END
B1-EMCC-64601 | -P20 | 02 |  | PE-L1-4C70/35-01 | PE-L1-4C70/35-01 | STG-B1-007 | DONE(9/28) | DONE | 1 | 74 | B1-EMCC-64601-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 70sqmm + 1C X 35sqmm | PE-L1-4C70/35-01 | 37 | 400 | E | 410 | STG / Lubricant oil system | B1-EMCC-64601 | 400V EMERGENCY MCC FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-SKD-13-201-P73A (B1-JBP-1309) | MOTOR MAIN OIL PUMP 1 | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, L2, L3, PE | B164-016BT0105 → B164-016BT0104 → B164-016BT0103 → B164-016BT0102 → B164-016BT0101 → B164-016BT0100 → B164-996BT0024 → M0504 → D0531-L44 → M0510 → D0502-L35 → M0326 → D0320-L24 → M0325 → D0319-L21 → M0324 → D0327-L21 → M0321 → D0317-L21 → M0320 → D0323-L21 → M0319 → D0316-L21 → M0318 → D0315-L24 → M0315 → D0314-L25 → B159-006AT0017 → B159-006AT0018 → B159-006AT0006 → B159-006AT0019 → B159-006AT0003 → B159-006AT0025 → D0326-L11 → M0316 → B113-997AT0010 → B113-017AT0009 → B113-017AT0002 → B113-017AT0001 → B113-016BC0001 → END
B1-EMCC-64602 | -P20 | 01 |  | PE-L1-4C70/35-01 | PE-L1-4C70/35-01 | STG-B1-008 | DONE(9/28) | DONE | 1 | 75 | B1-EMCC-64602-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 70sqmm + 1C X 35sqmm | PE-L1-4C70/35-01 | 37 | 400 | E | 410 | STG / Lubricant oil system | B1-EMCC-64602 | 400V EMERGENCY MCC FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-SKD-13-201-P73B (B1-JBP-1309) | MOTOR MAIN OIL PUMP 2 | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, L2, L3, PE | B164-016AT0121 → B164-016AT0120 → B164-016AT0119 → B164-016AT0118 → B164-016AT0117 → B164-016AT0116 → B164-996AT0023 → M0504 → D0531-L34 → M0510 → D0502-L36 → M0326 → D0320-L36 → M0325 → D0319-L32 → M0324 → D0327-L26 → M0321 → D0317-L15 → M0320 → D0323-L22 → M0319 → D0316-L22 → M0318 → D0315-L21 → M0315 → D0314-L26 → B159-006BT0013 → B159-006BT0024 → B159-006BT0023 → B159-006BT0022 → B159-006BT0010 → B159-006BT0018 → B159-006BT0006 → B159-006BT0019 → B159-006BT0001 → D0326-L12 → M0316 → B113-996AT0012 → B113-016AT0011 → B113-016AT0002 → B113-016AT0001 → B113-016BC0002 → END
B1-EMCC-64601 | -P20 | 03 |  | PE-L1-3C4-22 | PE-L1-3C4-22 | STG-B1-009 | DONE(9/28) | DONE | 1 | 76 | B1-EMCC-64601-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-22 | 0.2 | 230 | E | 410 | STG / Lubricant oil system | B1-EMCC-64601 | 400V EMERGENCY MCC FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-SKD-13-201-P73A | MOTOR MAIN OIL PUMP 1 MOTER HEATER | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, N, PE | B164-016BT0105 → B164-016BT0104 → B164-016BT0103 → B164-016BT0102 → B164-016BT0101 → B164-016BT0100 → B164-996BT0024 → M0504 → D0531-L44 → M0510 → D0502-L35 → M0326 → D0320-L24 → M0325 → D0319-L21 → M0324 → D0327-L21 → M0321 → D0317-L21 → M0320 → D0323-L21 → M0319 → D0316-L21 → M0318 → D0315-L24 → M0315 → D0314-L25 → B159-006BT0013 → B159-006BT0024 → B159-006BT0023 → B159-006BT0022 → B159-006BT0010 → B159-006BT0018 → B159-006BT0006 → B159-006BT0019 → B159-006BT0001 → D0326-L11 → M0316 → B113-996AT0012 → B113-016AT0011 → B113-016AT0002 → B113-016AT0001 → B113-016BC0001 → END
B1-EMCC-64602 | -P20 | 02 |  | PE-L1-3C4-23 | PE-L1-3C4-23 | STG-B1-010 | DONE(9/28) | DONE | 1 | 77 | B1-EMCC-64602-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-23 | 0.2 | 230 | E | 410 | STG / Lubricant oil system | B1-EMCC-64602 | 400V EMERGENCY MCC FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-SKD-13-201-P73B | MOTOR MAIN OIL PUMP 2 MOTER HEATER | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, N, PE | B164-016AT0121 → B164-016AT0120 → B164-016AT0119 → B164-016AT0118 → B164-016AT0117 → B164-016AT0116 → B164-996AT0023 → M0504 → D0531-L34 → M0510 → D0502-L36 → M0326 → D0320-L36 → M0325 → D0319-L21 → M0324 → D0327-L21 → M0321 → D0317-L21 → M0320 → D0323-L21 → M0319 → D0316-L21 → M0318 → D0315-L21 → M0315 → D0314-L26 → B159-006BT0013 → B159-006BT0024 → B159-006BT0023 → B159-006BT0022 → B159-006BT0010 → B159-006BT0018 → B159-006BT0006 → B159-006BT0019 → B159-006BT0001 → D0326-L12 → M0316 → B113-996AT0012 → B113-016AT0011 → B113-016AT0002 → B113-016AT0001 → B113-016BC0002 → END
B1-EMCC-64602 | -P20 | 03 |  | PE-L1-4C70/35-02 | PE-L1-4C70/35-02 | STG-B1-011 | DONE(10/6) | DONE | 1 | 78 | B1-EMCC-64602-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 70sqmm + 1C X 35sqmm | PE-L1-4C70/35-02 | 30 | 400 | E | 400 | STG / Lubricant oil system | B1-EMCC-64602 | 400V EMERGENCY MCC FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-SKD-13-201-P78A | MOTOR JACKING OIL PUMP 1 | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, L2, L3, PE | B164-016AT0121 → B164-016AT0120 → B164-016AT0119 → B164-016AT0118 → B164-016AT0117 → B164-016AT0116 → B164-996AT0023 → M0504 → D0531-L44 → M0510 → D0502-L35 → M0326 → D0320-L35 → M0325 → D0319-L31 → M0324 → D0327-L25 → M0321 → D0317-L14 → M0320 → D0323-L14 → M0319 → D0316-L14 → M0318 → D0315-L25 → M0315 → D0314-L25 → B159-006AT0017 → B159-006AT0018 → B159-006AT0006 → B159-006AT0019 → B159-006AT0003 → B159-006AT0025 → D0326-L11 → M0316 → B113-997AT0010 → B113-017AT0009 → B113-017AT0002 → B113-017AT0001 → B113-016BC0003 → END
B1-EMCC-64601 | -P20 | 04 |  | PE-L1-4C70/35-02 | PE-L1-4C70/35-02 | STG-B1-012 | DONE(10/6) | DONE | 1 | 79 | B1-EMCC-64601-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 70sqmm + 1C X 35sqmm | PE-L1-4C70/35-02 | 30 | 400 | E | 410 | STG / Lubricant oil system | B1-EMCC-64601 | 400V EMERGENCY MCC FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-SKD-13-201-P78B | MOTOR JACKING OIL PUMP 2 | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, L2, L3, PE | B164-016BT0105 → B164-016BT0104 → B164-016BT0103 → B164-016BT0102 → B164-016BT0101 → B164-016BT0100 → B164-996BT0024 → M0504 → D0531-L34 → M0510 → D0502-L36 → M0326 → D0320-L36 → M0325 → D0319-L32 → M0324 → D0327-L26 → M0321 → D0317-L15 → M0320 → D0323-L22 → M0319 → D0316-L15 → M0318 → D0315-L16 → M0315 → D0314-L26 → B159-006BT0013 → B159-006BT0024 → B159-006BT0023 → B159-006BT0022 → B159-006BT0010 → B159-006BT0018 → B159-006BT0006 → B159-006BT0019 → B159-006BT0001 → D0326-L12 → M0316 → B113-996AT0012 → B113-016AT0011 → B113-016AT0002 → B113-016AT0001 → B113-016BC0004 → END
B1-EMCC-64602 | -P20 | 04 |  | PE-L1-3C4-23 | PE-L1-3C4-23 | STG-B1-012-001 | DONE(9/28) | DONE | 1 | 80 | B1-EMCC-64602-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-23 | 0.2 | 230 | E | 410 | STG / Lubricant oil system | B1-EMCC-64602 | 400V EMERGENCY MCC FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-SKD-13-201-P78A | MOTOR JACKING OIL PUMP 1 MOTER HEATER | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, N, PE | B164-016AT0121 → B164-016AT0120 → B164-016AT0119 → B164-016AT0118 → B164-016AT0117 → B164-016AT0116 → B164-996AT0023 → M0504 → D0531-L44 → M0510 → D0502-L35 → M0326 → D0320-L35 → M0325 → D0319-L31 → M0324 → D0327-L25 → M0321 → D0317-L14 → M0320 → D0323-L14 → M0319 → D0316-L14 → M0318 → D0315-L25 → M0315 → D0314-L25 → B159-006BT0013 → B159-006BT0024 → B159-006BT0023 → B159-006BT0022 → B159-006BT0010 → B159-006BT0018 → B159-006BT0006 → B159-006BT0019 → B159-006BT0001 → D0326-L11 → M0316 → B113-996AT0012 → B113-016AT0011 → B113-016AT0002 → B113-016AT0001 → B113-016BC0003 → END
B1-EMCC-64601 | -P20 | 05 |  | PE-L1-3C4-23 | PE-L1-3C4-23 | STG-B1-012-002 | DONE(9/28) | DONE | 1 | 81 | B1-EMCC-64601-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-23 | 0.2 | 230 | E | 410 | STG / Lubricant oil system | B1-EMCC-64601 | 400V EMERGENCY MCC FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-SKD-13-201-P78B | MOTOR JACKING OIL PUMP 2 MOTER HEATER | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, N, PE | B164-016BT0105 → B164-016BT0104 → B164-016BT0103 → B164-016BT0102 → B164-016BT0101 → B164-016BT0100 → B164-996BT0024 → M0504 → D0531-L34 → M0510 → D0502-L36 → M0326 → D0320-L36 → M0325 → D0319-L32 → M0324 → D0327-L26 → M0321 → D0317-L15 → M0320 → D0323-L22 → M0319 → D0316-L15 → M0318 → D0315-L16 → M0315 → D0314-L26 → B159-006BT0013 → B159-006BT0024 → B159-006BT0023 → B159-006BT0022 → B159-006BT0010 → B159-006BT0018 → B159-006BT0006 → B159-006BT0019 → B159-006BT0001 → D0326-L12 → M0316 → B113-996AT0012 → B113-016AT0011 → B113-016AT0002 → B113-016AT0001 → B113-016BC0004 → END
B1-MCC-59601 | -P20 | 01 |  | PE-L1-4C4-24 | PE-L1-4C4-24 | STG-B1-013 |  |  | 1 | 82 | B1-MCC-59601-P2001 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-24 | 5 | 400 | N | 60 | STG / Lubricant oil system | B1-MCC-59601 | 400V MCC FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-SKD-13-202 | OIL CLEANING UNIT POWER SUPPLY- A | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, L2, L3, PE | B159-006AT0003 → B159-006AT0025 → D0326-L11 → M0316 → B113-006AC0001 → END
B1-MCC-59602 | -P20 | 01 |  | PE-L1-4C4-24 | PE-L1-4C4-24 | STG-B1-015 |  |  | 1 | 83 | B1-MCC-59602-P2001 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-24 | 5.5 | 400 | N | 90 | STG / Lubricant oil system | B1-MCC-59602 | 400V MCC FOR ST #1 FOR BLOCK #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-SKD-13-201-DR80A | MOTOR OIL VAPOUR EXHAUSTION DEVICE 1 | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, L2, L3, PE | B159-006AT0006 → B159-006AT0005 → B159-006AT0014 → B159-006AT0025 → D0326-L11 → M0316 → B113-997AT0010 → B113-017AT0009 → B113-017AT0002 → B113-017AT0001 → B113-016BC0004 → END
B1-MCC-59601 | -P20 | 02 |  | PE-L1-4C4-24 | PE-L1-4C4-24 | STG-B1-016 |  |  | 1 | 84 | B1-MCC-59601-P2002 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-24 | 5.5 | 400 | N | 80 | STG / Lubricant oil system | B1-MCC-59601 | 400V MCC FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-SKD-13-201-DR80B | MOTOR OIL VAPOUR EXHAUSTION DEVICE 2 | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, L2, L3, PE | B159-006BT0003 → B159-006BT0001 → D0326-L12 → M0316 → B113-996AT0012 → B113-016AT0011 → B113-016AT0002 → B113-016AT0001 → B113-016BC0003 → END
B1-MCC-59602 | -P20 | 02 |  | PE-L1-4C10-01 | PE-L1-4C10-01 | STG-B1-017 |  |  | 1 | 85 | B1-MCC-59602-P2002 | 0.6/1kV CU/XLPE/LSZH | 4C x 10sqmm | PE-L1-4C10-01 | 17.02 | 400 | N | 90 | STG / Control Oil System | B1-MCC-59602 | 400V MCC FOR ST #1 FOR BLOCK #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-SKD-13-101-M01A | MOTOR CONTROL OIL PUMP 1 | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, L2, L3, PE | B159-006AT0006 → B159-006AT0005 → B159-006AT0014 → B159-006AT0025 → D0326-L11 → M0316 → B113-997AT0010 → B113-017AT0009 → B113-017AT0002 → B113-017AT0001 → B113-016BC0006 → END
B1-MCC-59601 | -P20 | 03 |  | PE-L1-4C6-01 | PE-L1-4C6-01 | STG-B1-018 |  |  | 1 | 86 | B1-MCC-59601-P2003 | 0.6/1kV CU/XLPE/LSZH | 4C x 6sqmm | PE-L1-4C6-01 | 17.02 | 400 | N | 90 | STG / Control Oil System | B1-MCC-59601 | 400V MCC FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-SKD-13-101-M01B | MOTOR CONTROL OIL PUMP 2 | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, L2, L3, PE | B159-006BT0003 → B159-006BT0001 → D0326-L12 → M0316 → B113-996AT0012 → B113-016AT0011 → B113-016AT0002 → B113-016AT0001 → B113-016BC0006 → END
B1-DB-59601 | -P20 | 03 |  | PE-L1-3C10-01 | PE-L1-3C10-01 | STG-B1-019 |  |  | 1 | 87 | B1-DB-59601-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 10sqmm | PE-L1-3C10-01 | 3 | 230 | N | 90 | STG / Control Oil System | B1-DB-59601 | 400V-230V DIST. BOARD FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-JB-13702 | JB HPH SOCKET POWER SUPPLY- A | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, N, PE | B159-006AT0003 → B159-006AT0025 → D0326-L11 → M0316 → B113-996AT0012 → B113-016AT0011 → B113-016AT0002 → B113-016AT0001 → B113-016BC0006 → END
B1-DB-59601 | -P20 | 04 |  | PE-L1-3C10-01 | PE-L1-3C10-01 | STG-B1-019-001 |  |  | 1 | 88 | B1-DB-59601-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 10sqmm | PE-L1-3C10-01 | 3 | 230 | N | 90 | STG / Control Oil System | B1-DB-59601 | 400V-230V DIST. BOARD FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-JB-13602 | JB HPH MOTORS POWER SUPPLY- A | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, N, PE | B159-006AT0003 → B159-006AT0025 → D0326-L12 → M0316 → B113-996AT0012 → B113-016AT0011 → B113-016AT0002 → B113-016AT0001 → B113-016BC0006 → END
B1-MCC-59602 | -P20 | 03 |  | PE-L1-4C4-25 | PE-L1-4C4-25 | STG-B1-020 |  |  | 1 | 89 | B1-MCC-59602-P2003 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-25 | 6.9 | 400 | N | 100 | STG | B1-MCC-59602 | 400V MCC FOR ST #1 FOR BLOCK #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-SKD-13-921-DR02A | MOTOR OF VENT STEAM COND. EXHAUST FAN 1 | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, L2, L3, PE | B159-006AT0006 → B159-006AT0005 → B159-006AT0014 → B159-006AT0025 → D0326-L13 → M0316 → B113-996AT0012 → B113-016AT0011 → B113-016AT0003 → B113-016AT0004 → B113-016AT0005 → B113-016AT0006 → B113-016BC0048 → END
B1-MCC-59601 | -P20 | 04 |  | PE-L1-4C4-01 | PE-L1-4C4-01 | STG-B1-021 |  |  | 1 | 90 | B1-MCC-59601-P2004 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-01 | 6.9 | 400 | N | 100 | STG | B1-MCC-59601 | 400V MCC FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-SKD-13-921-DR02B | MOTOR OF VENT STEAM COND. EXHAUST FAN 2 | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, L2, L3, PE | B159-006BT0003 → B159-006BT0001 → D0326-L14 → M0316 → B113-997AT0010 → B113-017AT0009 → B113-017AT0003 → B113-017AT0004 → B113-017AT0005 → B113-017AT0006 → B113-016BC0049 → END
B1-MCC-59601 | -P20 | 05 |  | PE-L1-4C4-24 | PE-L1-4C4-24 | STG-B1-022 |  |  | 1 | 91 | B1-MCC-59601-P2005 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-24 | 0.37 | 400 | N | 90 | STG / Lubricant oil system | B1-MCC-59601 | 400V MCC FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-SKD-13-201-MOV01 | EDF MAIN OIL PUMP 1 DISCHARGE | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, L2, L3, PE | B159-006AT0003 → B159-006AT0025 → D0326-L13 → M0316 → B113-996AT0012 → B113-016AT0011 → B113-016AT0002 → B113-016AT0001 → B113-016BC0006 → END
B1-MCC-59602 | -P20 | 04 |  | PE-L1-4C4-24 | PE-L1-4C4-24 | STG-B1-023 |  |  | 1 | 92 | B1-MCC-59602-P2004 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-24 | 0.37 | 400 | N | 100 | STG / Lubricant oil system | B1-MCC-59602 | 400V MCC FOR ST #1 FOR BLOCK #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-SKD-13-201-MOV13 | EDF MAIN OIL PUMP 2 DISCHARGE | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, L2, L3, PE | B159-006AT0006 → B159-006AT0005 → B159-006AT0014 → B159-006AT0025 → D0326-L14 → M0316 → B113-996AT0012 → B113-016AT0011 → B113-016AT0002 → B113-016AT0001 → B113-016BC0006 → END
B1-MCC-59602 | -P20 | 05 |  | PE-L1-4C6-01 | PE-L1-4C6-01 | STG-B1-030 |  |  | 1 | 93 | B1-MCC-59602-P2005 | 0.6/1kV CU/XLPE/LSZH | 4C x 6sqmm | PE-L1-4C6-01 | 11 | 400 | N | 130 | STG | B1-MCC-59602 | 400V MCC FOR ST #1 FOR BLOCK #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-P-13-502A | MOTOR VACUUM FLASH TANK PUMP 1 | 1.1_MAIN BUILDING COMPLEX / STG AREA PIT | L1, L2, L3, PE | B159-006AT0006 → B159-006AT0005 → B159-006AT0014 → B159-006AT0025 → D0326-L13 → M0316 → B113-997AT0010 → B113-017AT0009 → B113-017AT0003 → B113-017AT0004 → B113-017AT0005 → B113-017AT0006 → B113-017AT0007 → B113-006AC0005 → B113-016AC0011 → B113-016AC0009 → B113-016AC0006 → END
B1-MCC-59601 | -P20 | 06 |  | PE-L1-4C6-01 | PE-L1-4C6-01 | STG-B1-031 |  |  | 1 | 94 | B1-MCC-59601-P2006 | 0.6/1kV CU/XLPE/LSZH | 4C x 6sqmm | PE-L1-4C6-01 | 11 | 400 | N | 130 | STG | B1-MCC-59601 | 400V MCC FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-P-13-502B | MOTOR VACUUM FLASH TANK PUMP 2 | 1.1_MAIN BUILDING COMPLEX / STG AREA PIT | L1, L2, L3, PE | B159-006BT0003 → B159-006BT0001 → D0326-L14 → M0316 → B113-996AT0012 → B113-016AT0011 → B113-016AT0003 → B113-016AT0004 → B113-016AT0005 → B113-016AT0006 → B113-016AT0007 → B113-006AC0006 → B113-016AC0012 → B113-016AC0010 → B113-016AC0005 → END
B1-MCC-59602 | -P20 | 06 |  | PE-L1-5C4-01 | PE-L1-5C4-01 | STG-B1-032 |  |  | 1 | 95 | B1-MCC-59602-P2006 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-01 | 3.5 | 400 | N | 90 | STG | B1-MCC-59602 | 400V MCC FOR ST #1 FOR BLOCK #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, N, PE | B1-JB-13601 | JB GENERATOR POWER SUPPLY- A | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, L2, L3, N, PE | B159-006AT0006 → B159-006AT0005 → B159-006AT0014 → B159-006AT0025 → D0326-L13 → M0316 → B113-996AT0012 → B113-016AT0011 → B113-016AT0003 → B113-016AT0004 → B113-016BC0031 → END
B1-DB-59601 | -P20 | 05 |  | PE-L1-3C4-01 | PE-L1-3C4-01 | STG-B1-032-001 |  |  | 1 | 96 | B1-DB-59601-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-01 | 2 | 230 | N | 80 | STG | B1-DB-59601 | 400V-230V DIST. BOARD FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-JB-13710 | GENERATOR CT BOX (AUX. POWER) | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, N, PE | B159-006AT0003 → B159-006AT0025 → D0326-L14 → B113-996AT0012 → B113-016AT0011 → B113-016AT0003 → B113-016AT0004 → B113-016AT0005 → B113-016BC0030 → END
B1-DB-59602 | -P20 | 01 |  | PE-L1-3C4-01 | PE-L1-3C4-01 | STG-B1-032-002 |  |  | 1 | 97 | B1-DB-59602-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-01 | 2 | 230 | N | 80 | STG | B1-DB-59602 | 400V-230V DIST. BOARD FOR ST #1 FOR BLOCK #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-JB-13720 | NEUTRAL CUBICLE BOX (AUX. POWER) | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, N, PE | B159-006AT0006 → B159-006AT0005 → B159-006AT0014 → B159-006AT0025 → D0326-L13 → M0316 → B113-996AT0012 → B113-016AT0011 → B113-016AT0003 → B113-017BC0001 → END
B1-MCC-59601 | -P20 | 07 |  | PE-L1-4C16-01 | PE-L1-4C16-01 | STG-B1-033 |  |  | 1 | 98 | B1-MCC-59601-P2007 | 0.6/1kV CU/XLPE/LSZH | 4C x 16sqmm | PE-L1-4C16-01 | 25 | 400 | N | 80 | STG / Lubricant oil system | B1-MCC-59601 | 400V MCC FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-SKD-13-201-H71 | HEATER MAIN OIL TANK | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, L2, L3, PE | B159-006AT0003 → B159-006AT0025 → D0326-L14 → M0316 → B113-996AT0012 → B113-016AT0011 → B113-016AT0002 → B113-016AT0001 → B113-016BC0004 → END
B1-MCC-59602 | -P20 | 07 |  | PE-L1-4C16-01 | PE-L1-4C16-01 | STG-B1-034 |  |  | 1 | 99 | B1-MCC-59602-P2007 | 0.6/1kV CU/XLPE/LSZH | 4C x 16sqmm | PE-L1-4C16-01 | 25 | 400 | N | 90 | STG / Lubricant oil system | B1-MCC-59602 | 400V MCC FOR ST #1 FOR BLOCK #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-SKD-13-201-H72 | HEATER 2 MAIN OIL TANK | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, L2, L3, PE | B159-006AT0006 → B159-006AT0005 → B159-006AT0014 → B159-006AT0025 → D0326-L13 → M0316 → B113-996AT0012 → B113-016AT0011 → B113-016AT0002 → B113-016AT0001 → B113-016BC0003 → END
B1-DCP-59702 | -P20 | 02 |  | PE-L1-2C4-06 | PE-L1-2C4-06 | STG-B1-036 |  |  | 1 | 100 | B1-DCP-59702-P2002 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-06 | 0.5 | 220 | D | 110 | STG | B1-DCP-59702 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L+, L- | B1-PA-13701 | GEN.ONLINE MONITORING POWER SUPPLY (MAIN) | 1.1_MAIN BUILDING COMPLEX / STG #1 | L+, L- | B159-006AT0014 → B159-006AT0025 → D0326-L13 → M0316 → B113-997AT0010 → B113-017AT0009 → B113-017AT0003 → B113-017AT0004 → B113-017AT0005 → B113-017AT0006 → B113-017AT0007 → B113-016BC0026 → END
B1-DCP-59701 | -P20 | 02 |  | PE-L1-2C4-03 | PE-L1-2C4-03 | STG-B1-037 |  |  | 1 | 101 | B1-DCP-59701-P2002 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-03 | 0.5 | 220 | D | 120 | STG | B1-DCP-59701 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L+, L- | B1-PA-13701 | GEN.ONLINE MONITORING POWER SUPPLY (BACK UP) | 1.1_MAIN BUILDING COMPLEX / STG #1 | L+, L- | B159-006BT0005 → B159-006BT0006 → B159-006BT0019 → B159-006BT0001 → D0326-L14 → M0316 → B113-996AT0012 → B113-016AT0011 → B113-016AT0003 → B113-016AT0004 → B113-016AT0005 → B113-016AT0006 → B113-016AT0007 → B113-016BC0027 → END
B1-DB-59602 | -P20 | 02 |  | PE-L1-3C6-03 | PE-L1-3C6-03 | STG-B1-037-001 |  |  | 1 | 102 | B1-DB-59602-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-03 | 2 | 230 | N | 120 | STG | B1-DB-59602 | 400V-230V DIST. BOARD FOR ST #1 FOR BLOCK #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-PA-13701 | GEN.ONLINE MONITORING POWER SUPPLY (AUX. POWER) | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, N, PE | B159-006AT0006 → B159-006AT0005 → B159-006AT0014 → B159-006AT0025 → D0326-L13 → M0316 → B113-996AT0012 → B113-016AT0011 → B113-016AT0003 → B113-016AT0004 → B113-016AT0005 → B113-016AT0006 → B113-016AT0007 → B113-016BC0027 → END
B1-MCC-59601 | -P20 | 08 |  | PE-L1-4C4-05 | PE-L1-4C4-05 | STG-B1-038 |  |  | 1 | 103 | B1-MCC-59601-P2008 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-05 | 1.5 | 400 | N | 120 | STG | B1-MCC-59601 | 400V MCC FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-MOV-13-566 | EDSV DRAIN T1 | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, L2, L3, PE | B159-006AT0003 → B159-006AT0025 → D0314-L22 → M0315 → D0315-L22 → M0318 → D0331-L14 → M0317 → B113-016BC0046 → END
B1-MCC-59602 | -P20 | 08 |  | PE-L1-4C4-01 | PE-L1-4C4-01 | STG-B1-039 |  |  | 1 | 104 | B1-MCC-59602-P2008 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-01 | 1.5 | 400 | N | 130 | STG | B1-MCC-59602 | 400V MCC FOR ST #1 FOR BLOCK #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-MOV-13-561 | EDSV DRAIN T2 | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, L2, L3, PE | B159-006AT0006 → B159-006AT0005 → B159-006AT0014 → B159-006AT0025 → D0314-L21 → M0315 → D0315-L21 → M0318 → D0331-L15 → M0317 → B113-016BC0047 → END
B1-MCC-59601 | -P20 | 09 |  | PE-L1-4C4-01 | PE-L1-4C4-01 | STG-B1-040 |  |  | 1 | 105 | B1-MCC-59601-P2009 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-01 | 1.5 | 400 | N | 120 | STG | B1-MCC-59601 | 400V MCC FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-MOV-13-564 | EDSV DRAIN T3 | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, L2, L3, PE | B159-006AT0003 → B159-006AT0025 → D0314-L22 → M0315 → D0315-L22 → M0318 → D0331-L14 → M0317 → B113-016BC0045 → END
B1-MCC-59602 | -P20 | 09 |  | PE-L1-4C4-01 | PE-L1-4C4-01 | STG-B1-041 |  |  | 1 | 106 | B1-MCC-59602-P2009 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-01 | 1.5 | 400 | N | 130 | STG | B1-MCC-59602 | 400V MCC FOR ST #1 FOR BLOCK #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-MOV-13-565 | EDSV DRAIN T5 | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, L2, L3, PE | B159-006AT0006 → B159-006AT0005 → B159-006AT0014 → B159-006AT0025 → D0314-L21 → M0315 → D0315-L21 → M0318 → D0331-L15 → M0317 → B113-016BC0044 → END
B1-MCC-59601 | -P20 | 10 |  | PE-L1-4C4-25 | PE-L1-4C4-25 | STG-B1-044 |  |  | 1 | 107 | B1-MCC-59601-P2010 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-25 | 1.5 | 400 | N | 120 | STG | B1-MCC-59601 | 400V MCC FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-MOV-13-405 | EDSV DRAIN L1 | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, L2, L3, PE | B159-006AT0003 → B159-006AT0025 → D0314-L22 → M0315 → D0315-L22 → M0318 → D0331-L14 → M0317 → B113-016BC0042 → END
B1-MCC-59602 | -P20 | 10 |  | PE-L1-4C4-25 | PE-L1-4C4-25 | STG-B1-045 |  |  | 1 | 108 | B1-MCC-59602-P2010 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-25 | 1.5 | 400 | N | 130 | STG | B1-MCC-59602 | 400V MCC FOR ST #1 FOR BLOCK #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-MOV-13-409 | EDSV DRAIN L2 | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, L2, L3, PE | B159-006AT0006 → B159-006AT0005 → B159-006AT0014 → B159-006AT0025 → D0314-L21 → M0315 → D0315-L21 → M0318 → D0331-L15 → M0317 → B113-016BC0041 → END
B1-MCC-59601 | -P20 | 11 |  | PE-L1-4C4-25 | PE-L1-4C4-25 | STG-B1-046 |  |  | 1 | 109 | B1-MCC-59601-P2011 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-25 | 1.5 | 400 | N | 120 | STG | B1-MCC-59601 | 400V MCC FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-PCV-13-659 | EDCV SEALING GLAND | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, L2, L3, PE | B159-006AT0003 → B159-006AT0025 → D0326-L12 → M0316 → B113-996AT0012 → B113-016AT0011 → B113-016AT0003 → B113-016AT0004 → B113-016AT0005 → B113-016AT0006 → B113-016AT0007 → B113-016BC0050 → END
B1-MCC-59602 | -P20 | 11 |  | PE-L1-4C4-25 | PE-L1-4C4-25 | STG-B1-047 |  |  | 1 | 110 | B1-MCC-59602-P2011 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-25 | 1.5 | 400 | N | 130 | STG | B1-MCC-59602 | 400V MCC FOR ST #1 FOR BLOCK #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-PCV-13-651 | EDCV REAR GLAND TO VACUUM FLASH TANK | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, L2, L3, PE | B159-006AT0006 → B159-006AT0005 → B159-006AT0014 → B159-006AT0025 → D0326-L12 → M0316 → B113-996AT0012 → B113-016AT0011 → B113-016AT0003 → B113-016AT0004 → B113-016AT0005 → B113-016AT0006 → B113-016AT0007 → B113-016BC0051 → END
B1-MCC-59602 | -P20 | 12 |  | PE-L1-4C4-25 | PE-L1-4C4-25 | STG-B1-048 |  |  | 1 | 111 | B1-MCC-59602-P2012 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-25 | 1.5 | 400 | N | 110 | STG | B1-MCC-59602 | 400V MCC FOR ST #1 FOR BLOCK #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-PCV-13-601 | EDCV INNER GLD.STEAM | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, L2, L3, PE | B159-006AT0006 → B159-006AT0005 → B159-006AT0014 → B159-006AT0025 → D0326-L12 → M0316 → B113-996AT0012 → B113-016AT0011 → B113-016AT0003 → B113-016AT0004 → B113-016AT0005 → B113-016AT0006 → B113-016AT0007 → B113-016BC0052 → END
B1-MCC-59602 | -P20 | 13 |  | PE-L1-4C4-25 | PE-L1-4C4-25 | STG-B1-048-001 |  |  | 1 | 112 | B1-MCC-59602-P2013 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-25 | 1.5 | 400 | N | 130 | STG | B1-MCC-59602 | 400V MCC FOR ST #1 FOR BLOCK #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-MOV-13-607 | EDSV DRAIN G1 | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, L2, L3, PE | B159-006AT0006 → B159-006AT0005 → B159-006AT0014 → B159-006AT0025 → D0314-L21 → M0315 → D0315-L21 → M0318 → D0331-L15 → M0317 → B113-016BC0043 → END
B1-MCC-59601 | -P20 | 12 |  | PE-L1-4C4-25 | PE-L1-4C4-25 | STG-B1-048-002 |  |  | 1 | 113 | B1-MCC-59601-P2012 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-25 | 1.5 | 400 | N | 130 | STG | B1-MCC-59601 | 400V MCC FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-LCV-13-501 | EDCV COND.MINIMAL FROM FLT TO COND. | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, L2, L3, PE | B159-006AT0003 → B159-006AT0025 → D0326-L12 → M0316 → B113-996AT0012 → B113-016AT0011 → B113-016AT0003 → B113-016AT0004 → B113-016AT0005 → B113-016AT0006 → B113-016AT0007 → B113-016BC0054 → END
B1-MCC-59601 | -P20 | 13 |  | PE-L1-4C4-25 | PE-L1-4C4-25 | STG-B1-048-003 |  |  | 1 | 114 | B1-MCC-59601-P2013 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-25 | 1.5 | 400 | N | 100 | STG | B1-MCC-59601 | 400V MCC FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-FCV-13-531 | EDCV SPRAY.FLT | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, L2, L3, PE | B159-006AT0003 → B159-006AT0025 → D0326-L12 → M0316 → B113-996AT0012 → B113-016AT0011 → B113-016AT0003 → B113-016AT0004 → B113-016AT0005 → B113-016AT0006 → B113-016AT0007 → B113-016BC0055 → END
B1-MCC-59601 | -P20 | 14 |  | PE-L1-4C4-02 | PE-L1-4C4-02 | STG-B1-048-004 |  |  | 1 | 115 | B1-MCC-59601-P2014 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-02 | 1.5 | 400 | N | 130 | STG | B1-MCC-59601 | 400V MCC FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-MOV-13-772 | EDSV SPRAY.1 STG OUTLET | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, L2, L3, PE | B159-006AT0003 → B159-006AT0025 → D0314-L22 → M0315 → D0315-L22 → M0318 → D0331-L14 → M0317 → B113-016BC0040 → END
B1-MCC-59602 | -P20 | 14 | 재배정 | PE-L1-4C4-02 | PE-L1-4C4-01 | STG-B1-048-005 |  |  | 1 | 116 | B1-MCC-59602-P2014 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-01 | 1.5 | 400 | N | 130 | STG | B1-MCC-59602 | 400V MCC FOR ST #1 FOR BLOCK #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-MOV-13-777 | EDSV SPRAY.2 STG OUTLET | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, L2, L3, PE | B159-006AT0006 → B159-006AT0005 → B159-006AT0014 → B159-006AT0025 → D0314-L23 → M0315 → D0315-L23 → M0318 → D0331-L21 → M0317 → B113-016BC0039 → END
B1-DCP-59702 | -P20 | 03 |  | PE-L1-2C6-01 | PE-L1-2C6-01 | STG-B1-049 |  |  | 1 | 117 | B1-DCP-59702-P2003 | 0.6/1kV CU/XLPE/LSZH | 2C x 6sqmm | PE-L1-2C6-01 | 2 | 220 | D | 30 | STG | B1-DCP-59702 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L+, L- | B1-TCS-1301A | TPS/TCS POWER SUPPLY (MAIN) | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L+, L- | B159-007AT0016 → B159-007AT0017 → B159-007AT0012 → END
B1-UPSP-59701 | -P20 | 01 |  | PE-L1-3C6-03 | PE-L1-3C6-03 | STG-B1-050 |  |  | 1 | 118 | B1-UPSP-59701-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-03 | 2 | 230 | U | 60 | STG | B1-UPSP-59701 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR STG #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-TCS-1301A | TPS/TCS POWER SUPPLY (BACK UP) | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B159-006BT0003 → B159-006BT0019 → B159-006BT0006 → B159-006BT0018 → B159-006BT0010 → B159-006BT0022 → B159-006BT0023 → END
B1-DB-59601 | -P20 | 06 |  | PE-L1-3C4-01 | PE-L1-3C4-01 | STG-B1-051 |  |  | 1 | 119 | B1-DB-59601-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-01 | 0.2 | 230 | N | 60 | STG | B1-DB-59601 | 400V-230V DIST. BOARD FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-TCS-1301A | TPS/TCS POWER SUPPLY (AUX. POWER) | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B159-006BT0003 → B159-006BT0019 → B159-006BT0006 → B159-006BT0018 → B159-006BT0010 → B159-006BT0022 → B159-006BT0023 → B159-006BT0012 → END
B1-DCP-59701 | -P20 | 03 |  | PE-L1-2C4-03 | PE-L1-2C4-03 | STG-B1-052 |  |  | 1 | 120 | B1-DCP-59701-P2003 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-03 | 0.7 | 220 | D | 40 | STG | B1-DCP-59701 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L+, L- | B1-TCS-1311 | TPC POWER SUPPLY (MAIN) | 1.1_MAIN BUILDING COMPLEX / EXCITATION ROOM | L+, L- | B159-007AT0014 → B159-007AT0015 → B159-007AT0016 → B159-007AT0011 → END
B1-UPSP-59701 | -P20 | 02 |  | PE-L1-3C4-01 | PE-L1-3C4-01 | STG-B1-053 |  |  | 1 | 121 | B1-UPSP-59701-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-01 | 0.7 | 230 | U | 60 | STG | B1-UPSP-59701 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR STG #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-TCS-1311 | TPC POWER SUPPLY (BACK UP) | 1.1_MAIN BUILDING COMPLEX / EXCITATION ROOM | L1, N, PE | B159-006BT0003 → B159-006BT0019 → B159-006BT0006 → B159-006BT0018 → B159-006BT0010 → B159-006BT0022 → B159-006BT0011 → END
B1-DB-59602 | -P20 | 03 |  | PE-L1-3C4-01 | PE-L1-3C4-01 | STG-B1-054 |  |  | 1 | 122 | B1-DB-59602-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-01 | 1 | 230 | N | 40 | STG | B1-DB-59602 | 400V-230V DIST. BOARD FOR ST #1 FOR BLOCK #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-TCS-1311 | TPC POWER SUPPLY (AUX. POWER) | 1.1_MAIN BUILDING COMPLEX / EXCITATION ROOM | L1, N, PE | B159-006BT0005 → B159-006BT0018 → B159-006BT0010 → B159-006BT0022 → B159-006BT0011 → END
B1-DCP-59701 | -P20 | 04 |  | PE-L1-2C4-03 | PE-L1-2C4-03 | STG-B1-055 |  |  | 1 | 123 | B1-DCP-59701-P2004 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-03 | 0.6 | 220 | D | 40 | STG | B1-DCP-59701 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L+, L- | B1-TCS-1321 | VMS POWER SUPPLY (MAIN) | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L+, L- | B159-007AT0014 → B159-007AT0015 → B159-007AT0016 → B159-007AT0011 → END
B1-UPSP-59702 | -P20 | 01 |  | PE-L1-3C4-01 | PE-L1-3C4-01 | STG-B1-056 |  |  | 1 | 124 | B1-UPSP-59702-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-01 | 0.6 | 230 | U | 60 | STG | B1-UPSP-59702 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR STG #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-TCS-1321 | VMS POWER SUPPLY (BACK UP) | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B159-006BT0003 → B159-006BT0019 → B159-006BT0006 → B159-006BT0018 → B159-006BT0010 → B159-006BT0022 → B159-006BT0011 → END
B1-DB-59601 | -P20 | 07 |  | PE-L1-3C4-01 | PE-L1-3C4-01 | STG-B1-057 |  |  | 1 | 125 | B1-DB-59601-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-01 | 0.6 | 230 | N | 60 | STG | B1-DB-59601 | 400V-230V DIST. BOARD FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-TCS-1321 | VMS POWER SUPPLY (AUX. POWER) | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B159-006BT0003 → B159-006BT0019 → B159-006BT0006 → B159-006BT0018 → B159-006BT0010 → B159-006BT0022 → B159-006BT0011 → END
B1-DCP-59701 | -P20 | 05 |  | PE-L1-2C4-03 | PE-L1-2C4-03 | STG-B1-058 |  |  | 1 | 126 | B1-DCP-59701-P2005 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-03 | 0.5 | 220 | D | 30 | STG | B1-DCP-59701 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L+, L- | B1-PRP-13701 | GEN. PROTECTION PANEL (MAIN) | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L+, L- | B159-007AT0016 → B159-007AT0017 → B159-007AT0012 → END
B1-DCP-59702 | -P20 | 04 |  | PE-L1-2C4-03 | PE-L1-2C4-03 | STG-B1-059 |  |  | 1 | 127 | B1-DCP-59702-P2004 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-03 | 0.5 | 220 | D | 40 | STG | B1-DCP-59702 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L+, L- | B1-PRP-13701 | GEN. PROTECTION PANEL (BACK UP) | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L+, L- | B159-006BT0005 → B159-006BT0018 → B159-006BT0010 → B159-006BT0022 → B159-006BT0023 → B159-006BT0012 → END
B1-DB-59602 | -P20 | 04 |  | PE-L1-3C4-01 | PE-L1-3C4-01 | STG-B1-060 |  |  | 1 | 128 | B1-DB-59602-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-01 | 2 | 230 | N | 40 | STG | B1-DB-59602 | 400V-230V DIST. BOARD FOR ST #1 FOR BLOCK #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-PRP-13701 | GEN. PROTECTION PANEL (AUX. POWER) | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B159-006BT0018 → B159-006BT0010 → B159-006BT0022 → B159-006BT0023 → B159-006BT0012 → END
B1-DCP-59702 | -P20 | 05 |  | PE-L1-2C4-03 | PE-L1-2C4-03 | STG-B1-061 |  |  | 1 | 129 | B1-DCP-59702-P2005 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-03 | 0.5 | 220 | D | 30 | STG | B1-DCP-59702 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L+, L- | B1-CP-13701 | GEN. AVR, SYNCH. AND MEAS. PANEL (MAIN) | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L+, L- | B159-007AT0016 → B159-007AT0017 → B159-007AT0012 → END
B1-DCP-59701 | -P20 | 06 |  | PE-L1-2C4-06 | PE-L1-2C4-06 | STG-B1-062 |  |  | 1 | 130 | B1-DCP-59701-P2006 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-06 | 0.5 | 220 | D | 40 | STG | B1-DCP-59701 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L+, L- | B1-CP-13701 | GEN. AVR, SYNCH. AND MEAS. PANEL (BACK UP) | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L+, L- | B159-006BT0005 → B159-006BT0018 → B159-006BT0010 → B159-006BT0022 → B159-006BT0023 → B159-006BT0012 → END
B1-DB-59601 | -P20 | 08 |  | PE-L1-3C4-01 | PE-L1-3C4-01 | STG-B1-063 |  |  | 1 | 131 | B1-DB-59601-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-01 | 2 | 230 | N | 60 | STG | B1-DB-59601 | 400V-230V DIST. BOARD FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-CP-13701 | GEN. AVR, SYNCH. AND MEAS. PANEL (AUX. POWER) | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B159-006BT0003 → B159-006BT0019 → B159-006BT0006 → B159-006BT0018 → B159-006BT0010 → B159-006BT0022 → B159-006BT0023 → B159-006BT0012 → END
B1-DCP-59702 | -P20 | 06 |  | PE-L1-2C4-06 | PE-L1-2C4-06 | STG-B1-064 |  |  | 1 | 132 | B1-DCP-59702-P2006 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-06 | 0.5 | 220 | D | 50 | STG | B1-DCP-59702 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L+, L- | B1-CP-13501 | GEN EXCITATION PANEL (MAIN) | 1.1_MAIN BUILDING COMPLEX / EXCITATION ROOM | L+, L- | B159-006AT0005 → B159-006AT0006 → B159-006AT0019 → B113-007CC0001 → END
B1-DCP-59701 | -P20 | 07 |  | PE-L1-2C4-06 | PE-L1-2C4-06 | STG-B1-065 |  |  | 1 | 133 | B1-DCP-59701-P2007 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-06 | 0.5 | 220 | D | 50 | STG | B1-DCP-59701 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L+, L- | B1-CP-13501 | GEN EXCITATION PANEL (BACK UP) | 1.1_MAIN BUILDING COMPLEX / EXCITATION ROOM | L+, L- | B159-006BT0005 → B159-006BT0006 → B159-006BT0019 → B113-007CC0002 → END
B1-MCC-59602 | -P20 | 15 |  | PE-L1-5C4-01 | PE-L1-5C4-01 | STG-B1-066 |  |  | 1 | 134 | B1-MCC-59602-P2015 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-01 | 2 | 400 | N | 40 | STG | B1-MCC-59602 | 400V MCC FOR ST #1 FOR BLOCK #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, N, PE | B1-CP-13501 | GEN EXCITATION PANEL (AUX. POWER) | 1.1_MAIN BUILDING COMPLEX / EXCITATION ROOM | L1, L2, L3, N, PE | B159-006BT0006 → B159-006BT0019 → B113-006CC0005 → END
B1-DB-59601 | -P20 | 09 |  | PE-L1-3C6-01 | PE-L1-3C6-01 | STG-B1-066-002 |  |  | 1 | 135 | B1-DB-59601-P2009 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-01 | 2 | 230 | N | 110 | STG | B1-DB-59601 | 400V-230V DIST. BOARD FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-JB-13730 | EXCIT.TRANSF.POWER SUPPLY- A | 1.1_MAIN BUILDING COMPLEX / EXCITATION TR ROOM | L1, N, PE | B159-006AT0003 → B159-006AT0014 → B159-006AT0005 → B159-006AT0018 → B159-006AT0017 → D0314-L23 → M0315 → D0315-L23 → M0318 → B113-007CC0006 → END
B1-UPSP-59702 | -P20 | 02 |  | PE-L1-3C6-03 | PE-L1-3C6-03 | STG-B1-066-003 |  |  | 1 | 136 | B1-UPSP-59702-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-03 | 2 | 230 | U | 120 | STG | B1-UPSP-59702 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR STG #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-JB-13730 | EXCIT.TRANSF.POWER SUPPLY- B | 1.1_MAIN BUILDING COMPLEX / EXCITATION TR ROOM | L1, N, PE | B159-006BT0003 → B159-006BT0019 → B159-006BT0006 → B159-006BT0018 → B159-006BT0010 → B159-006BT0022 → B159-006BT0023 → B159-006BT0024 → B159-006BT0013 → D0314-L22 → M0315 → D0315-L22 → M0318 → B113-007CC0006 → END
B1-UPSP-73701 | -P20 | 02 |  | PE-L1-3C6-05 | PE-L1-3C6-05 | STG-B1-067-001 |  |  | 1 | 137 | B1-UPSP-73701-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-05 | 2 | 230 | U | 30 | STG | B1-UPSP-73701 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ADMIN. - BLOCK#1 - A | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B1-TCS-1320 | TCS SERVER(TLCS) CABINET (MAIN) | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / SERVER ROOM | L1, N, PE | B073-017AT0013 → B073-017AT0015 → B073-017AT0011 → END
B1-UPSP-73702 | -P20 | 02 |  | PE-L1-3C6-05 | PE-L1-3C6-05 | STG-B1-067-003 |  |  | 1 | 138 | B1-UPSP-73702-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-05 | 2 | 230 | U | 30 | STG | B1-UPSP-73702 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ADMIN. - BLOCK#1 - B | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B1-TCS-1320 | TCS SERVER(TLCS) CABINET (BACK UP) | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / SERVER ROOM | L1, N, PE | B073-016AT0013 → B073-016AT0015 → B073-016AT0011 → END
B1-UPSP-73701 | -P20 | 03 |  | PE-L1-3C4-26 | PE-L1-3C4-26 | STG-B1-070-001 |  |  | 1 | 139 | B1-UPSP-73701-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-26 | 0.5 | 230 | U | 70 | STG | B1-UPSP-73701 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ADMIN. - BLOCK#1 - A | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B1-TCS-1310S | HIS.SERVER POWER SUPPLY-A | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / SERVER ROOM | L1, N, PE | FIELD RUN
B1-UPSP-73702 | -P20 | 03 |  | PE-L1-3C4-26 | PE-L1-3C4-26 | STG-B1-070-002 |  |  | 1 | 140 | B1-UPSP-73702-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-26 | 2 | 230 | U | 70 | STG | B1-UPSP-73702 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ADMIN. - BLOCK#1 - B | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B1-TCS-1300A | FOPP POWER SUPPLY | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / SERVER ROOM | L1, N, PE | FIELD RUN
B1-DCP-59702 | -P20 | 07 |  | PE-L1-2C6-01 | PE-L1-2C6-01 | STG-B1-071 |  |  | 1 | 141 | B1-DCP-59702-P2007 | 0.6/1kV CU/XLPE/LSZH | 2C x 6sqmm | PE-L1-2C6-01 | 1 | 220 | D | 100 | STG | B1-DCP-59702 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L+, L- | B1-JBX-1302 | JB EWV | 1.1_MAIN BUILDING COMPLEX / STG #1 | L+, L- | B159-006BT0005 → B159-006BT0006 → B159-006BT0019 → B159-006BT0001 → D0326-L15 → M0316 → B213-996AT0012 → B213-016AT0011 → B213-016AT0003 → B213-016AT0004 → B213-016AT0005 → B113-016BC0027 → END
B1-DB-59601 | -P20 | 10 |  | PE-L1-3C4-01 | PE-L1-3C4-01 | STG-B1-072 |  |  | 1 | 142 | B1-DB-59601-P2010 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-01 | 1 | 230 | N | 80 | STG | B1-DB-59601 | 400V-230V DIST. BOARD FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-JB-13701 | JB GENERATOR COLLECTOR HOUSING | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, N, PE | B159-006AT0003 → B159-006AT0025 → D0326-L21 → M0316 → B113-996AT0012 → B113-016AT0011 → B113-016AT0003 → B113-017BC0002 → END
B2-DCP-59701 | -P20 | 01 |  | PE-L1-2C25-01 | PE-L1-2C25-01 | STG-B2-002 |  |  | 1 | 143 | B2-DCP-59701-P2001 | 0.6/1kV CU/XLPE/LSZH | 2C x 25sqmm | PE-L1-2C25-01 | 11 | 220 | D | 30 | STG / Lubricant oil system | B2-DCP-59701 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L+, L- | B2-MS-13701 | DC STARTER EOP (MAIN) | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L+, L- | B259-006AT0014 → B259-006AT0003 → END
B2-DCP-59702 | -P20 | 01 |  | PE-L1-2C25-01 | PE-L1-2C25-01 | STG-B2-003 |  |  | 1 | 144 | B2-DCP-59702-P2001 | 0.6/1kV CU/XLPE/LSZH | 2C x 25sqmm | PE-L1-2C25-01 | 11 | 220 | D | 40 | STG / Lubricant oil system | B2-DCP-59702 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L+, L- | B2-MS-13701 | DC STARTER EOP (BACK UP) | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L+, L- | B259-006BT0005 → B259-006BT0006 → B259-006BT0019 → B259-006BT0001 → END
B2-DB-59601 | -P20 | 01 |  | PE-L1-3C4-23 | PE-L1-3C4-23 | STG-B2-004 |  |  | 1 | 145 | B2-DB-59601-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-23 | 2 | 230 | N | 20 | STG / Lubricant oil system | B2-DB-59601 | 400V-230V DIST. BOARD FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B2-MS-13701 | DC STARTER EOP (AUX. POWER) | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, N, PE | B259-006AT0003 → END
B2-EMCC-64601 | -P20 | 01 |  | PE-L1-5C95/50-03 | PE-L1-5C95/50-03 | STG-B2-005 |  |  | 1 | 146 | B2-EMCC-64601-P2001 | 0.6/1kV CU/XLPE/LSZH | 4C x 95sqmm + 1C X 50sqmm | PE-L1-5C95/50-03 | 45 | 400 | E | 240 | STG | B2-EMCC-64601 | 400V EMERGENCY MCC FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, N, PE | B2-VSD-13601 | FRQ.CONV.TURN.GEAR POWER SUPPLY | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, L2, L3, N, PE | B264-016BT0030 → B264-016BT0029 → B264-996BT0012 → M0407 → D0302-L36 → M0302 → D0303-L36 → M0303 → D0305-L27 → M0306 → D0321-L27 → M0307 → D0306-L25 → M0308 → D0308-L15 → M0310 → D0309-L15 → M0311 → D0310-L25 → B259-006BT0013 → B259-006BT0024 → B259-006BT0023 → B259-006BT0022 → B259-006BT0010 → B259-006BT0018 → B259-006BT0006 → B259-006BT0019 → B259-006BT0001 → END
B2-DB-59601 | -P20 | 02 |  | PE-L1-3C4-19 | PE-L1-3C4-19 | STG-B2-006 |  |  | 1 | 147 | B2-DB-59601-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-19 | 2 | 230 | N | 20 | STG | B2-DB-59601 | 400V-230V DIST. BOARD FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B2-VSD-13601 | FRQ.CONV.TURN.GEAR POWER SUPPLY (AUX. POWER) | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, N, PE | B259-006AT0003 → END
B2-EMCC-64601 | -P20 | 02 |  | PE-L1-4C70/35-03 | PE-L1-4C70/35-03 | STG-B2-007 |  |  | 1 | 148 | B2-EMCC-64601-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 70sqmm + 1C X 35sqmm | PE-L1-4C70/35-03 | 37 | 400 | E | 260 | STG / Lubricant oil system | B2-EMCC-64601 | 400V EMERGENCY MCC FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-SKD-13-201-P73A | MOTOR MAIN OIL PUMP 1 | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, L2, L3, PE | B264-016BT0030 → B264-016BT0029 → B264-996BT0012 → M0407 → D0302-L35 → M0302 → D0303-L36 → M0303 → D0305-L26 → M0306 → D0321-L22 → M0307 → D0306-L23 → M0308 → D0308-L24 → M0310 → D0309-L24 → M0311 → D0310-L24 → B259-007AT0017 → B259-007AT0016 → B259-007AT0015 → B259-007AT0014 → B259-007AT0025 → D0325-L11 → M0313 → B213-997AT0010 → B213-017AT0009 → B213-017AT0002 → B213-017AT0001 → B213-016BC0002 → END
B2-EMCC-64602 | -P20 | 01 |  | PE-L1-4C70/35-03 | PE-L1-4C70/35-03 | STG-B2-008 |  |  | 1 | 149 | B2-EMCC-64602-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 70sqmm + 1C X 35sqmm | PE-L1-4C70/35-03 | 37 | 400 | E | 290 | STG / Lubricant oil system | B2-EMCC-64602 | 400V EMERGENCY MCC FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-SKD-13-201-P73B | MOTOR MAIN OIL PUMP 2 | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, L2, L3, PE | B264-016CT0049 → B264-016CT0048 → B264-996CT0017 → M0407 → D0302-L37 → M0302 → D0303-L37 → M0303 → D0305-L32 → M0306 → D0321-L32 → M0307 → D0306-L32 → M0308 → D0308-L21 → M0310 → D0309-L21 → M0311 → D0310-L21 → B259-006BT0013 → B259-006BT0024 → B259-006BT0023 → B259-006BT0022 → B259-006BT0010 → B259-006BT0018 → B259-006BT0006 → B259-006BT0019 → B259-006BT0001 → D0325-L12 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0002 → B213-016AT0001 → B213-016BC0001 → END
B2-EMCC-64601 | -P20 | 03 |  | PE-L1-3C4-23 | PE-L1-3C4-23 | STG-B2-009 |  |  | 1 | 150 | B2-EMCC-64601-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-23 | 0.2 | 230 | E | 290 | STG / Lubricant oil system | B2-EMCC-64601 | 400V EMERGENCY MCC FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-SKD-13-201-P73A | MOTOR MAIN OIL PUMP 1 MOTER HEATER | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, N, PE | B264-016BT0030 → B264-016BT0029 → B264-996BT0012 → M0407 → D0302-L35 → M0302 → D0303-L36 → M0303 → D0305-L26 → M0306 → D0321-L22 → M0307 → D0306-L23 → M0308 → D0308-L24 → M0310 → D0309-L24 → M0311 → D0310-L24 → B259-006BT0013 → B259-006BT0024 → B259-006BT0023 → B259-006BT0022 → B259-006BT0010 → B259-006BT0018 → B259-006BT0006 → B259-006BT0019 → B259-006BT0001 → D0325-L11 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0002 → B213-016AT0001 → B213-016BC0002 → END
B2-EMCC-64602 | -P20 | 02 |  | PE-L1-3C4-23 | PE-L1-3C4-23 | STG-B2-010 |  |  | 1 | 151 | B2-EMCC-64602-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-23 | 0.2 | 230 | E | 290 | STG / Lubricant oil system | B2-EMCC-64602 | 400V EMERGENCY MCC FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-SKD-13-201-P73B | MOTOR MAIN OIL PUMP 2 MOTER HEATER | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, N, PE | B264-016CT0049 → B264-016CT0048 → B264-996CT0017 → M0407 → D0302-L37 → M0302 → D0303-L37 → M0303 → D0305-L32 → M0306 → D0321-L32 → M0307 → D0306-L32 → M0308 → D0308-L21 → M0310 → D0309-L21 → M0311 → D0310-L21 → B259-006BT0013 → B259-006BT0024 → B259-006BT0023 → B259-006BT0022 → B259-006BT0010 → B259-006BT0018 → B259-006BT0006 → B259-006BT0019 → B259-006BT0001 → D0325-L12 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0002 → B213-016AT0001 → B213-016BC0001 → END
B2-EMCC-64602 | -P20 | 03 |  | PE-L1-4C50/25-03 | PE-L1-4C50/25-03 | STG-B2-011 |  |  | 1 | 152 | B2-EMCC-64602-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 50sqmm + 1C X 25sqmm | PE-L1-4C50/25-03 | 30 | 400 | E | 260 | STG / Lubricant oil system | B2-EMCC-64602 | 400V EMERGENCY MCC FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-SKD-13-201-P78A | MOTOR JACKING OIL PUMP 1 | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, L2, L3, PE | B264-016CT0049 → B264-016CT0048 → B264-996CT0017 → M0407 → D0302-L35 → M0302 → D0303-L36 → M0303 → D0305-L26 → M0306 → D0321-L22 → M0307 → D0306-L24 → M0308 → D0308-L24 → M0310 → D0309-L24 → M0311 → D0310-L24 → B259-007AT0017 → B259-007AT0016 → B259-007AT0015 → B259-007AT0014 → B259-007AT0025 → D0325-L11 → M0313 → B213-997AT0010 → B213-017AT0009 → B213-017AT0002 → B213-017AT0001 → B213-016BC0004 → END
B2-EMCC-64601 | -P20 | 04 |  | PE-L1-4C50/25-03 | PE-L1-4C50/25-03 | STG-B2-012 |  |  | 1 | 153 | B2-EMCC-64601-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 50sqmm + 1C X 25sqmm | PE-L1-4C50/25-03 | 30 | 400 | E | 290 | STG / Lubricant oil system | B2-EMCC-64601 | 400V EMERGENCY MCC FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-SKD-13-201-P78B | MOTOR JACKING OIL PUMP 2 | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, L2, L3, PE | B264-016BT0030 → B264-016BT0029 → B264-996BT0012 → M0407 → D0302-L37 → M0302 → D0303-L37 → M0303 → D0305-L32 → M0306 → D0321-L32 → M0307 → D0306-L32 → M0308 → D0308-L21 → M0310 → D0309-L21 → M0311 → D0310-L21 → B259-006BT0013 → B259-006BT0024 → B259-006BT0023 → B259-006BT0022 → B259-006BT0010 → B259-006BT0018 → B259-006BT0006 → B259-006BT0019 → B259-006BT0001 → D0325-L12 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0002 → B213-016AT0001 → B213-016BC0003 → END
B2-EMCC-64602 | -P20 | 04 |  | PE-L1-3C4-24 | PE-L1-3C4-24 | STG-B2-012-001 |  |  | 1 | 154 | B2-EMCC-64602-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-24 | 0.2 | 230 | E | 260 | STG / Lubricant oil system | B2-EMCC-64602 | 400V EMERGENCY MCC FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-SKD-13-201-P78A | MOTOR JACKING OIL PUMP 1 MOTER HEATER | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, N, PE | B264-016CT0049 → B264-016CT0048 → B264-996CT0017 → M0407 → D0302-L35 → M0302 → D0303-L36 → M0303 → D0305-L26 → M0306 → D0321-L22 → M0307 → D0306-L24 → M0308 → D0308-L24 → M0310 → D0309-L24 → M0311 → D0310-L24 → B259-006AT0017 → B259-006AT0016 → B259-006AT0015 → B259-006AT0014 → B259-006AT0025 → D0325-L11 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0002 → B213-016AT0001 → B213-016BC0004 → END
B2-EMCC-64601 | -P20 | 05 |  | PE-L1-3C4-24 | PE-L1-3C4-24 | STG-B2-012-002 |  |  | 1 | 155 | B2-EMCC-64601-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-24 | 0.2 | 230 | E | 260 | STG / Lubricant oil system | B2-EMCC-64601 | 400V EMERGENCY MCC FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-SKD-13-201-P78B | MOTOR JACKING OIL PUMP 2 MOTER HEATER | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, N, PE | B264-016BT0030 → B264-016BT0029 → B264-996BT0012 → M0407 → D0302-L37 → M0302 → D0303-L37 → M0303 → D0305-L32 → M0306 → D0321-L32 → M0307 → D0306-L32 → M0308 → D0308-L21 → M0310 → D0309-L21 → M0311 → D0310-L21 → B259-006AT0017 → B259-006AT0016 → B259-006AT0015 → B259-006AT0014 → B259-006AT0025 → D0325-L12 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0002 → B213-016AT0001 → B213-016BC0003 → END
B2-MCC-59601 | -P20 | 01 |  | PE-L1-4C4-24 | PE-L1-4C4-24 | STG-B2-013 |  |  | 1 | 156 | B2-MCC-59601-P2001 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-24 | 5 | 400 | N | 60 | STG / Lubricant oil system | B2-MCC-59601 | 400V MCC FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-SKD-13-202 | OIL CLEANING UNIT POWER SUPPLY- A | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, L2, L3, PE | B259-006AT0003 → B259-006AT0025 → D0325-L11 → M0313 → B213-006AC0001 → END
B2-MCC-59601 | -P20 | 02 | From변경 | PE-L1-4C4-24 | PE-L1-4C4-24 | STG-B2-015 | B2-MCC-59601-P2002 |  | 1 | 157 | B2-MCC-59602-P2001 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-24 | 5.5 | 400 | N | 80 | STG / Lubricant oil system | B2-MCC-59602 | 400V MCC FOR ST #2 FOR BLOCK #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-SKD-13-201-DR80A | MOTOR OIL VAPOUR EXHAUSTION DEVICE 1 | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, L2, L3, PE | B259-006BT0006 → B259-006BT0019 → B259-006BT0001 → D0325-L11 → M0313 → B213-997AT0010 → B213-017AT0009 → B213-017AT0002 → B213-017AT0001 → B213-016BC0004 → END
B2-MCC-59602 | -P20 | 01 | From변경 | PE-L1-4C4-24 | PE-L1-4C4-24 | STG-B2-016 | B2-MCC-59602-P2001 |  | 1 | 158 | B2-MCC-59601-P2002 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-24 | 5.5 | 400 | N | 80 | STG / Lubricant oil system | B2-MCC-59601 | 400V MCC FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-SKD-13-201-DR80B | MOTOR OIL VAPOUR EXHAUSTION DEVICE 2 | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, L2, L3, PE | B259-006AT0003 → B259-006AT0025 → D0325-L12 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0002 → B213-016AT0001 → B213-016BC0003 → END
B2-MCC-59602 | -P20 | 02 |  | PE-L1-4C6-02 | PE-L1-4C6-02 | STG-B2-017 |  |  | 1 | 159 | B2-MCC-59602-P2002 | 0.6/1kV CU/XLPE/LSZH | 4C x 6sqmm | PE-L1-4C6-02 | 17.02 | 400 | N | 90 | STG / Control Oil System | B2-MCC-59602 | 400V MCC FOR ST #2 FOR BLOCK #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-SKD-13-101-M01A | MOTOR CONTROL OIL PUMP 1 | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, L2, L3, PE | B259-006AT0006 → B259-006AT0005 → B259-006AT0014 → B259-006AT0025 → D0325-L15 → M0313 → B213-997AT0010 → B213-017AT0009 → B213-017AT0002 → B213-017AT0001 → B213-016BC0006 → END
B2-MCC-59601 | -P20 | 03 |  | PE-L1-4C6-03 | PE-L1-4C6-03 | STG-B2-018 |  |  | 1 | 160 | B2-MCC-59601-P2003 | 0.6/1kV CU/XLPE/LSZH | 4C x 6sqmm | PE-L1-4C6-03 | 17.02 | 400 | N | 90 | STG / Control Oil System | B2-MCC-59601 | 400V MCC FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-SKD-13-101-M01B | MOTOR CONTROL OIL PUMP 2 | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, L2, L3, PE | B259-006BT0003 → B259-006BT0001 → D0325-L11 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0002 → B213-016AT0001 → B113-016BC0006 → END
B2-DB-59601 | -P20 | 03 | From변경 | PE-L1-3C10-02 | PE-L1-3C10-02 | STG-B2-019 |  |  | 1 | 161 | B2-DB-59601-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 10sqmm | PE-L1-3C10-02 | 3 | 230 | N | 90 | STG / Control Oil System | B2-DB-59601 | 400V-230V DIST. BOARD FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B2-JB-13702 | JB HPH SOCKET POWER SUPPLY- A | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, N, PE | B259-006AT0003 → B259-006AT0025 → D0325-L11 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0002 → B213-016AT0001 → B213-016BC0006 → END
B2-DB-59601 | -P20 | 04 | From변경 | PE-L1-3C10-02 | PE-L1-3C10-02 | STG-B2-019-001 |  |  | 1 | 162 | B2-DB-59601-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 10sqmm | PE-L1-3C10-02 | 3 | 230 | N | 90 | STG / Control Oil System | B2-DB-59601 | 400V-230V DIST. BOARD FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B2-JB-13602 | JB HPH MOTORS POWER SUPPLY- A | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, N, PE | B259-006AT0003 → B259-006AT0025 → D0325-L11 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0002 → B213-016AT0001 → B213-016BC0006 → END
B2-MCC-59602 | -P20 | 03 |  | PE-L1-4C4-25 | PE-L1-4C4-25 | STG-B2-020 |  |  | 1 | 163 | B2-MCC-59602-P2003 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-25 | 6.9 | 400 | N | 100 | STG | B2-MCC-59602 | 400V MCC FOR ST #2 FOR BLOCK #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-SKD-13-921-DR02A | MOTOR OF VENT STEAM COND. EXHAUST FAN 1 | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, L2, L3, PE | B259-006AT0006 → B259-006AT0005 → B259-006AT0014 → B259-006AT0025 → D0325-L13 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0003 → B213-016AT0004 → B213-016AT0005 → B213-016AT0006 → B213-016BC0050 → END
B2-MCC-59601 | -P20 | 04 |  | PE-L1-4C4-25 | PE-L1-4C4-25 | STG-B2-021 |  |  | 1 | 164 | B2-MCC-59601-P2004 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-25 | 6.9 | 400 | N | 100 | STG | B2-MCC-59601 | 400V MCC FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-SKD-13-921-DR02B | MOTOR OF VENT STEAM COND. EXHAUST FAN 2 | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, L2, L3, PE | B259-006BT0003 → B259-006BT0001 → D0325-L14 → M0313 → B213-997AT0010 → B213-017AT0009 → B213-017AT0003 → B213-017AT0004 → B213-017AT0005 → B213-017AT0006 → B213-016BC0051 → END
B2-MCC-59601 | -P20 | 05 |  | PE-L1-4C4-24 | PE-L1-4C4-24 | STG-B2-022 |  |  | 1 | 165 | B2-MCC-59601-P2005 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-24 | 0.37 | 400 | N | 80 | STG / Lubricant oil system | B2-MCC-59601 | 400V MCC FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-SKD-13-201-MOV01 | EDF MAIN OIL PUMP 1 DISCHARGE | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, L2, L3, PE | B259-006AT0003 → B259-006AT0025 → D0325-L13 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0002 → B213-016AT0001 → B213-016BC0004 → END
B2-MCC-59602 | -P20 | 04 |  | PE-L1-4C4-24 | PE-L1-4C4-24 | STG-B2-023 |  |  | 1 | 166 | B2-MCC-59602-P2004 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-24 | 0.37 | 400 | N | 80 | STG / Lubricant oil system | B2-MCC-59602 | 400V MCC FOR ST #2 FOR BLOCK #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-SKD-13-201-MOV13 | EDF MAIN OIL PUMP 2 DISCHARGE | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, L2, L3, PE | B259-006AT0006 → B259-006AT0005 → B259-006AT0014 → B259-006AT0025 → D0325-L14 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0002 → B213-016AT0001 → B213-016BC0003 → END
B2-MCC-59602 | -P20 | 05 |  | PE-L1-4C6-02 | PE-L1-4C6-02 | STG-B2-030 |  |  | 1 | 167 | B2-MCC-59602-P2005 | 0.6/1kV CU/XLPE/LSZH | 4C x 6sqmm | PE-L1-4C6-02 | 11 | 400 | N | 130 | STG | B2-MCC-59602 | 400V MCC FOR ST #2 FOR BLOCK #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-P-13-502A | MOTOR VACUUM FLASH TANK PUMP 1 | 1.1_MAIN BUILDING COMPLEX / STG AREA PIT | L1, L2, L3, PE | B259-006AT0006 → B259-006AT0005 → B259-006AT0014 → B259-006AT0025 → D0325-L13 → M0313 → B213-997AT0010 → B213-017AT0009 → B213-017AT0003 → B213-017AT0004 → B213-017AT0005 → B213-017AT0006 → B213-017AT0007 → B213-016BC0037 → B213-006AC0006 → B213-016AC0012 → B213-016AC0010 → B213-016AC0006 → END
B2-MCC-59601 | -P20 | 06 |  | PE-L1-4C6-01 | PE-L1-4C6-01 | STG-B2-031 |  |  | 1 | 168 | B2-MCC-59601-P2006 | 0.6/1kV CU/XLPE/LSZH | 4C x 6sqmm | PE-L1-4C6-01 | 11 | 400 | N | 140 | STG | B2-MCC-59601 | 400V MCC FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-P-13-502B | MOTOR VACUUM FLASH TANK PUMP 2 | 1.1_MAIN BUILDING COMPLEX / STG AREA PIT | L1, L2, L3, PE | B259-006BT0003 → B259-006BT0001 → D0325-L14 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0003 → B213-016AT0004 → B213-016AT0005 → B213-016AT0006 → B213-016AT0007 → B213-016BC0036 → B213-006AC0005 → B213-016AC0011 → B213-016AC0009 → B213-016AC0005 → END
B2-MCC-59602 | -P20 | 06 |  | PE-L1-5C4-03 | PE-L1-5C4-03 | STG-B2-032 |  |  | 1 | 169 | B2-MCC-59602-P2006 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-03 | 3.5 | 400 | N | 80 | STG | B2-MCC-59602 | 400V MCC FOR ST #2 FOR BLOCK #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, N, PE | B2-JB-13601 | JB GENERATOR POWER SUPPLY- A | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, L2, L3, N, PE | B259-006AT0006 → B259-006AT0005 → B259-006AT0014 → B259-006AT0025 → D0325-L13 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0003 → B213-016AT0004 → B213-016BC0031 → END
B2-DB-59601 | -P20 | 05 |  | PE-L1-3C4-29 | PE-L1-3C4-29 | STG-B2-032-001 |  |  | 1 | 170 | B2-DB-59601-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-29 | 2 | 230 | N | 80 | STG | B2-DB-59601 | 400V-230V DIST. BOARD FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B2-JB-13710 | GENERATOR CT BOX (AUX. POWER) | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, N, PE | B259-006AT0003 → B259-006AT0025 → D0325-L14 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0003 → B213-016AT0004 → B213-016AT0005 → B213-016BC0030 → END
B2-DB-59602 | -P20 | 01 |  | PE-L1-3C4-19 | PE-L1-3C4-19 | STG-B2-032-002 |  |  | 1 | 171 | B2-DB-59602-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-19 | 2 | 230 | N | 70 | STG | B2-DB-59602 | 400V-230V DIST. BOARD FOR ST #2 FOR BLOCK #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B2-JB-13720 | NEUTRAL CUBICLE BOX (AUX. POWER) | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, N, PE | B259-006AT0006 → B259-006AT0005 → B259-006AT0014 → B259-006AT0025 → D0325-L13 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0003 → B213-017BC0001 → END
B2-MCC-59601 | -P20 | 07 |  | PE-L1-4C16-01 | PE-L1-4C16-01 | STG-B2-033 |  |  | 1 | 172 | B2-MCC-59601-P2007 | 0.6/1kV CU/XLPE/LSZH | 4C x 16sqmm | PE-L1-4C16-01 | 25 | 400 | N | 80 | STG / Lubricant oil system | B2-MCC-59601 | 400V MCC FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-SKD-13-201-H71 | HEATER MAIN OIL TANK | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, L2, L3, PE | B259-006AT0003 → B259-006AT0025 → D0325-L14 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0002 → B213-016AT0001 → B213-016BC0004 → END
B2-MCC-59602 | -P20 | 07 |  | PE-L1-4C16-02 | PE-L1-4C16-02 | STG-B2-034 |  |  | 1 | 173 | B2-MCC-59602-P2007 | 0.6/1kV CU/XLPE/LSZH | 4C x 16sqmm | PE-L1-4C16-02 | 25 | 400 | N | 80 | STG / Lubricant oil system | B2-MCC-59602 | 400V MCC FOR ST #2 FOR BLOCK #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-SKD-13-201-H72 | HEATER 2 MAIN OIL TANK | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, L2, L3, PE | B259-006AT0006 → B259-006AT0005 → B259-006AT0014 → B259-006AT0025 → D0325-L13 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0002 → B213-016AT0001 → B213-016BC0003 → END
B2-DCP-59702 | -P20 | 02 |  | PE-L1-2C4-04 | PE-L1-2C4-04 | STG-B2-036 |  |  | 1 | 174 | B2-DCP-59702-P2002 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-04 | 0.5 | 220 | D | 100 | STG | B2-DCP-59702 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L+, L- | B2-PA-13701 | GEN.ONLINE MONITORING POWER SUPPLY (MAIN) | 1.1_MAIN BUILDING COMPLEX / STG #2 | L+, L- | B259-006AT0014 → B259-006AT0025 → D0325-L13 → M0313 → B213-997AT0010 → B213-017AT0009 → B213-017AT0003 → B213-017AT0004 → B213-017AT0005 → B213-017AT0006 → B213-017AT0007 → B213-016BC0026 → END
B2-DCP-59701 | -P20 | 02 |  | PE-L1-2C4-04 | PE-L1-2C4-04 | STG-B2-037 |  |  | 1 | 175 | B2-DCP-59701-P2002 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-04 | 0.5 | 220 | D | 120 | STG | B2-DCP-59701 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L+, L- | B2-PA-13701 | GEN.ONLINE MONITORING POWER SUPPLY (BACK UP) | 1.1_MAIN BUILDING COMPLEX / STG #2 | L+, L- | B259-006BT0005 → B259-006BT0006 → B259-006BT0019 → B259-006BT0001 → D0325-L14 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0003 → B213-016AT0004 → B213-016AT0005 → B213-016AT0006 → B213-016AT0007 → B213-016BC0026 → END
B2-DB-59602 | -P20 | 02 |  | PE-L1-3C6-05 | PE-L1-3C6-05 | STG-B2-037-001 |  |  | 1 | 176 | B2-DB-59602-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-05 | 2 | 230 | N | 110 | STG | B2-DB-59602 | 400V-230V DIST. BOARD FOR ST #2 FOR BLOCK #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B2-PA-13701 | GEN.ONLINE MONITORING POWER SUPPLY (AUX. POWER) | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, N, PE | B259-006AT0006 → B259-006AT0005 → B259-006AT0014 → B259-006AT0025 → D0325-L13 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0003 → B213-016AT0004 → B213-016AT0005 → B213-016AT0006 → B213-016AT0007 → B213-016BC0026 → END
B2-MCC-59601 | -P20 | 08 |  | PE-L1-4C4-18 | PE-L1-4C4-18 | STG-B2-038 |  |  | 1 | 177 | B2-MCC-59601-P2008 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-18 | 1.5 | 400 | N | 130 | STG | B2-MCC-59601 | 400V MCC FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-MOV-13-566 | EDSV DRAIN T1 | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, L2, L3, PE | B259-006AT0003 → B259-006AT0025 → B259-006AT0014 → B259-006AT0015 → B259-006AT0016 → B259-006AT0017 → D0310-L21 → M0311 → D0311-L14 → M0312 → D0330-L15 → M0314 → B213-016BC0048 → END
B2-MCC-59602 | -P20 | 08 |  | PE-L1-4C4-18 | PE-L1-4C4-18 | STG-B2-039 |  |  | 1 | 178 | B2-MCC-59602-P2008 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-18 | 1.5 | 400 | N | 130 | STG | B2-MCC-59602 | 400V MCC FOR ST #2 FOR BLOCK #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-MOV-13-561 | EDSV DRAIN T2 | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, L2, L3, PE | B259-006AT0006 → B259-006AT0005 → B259-006AT0014 → B259-006AT0025 → B259-006AT0015 → B259-006AT0016 → B259-006AT0017 → D0310-L22 → M0311 → D0311-L15 → M0312 → D0330-L14 → M0314 → B213-016BC0049 → END
B2-MCC-59601 | -P20 | 09 |  | PE-L1-4C4-18 | PE-L1-4C4-18 | STG-B2-040 |  |  | 1 | 179 | B2-MCC-59601-P2009 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-18 | 1.5 | 400 | N | 130 | STG | B2-MCC-59601 | 400V MCC FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-MOV-13-564 | EDSV DRAIN T3 | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, L2, L3, PE | B259-006AT0003 → B259-006AT0025 → B259-006AT0014 → B259-006AT0015 → B259-006AT0016 → B259-006AT0017 → D0310-L21 → M0311 → D0311-L14 → M0312 → D0330-L15 → M0314 → B213-016BC0047 → END
B2-MCC-59602 | -P20 | 09 |  | PE-L1-4C4-18 | PE-L1-4C4-18 | STG-B2-041 |  |  | 1 | 180 | B2-MCC-59602-P2009 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-18 | 1.5 | 400 | N | 130 | STG | B2-MCC-59602 | 400V MCC FOR ST #2 FOR BLOCK #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-MOV-13-565 | EDSV DRAIN T5 | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, L2, L3, PE | B259-006AT0006 → B259-006AT0005 → B259-006AT0014 → B259-006AT0025 → B259-006AT0015 → B259-006AT0016 → B259-006AT0017 → D0310-L22 → M0311 → D0311-L15 → M0312 → D0330-L14 → M0314 → B213-016BC0046 → END
B2-MCC-59601 | -P20 | 10 |  | PE-L1-4C4-18 | PE-L1-4C4-18 | STG-B2-044 |  |  | 1 | 181 | B2-MCC-59601-P2010 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-18 | 1.5 | 400 | N | 130 | STG | B2-MCC-59601 | 400V MCC FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-MOV-13-405 | EDSV DRAIN L1 | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, L2, L3, PE | B259-006AT0003 → B259-006AT0025 → B259-006AT0014 → B259-006AT0015 → B259-006AT0016 → B259-006AT0017 → D0310-L21 → M0311 → D0311-L14 → M0312 → D0330-L15 → M0314 → B213-016BC0044 → END
B2-MCC-59602 | -P20 | 10 |  | PE-L1-4C4-18 | PE-L1-4C4-18 | STG-B2-045 |  |  | 1 | 182 | B2-MCC-59602-P2010 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-18 | 1.5 | 400 | N | 130 | STG | B2-MCC-59602 | 400V MCC FOR ST #2 FOR BLOCK #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-MOV-13-409 | EDSV DRAIN L2 | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, L2, L3, PE | B259-006AT0006 → B259-006AT0005 → B259-006AT0014 → B259-006AT0025 → B259-006AT0015 → B259-006AT0016 → B259-006AT0017 → D0310-L22 → M0311 → D0311-L15 → M0312 → D0330-L14 → M0314 → B213-016BC0043 → END
B2-MCC-59601 | -P20 | 11 |  | PE-L1-4C4-25 | PE-L1-4C4-25 | STG-B2-046 |  |  | 1 | 183 | B2-MCC-59601-P2011 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-25 | 1.5 | 400 | N | 110 | STG | B2-MCC-59601 | 400V MCC FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-PCV-13-659 | EDCV SEALING GLAND | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, L2, L3, PE | B259-006AT0003 → B259-006AT0025 → D0325-L12 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0003 → B213-016AT0004 → B213-016AT0005 → B213-016AT0006 → B213-016AT0007 → B213-016BC0052 → END
B2-MCC-59602 | -P20 | 11 |  | PE-L1-4C4-25 | PE-L1-4C4-25 | STG-B2-047 |  |  | 1 | 184 | B2-MCC-59602-P2011 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-25 | 1.5 | 400 | N | 120 | STG | B2-MCC-59602 | 400V MCC FOR ST #2 FOR BLOCK #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-PCV-13-651 | EDCV REAR GLAND TO VACUUM FLASH TANK | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, L2, L3, PE | B259-006AT0006 → B259-006AT0005 → B259-006AT0014 → B259-006AT0025 → D0325-L12 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0003 → B213-016AT0004 → B213-016AT0005 → B213-016AT0006 → B213-016AT0007 → B213-016BC0053 → END
B2-MCC-59602 | -P20 | 12 |  | PE-L1-4C4-25 | PE-L1-4C4-25 | STG-B2-048 |  |  | 1 | 185 | B2-MCC-59602-P2012 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-25 | 1.5 | 400 | N | 110 | STG | B2-MCC-59602 | 400V MCC FOR ST #2 FOR BLOCK #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-PCV-13-601 | EDCV INNER GLD.STEAM | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, L2, L3, PE | B259-006AT0006 → B259-006AT0005 → B259-006AT0014 → B259-006AT0025 → D0325-L12 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0003 → B213-016AT0004 → B213-016AT0005 → B213-016AT0006 → B213-016AT0007 → B213-016BC0054 → END
B2-MCC-59602 | -P20 | 13 |  | PE-L1-4C4-18 | PE-L1-4C4-18 | STG-B2-048-001 |  |  | 1 | 186 | B2-MCC-59602-P2013 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-18 | 1.5 | 400 | N | 130 | STG | B2-MCC-59602 | 400V MCC FOR ST #2 FOR BLOCK #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-MOV-13-607 | EDSV DRAIN G1 | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, L2, L3, PE | B259-006AT0006 → B259-006AT0005 → B259-006AT0014 → B259-006AT0025 → B259-006AT0015 → B259-006AT0016 → B259-006AT0017 → D0310-L22 → M0311 → D0311-L15 → M0312 → D0330-L14 → M0314 → B213-016BC0045 → END
B2-MCC-59601 | -P20 | 12 |  | PE-L1-4C4-25 | PE-L1-4C4-25 | STG-B2-048-002 |  |  | 1 | 187 | B2-MCC-59601-P2012 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-25 | 1.5 | 400 | N | 130 | STG | B2-MCC-59601 | 400V MCC FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-LCV-13-501 | EDCV COND.MINIMAL FROM FLT TO COND. | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, L2, L3, PE | B259-006AT0003 → B259-006AT0025 → D0325-L12 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0003 → B213-016AT0004 → B213-016AT0005 → B213-016AT0006 → B213-016AT0007 → B213-016BC0055 → END
B2-MCC-59601 | -P20 | 13 |  | PE-L1-4C4-25 | PE-L1-4C4-25 | STG-B2-048-003 |  |  | 1 | 188 | B2-MCC-59601-P2013 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-25 | 1.5 | 400 | N | 120 | STG | B2-MCC-59601 | 400V MCC FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-FCV-13-531 | EDCV SPRAY.FLT | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, L2, L3, PE | B259-006AT0003 → B259-006AT0025 → D0325-L12 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0003 → B213-016AT0004 → B213-016AT0005 → B213-016AT0006 → B213-016AT0007 → B213-016BC0056 → END
B2-MCC-59601 | -P20 | 14 |  | PE-L1-4C4-18 | PE-L1-4C4-18 | STG-B2-048-004 |  |  | 1 | 189 | B2-MCC-59601-P2014 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-18 | 1.5 | 400 | N | 130 | STG | B2-MCC-59601 | 400V MCC FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-MOV-13-772 | EDSV SPRAY.1 STG OUTLET | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, L2, L3, PE | B259-006AT0003 → B259-006AT0025 → B259-006AT0014 → B259-006AT0015 → B259-006AT0016 → B259-006AT0017 → D0310-L21 → M0311 → D0311-L14 → M0312 → D0330-L15 → M0314 → B213-016BC0042 → END
B2-MCC-59602 | -P20 | 14 |  | PE-L1-4C4-18 | PE-L1-4C4-18 | STG-B2-048-005 |  |  | 1 | 190 | B2-MCC-59602-P2014 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-18 | 1.5 | 400 | N | 130 | STG | B2-MCC-59602 | 400V MCC FOR ST #2 FOR BLOCK #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-MOV-13-777 | EDSV SPRAY.2 STG OUTLET | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, L2, L3, PE | B259-006AT0006 → B259-006AT0005 → B259-006AT0014 → B259-006AT0025 → B259-006AT0015 → B259-006AT0016 → B259-006AT0017 → D0310-L22 → M0311 → D0311-L15 → M0312 → D0330-L14 → M0314 → B213-016BC0041 → END
B2-DCP-59702 | -P20 | 03 |  | PE-L1-2C6-02 | PE-L1-2C6-02 | STG-B2-049 |  |  | 1 | 191 | B2-DCP-59702-P2003 | 0.6/1kV CU/XLPE/LSZH | 2C x 6sqmm | PE-L1-2C6-02 | 2 | 220 | D | 30 | STG | B2-DCP-59702 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L+, L- | B2-TCS-1301A | TPS/TEC POWER SUPPLY (MAIN) | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L+, L- | B259-007AT0016 → B259-007AT0017 → B259-007AT0012 → END
B2-UPSP-59701 | -P20 | 01 |  | PE-L1-3C6-05 | PE-L1-3C6-05 | STG-B2-050 |  |  | 1 | 192 | B2-UPSP-59701-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-05 | 2 | 230 | U | 60 | STG | B2-UPSP-59701 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR STG #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B2-TCS-1301A | TPS/TEC POWER SUPPLY (BACK UP) | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B259-006BT0003 → B259-006BT0019 → B259-006BT0006 → B259-006BT0018 → B259-006BT0010 → B259-006BT0022 → B259-006BT0023 → B259-006BT0012 → END
B2-DB-59601 | -P20 | 06 |  | PE-L1-3C4-11 | PE-L1-3C4-11 | STG-B2-051 |  |  | 1 | 193 | B2-DB-59601-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-11 | 0.2 | 230 | N | 60 | STG | B2-DB-59601 | 400V-230V DIST. BOARD FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B2-TCS-1301A | TPS/TCS POWER SUPPLY (AUX. POWER) | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B259-006BT0003 → B259-006BT0019 → B259-006BT0006 → B259-006BT0018 → B259-006BT0010 → B259-006BT0022 → B259-006BT0023 → B259-006BT0012 → END
B2-DCP-59701 | -P20 | 03 |  | PE-L1-2C4-04 | PE-L1-2C4-04 | STG-B2-052 |  |  | 1 | 194 | B2-DCP-59701-P2003 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-04 | 0.7 | 220 | D | 30 | STG | B2-DCP-59701 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L+, L- | B2-TCS-1311 | TPC POWER SUPPLY (MAIN) | 1.1_MAIN BUILDING COMPLEX / EXCITATION ROOM | L+, L- | B259-007AT0014 → B259-007AT0015 → B259-007AT0016 → B259-007AT0011 → END
B2-UPSP-59701 | -P20 | 02 |  | PE-L1-3C4-29 | PE-L1-3C4-29 | STG-B2-053 |  |  | 1 | 195 | B2-UPSP-59701-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-29 | 0.7 | 230 | U | 50 | STG | B2-UPSP-59701 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR STG #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B2-TCS-1311 | TPC POWER SUPPLY (BACK UP) | 1.1_MAIN BUILDING COMPLEX / EXCITATION ROOM | L1, N, PE | B259-006BT0003 → B259-006BT0019 → B259-006BT0006 → B259-006BT0018 → B259-006BT0010 → B259-006BT0022 → B259-006BT0011 → END
B2-DB-59602 | -P20 | 03 |  | PE-L1-3C4-28 | PE-L1-3C4-28 | STG-B2-054 |  |  | 1 | 196 | B2-DB-59602-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-28 | 1 | 230 | N | 30 | STG | B2-DB-59602 | 400V-230V DIST. BOARD FOR ST #2 FOR BLOCK #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B2-TCS-1311 | TPC POWER SUPPLY (AUX. POWER) | 1.1_MAIN BUILDING COMPLEX / EXCITATION ROOM | L1, N, PE | B259-006BT0018 → B259-006BT0010 → B259-006BT0022 → B259-006BT0011 → END
B2-DCP-59701 | -P20 | 04 |  | PE-L1-2C4-04 | PE-L1-2C4-04 | STG-B2-055 |  |  | 1 | 197 | B2-DCP-59701-P2004 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-04 | 0.6 | 220 | D | 30 | STG | B2-DCP-59701 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L+, L- | B2-TCS-1321 | VMS POWER SUPPLY (MAIN) | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L+, L- | B259-007AT0014 → B259-007AT0015 → B259-007AT0016 → B259-007AT0011 → END
B2-UPSP-59702 | -P20 | 03 |  | PE-L1-3C4-28 | PE-L1-3C4-28 | STG-B2-056 |  |  | 1 | 198 | B2-UPSP-59702-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-28 | 0.6 | 230 | U | 50 | STG | B2-UPSP-59702 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR STG #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B2-TCS-1321 | VMS POWER SUPPLY (BACK UP) | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B259-006BT0003 → B259-006BT0019 → B259-006BT0006 → B259-006BT0018 → B259-006BT0010 → B259-006BT0022 → B259-006BT0011 → END
B2-DB-59601 | -P20 | 07 |  | PE-L1-3C4-28 | PE-L1-3C4-28 | STG-B2-057 |  |  | 1 | 199 | B2-DB-59601-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-28 | 0.6 | 230 | N | 50 | STG | B2-DB-59601 | 400V-230V DIST. BOARD FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B2-TCS-1321 | VMS POWER SUPPLY (AUX. POWER) | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B259-006BT0003 → B259-006BT0019 → B259-006BT0006 → B259-006BT0018 → B259-006BT0010 → B259-006BT0022 → B259-006BT0011 → END
B2-DCP-59701 | -P20 | 05 |  | PE-L1-2C4-04 | PE-L1-2C4-04 | STG-B2-058 |  |  | 1 | 200 | B2-DCP-59701-P2005 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-04 | 0.5 | 220 | D | 40 | STG | B2-DCP-59701 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L+, L- | B2-PRP-13701 | GEN. PROTECTION PANEL (MAIN) | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L+, L- | B259-007AT0006 → B259-007AT0007 → B259-007AT0009 → B259-007AT0021 → B259-007AT0010 → END
B2-DCP-59702 | -P20 | 04 |  | PE-L1-2C4-04 | PE-L1-2C4-04 | STG-B2-059 |  |  | 1 | 201 | B2-DCP-59702-P2004 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-04 | 0.5 | 220 | D | 40 | STG | B2-DCP-59702 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L+, L- | B2-PRP-13701 | GEN. PROTECTION PANEL (BACK UP) | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L+, L- | B259-006BT0005 → B259-006BT0018 → B259-006BT0010 → B259-006BT0022 → B259-006BT0023 → B259-006BT0012 → END
B2-DB-59602 | -P20 | 04 |  | PE-L1-3C4-28 | PE-L1-3C4-28 | STG-B2-060 |  |  | 1 | 202 | B2-DB-59602-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-28 | 2 | 230 | N | 40 | STG | B2-DB-59602 | 400V-230V DIST. BOARD FOR ST #2 FOR BLOCK #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B2-PRP-13701 | GEN. PROTECTION PANEL (AUX. POWER) | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B259-006BT0018 → B259-006BT0010 → B259-006BT0022 → B259-006BT0023 → B259-006BT0012 → END
B2-DCP-59702 | -P20 | 05 |  | PE-L1-2C4-04 | PE-L1-2C4-04 | STG-B2-061 |  |  | 1 | 203 | B2-DCP-59702-P2005 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-04 | 0.5 | 220 | D | 40 | STG | B2-DCP-59702 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L+, L- | B2-CP-13701 | GEN. AVR, SYNCH. AND MEAS. PANEL (MAIN) | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L+, L- | B259-007AT0006 → B259-007AT0007 → B259-007AT0009 → B259-007AT0021 → B259-007AT0010 → END
B2-DCP-59701 | -P20 | 06 |  | PE-L1-2C4-04 | PE-L1-2C4-04 | STG-B2-062 |  |  | 1 | 204 | B2-DCP-59701-P2006 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-04 | 0.5 | 220 | D | 40 | STG | B2-DCP-59701 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L+, L- | B2-CP-13701 | GEN. AVR, SYNCH. AND MEAS. PANEL (BACK BUP) | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L+, L- | B259-006BT0005 → B259-006BT0018 → B259-006BT0010 → B259-006BT0022 → B259-006BT0023 → B259-006BT0012 → END
B2-DB-59601 | -P20 | 08 |  | PE-L1-3C4-28 | PE-L1-3C4-28 | STG-B2-063 |  |  | 1 | 205 | B2-DB-59601-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-28 | 2 | 230 | N | 60 | STG | B2-DB-59601 | 400V-230V DIST. BOARD FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B2-CP-13701 | GEN. AVR, SYNCH. AND MEAS. PANEL (AUX. POWER) | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B259-006BT0003 → B259-006BT0019 → B259-006BT0006 → B259-006BT0018 → B259-006BT0010 → B259-006BT0022 → B259-006BT0023 → B259-006BT0012 → END
B2-DCP-59702 | -P20 | 06 |  | PE-L1-2C4-04 | PE-L1-2C4-04 | STG-B2-064 |  |  | 1 | 206 | B2-DCP-59702-P2006 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-04 | 0.5 | 220 | D | 40 | STG | B2-DCP-59702 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L+, L- | B2-CP-13501 | GEN EXCITATION PANEL (MAIN) | 1.1_MAIN BUILDING COMPLEX / EXCITATION ROOM | L+, L- | B259-006AT0005 → B259-006AT0006 → B259-006AT0019 → B213-007CC0001 → END
B2-DCP-59701 | -P20 | 07 |  | PE-L1-2C4-06 | PE-L1-2C4-06 | STG-B2-065 |  |  | 1 | 207 | B2-DCP-59701-P2007 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-06 | 0.5 | 220 | D | 40 | STG | B2-DCP-59701 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L+, L- | B2-CP-13501 | GEN EXCITATION PANEL (BACK UP) | 1.1_MAIN BUILDING COMPLEX / EXCITATION ROOM | L+, L- | B259-006BT0005 → B259-006BT0006 → B259-006BT0019 → B213-007CC0002 → END
B2-MCC-59602 | -P20 | 15 |  | PE-L1-5C4-03 | PE-L1-5C4-03 | STG-B2-066 |  |  | 1 | 208 | B2-MCC-59602-P2015 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-03 | 2 | 400 | N | 40 | STG | B2-MCC-59602 | 400V MCC FOR ST #2 FOR BLOCK #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, N, PE | B2-CP-13501 | GEN EXCITATION PANEL (AUX. POWER) | 1.1_MAIN BUILDING COMPLEX / EXCITATION ROOM | L1, L2, L3, N, PE | B259-006BT0006 → B259-006BT0019 → B213-006CC0005 → END
B2-DB-59601 | -P20 | 09 | From변경 | PE-L1-3C10-02 | PE-L1-3C10-02 | STG-B2-066-002 | B2-DB-59601-P2009 |  | 1 | 209 | B2-DB-59602-P2009 | 0.6/1kV CU/XLPE/LSZH | 3C x 10sqmm | PE-L1-3C10-02 | 2 | 230 | N | 90 | STG | B2-DB-59602 | 400V-230V DIST. BOARD FOR ST #2 FOR BLOCK #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B2-JB-13730 | EXCIT.TRANSF.POWER SUPPLY- A | 1.1_MAIN BUILDING COMPLEX / EXCITATION TR ROOM | L1, N, PE | B259-006AT0006 → B259-006AT0005 → B259-006AT0015 → B259-006AT0016 → B259-006AT0017 → D0310-L25 → M0311 → D0311-L15 → M0312 → B213-007CC0006 → END
B2-UPSP-59702 | -P20 | 01 |  | PE-L1-3C10-02 | PE-L1-3C10-02 | STG-B2-066-003 |  |  | 1 | 210 | B2-UPSP-59702-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 10sqmm | PE-L1-3C10-02 | 2 | 230 | U | 110 | STG | B2-UPSP-59702 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR STG #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B2-JB-13730 | EXCIT.TRANSF.POWER SUPPLY- B | 1.1_MAIN BUILDING COMPLEX / EXCITATION TR ROOM | L1, N, PE | B259-006BT0003 → B259-006BT0019 → B259-006BT0006 → B259-006BT0018 → B259-006BT0010 → B259-006BT0022 → B259-006BT0023 → B259-006BT0024 → B259-006BT0013 → D0310-L26 → M0311 → D0311-L16 → M0312 → B213-007CC0006 → END
B2-UPSP-73701 | -P20 | 04 | Drum재배정 | PE-L1-3C4-16 | PE-L1-3C4-05 | STG-B2-067-001 |  |  | 1 | 211 | B2-UPSP-73701-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-05 | 2 | 230 | U | 30 | STG | B2-UPSP-73701 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ADMIN. - BLOCK#2 - A | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B2-TCS-1320 | TCS SERVER(TLCS) CABINET (MAIN) | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / SERVER ROOM | L1, N, PE | B073-017AT0013 → B073-017AT0015 → B073-017AT0011 → END
B2-UPSP-73702 | -P20 | 04 |  | PE-L1-3C4-16 | PE-L1-3C4-16 | STG-B2-067-003 |  |  | 1 | 212 | B2-UPSP-73702-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-16 | 2 | 230 | U | 30 | STG | B2-UPSP-73702 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ADMIN. - BLOCK#2 - B | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B2-TCS-1320 | TCS SERVER(TLCS) CABINET (BACK UP) | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / SERVER ROOM | L1, N, PE | B073-016AT0013 → B073-016AT0015 → B073-016AT0011 → END
B2-UPSP-73701 | -P20 | 01 |  | PE-L1-3C4-26 | PE-L1-3C4-26 | STG-B2-070-001 |  |  | 1 | 213 | B2-UPSP-73701-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-26 | 0.5 | 230 | U | 70 | STG | B2-UPSP-73701 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ADMIN. - BLOCK#2 - A | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B2-TCS-1310S | HIS.SERVER POWER SUPPLY-A | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / SERVER ROOM | L1, N, PE | FIELD RUN
B2-UPSP-73702 | -P20 | 01 |  | PE-L1-3C4-26 | PE-L1-3C4-26 | STG-B2-070-002 |  |  | 1 | 214 | B2-UPSP-73702-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-26 | 2 | 230 | U | 70 | STG | B2-UPSP-73702 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ADMIN. - BLOCK#2 - B | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B2-TCS-1300A | FOPP POWER SUPPLY | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / SERVER ROOM | L1, N, PE | FIELD RUN
B2-DCP-59702 | -P20 | 07 |  | PE-L1-2C4-06 | PE-L1-2C4-06 | STG-B2-071 |  |  | 1 | 215 | B2-DCP-59702-P2007 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-06 | 1 | 220 | D | 120 | STG | B2-DCP-59702 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L+, L- | B2-JBX-1302 | JB EWV | 1.1_MAIN BUILDING COMPLEX / STG #2 | L+, L- | B259-006BT0005 → B259-006BT0006 → B259-006BT0019 → B259-006BT0001 → D0325-L15 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0003 → B213-016AT0004 → B213-016AT0005 → B213-016AT0006 → B213-016AT0007 → B213-016BC0027 → END
B2-DB-59602 | -P20 | 05 |  | PE-L1-3C4-16 | PE-L1-3C4-16 | STG-B2-072 |  |  | 1 | 216 | B2-DB-59602-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-16 | 1 | 230 | N | 70 | STG | B2-DB-59602 | 400V-230V DIST. BOARD FOR ST #2 FOR BLOCK #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B2-JB-13701 | JB GENERATOR COLLECTOR HOUSING | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, N, PE | B259-006AT0006 → B259-006AT0005 → B259-006AT0014 → B259-006AT0025 → D0325-L21 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0003 → B213-017BC0002 → END
B1-MCC-64602 | -P20 | 01 |  | PE-L1-4C10-01 | PE-L1-4C10-01 | HRSG-U1-001 |  |  | 1 | 217 | B1-MCC-64602-P2001 | 0.6/1kV CU/XLPE/LSZH | 4C x 10sqmm | PE-L1-4C10-01 | 15 | 400 | N | 175 | HRSG | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-P-14011A | HRSG #11 FW RECIRCULATION PUMP A - MOTOR | 1.1_MAIN BUILDING COMPLEX / HRSG #11 | L1, L2, L3, PE | B164-016ET0106 → B164-996ET0022 → M0504 → D0531-L24 → M0510 → D0517-L14 → M0501 → D0503-L35 → M0502 → D0504-L35 → M0503 → D0501-L35 → M0328 → B161-006AC0009 → END
B1-MCC-64601 | -P20 | 01 |  | PE-L1-4C10-01 | PE-L1-4C10-01 | HRSG-U1-002 |  |  | 1 | 218 | B1-MCC-64601-P2001 | 0.6/1kV CU/XLPE/LSZH | 4C x 10sqmm | PE-L1-4C10-01 | 15 | 400 | N | 170 | HRSG | B1-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-P-14011B | HRSG #11 FW RECIRCULATION PUMP B - MOTOR | 1.1_MAIN BUILDING COMPLEX / HRSG #11 | L1, L2, L3, PE | B164-016CT0098 → B164-016CT0099 → B164-996CT0022 → M0504 → D0531-L25 → M0510 → D0517-L15 → M0501 → D0503-L36 → M0502 → D0504-L36 → M0503 → D0501-L36 → M0328 → B161-006AC0008 → END
B1-MCC-64601 | -P20 | 02 |  | PE-L1-4C4-06 | PE-L1-4C4-06 | HRSG-U1-005 |  |  | 1 | 219 | B1-MCC-64601-P2002 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-06 | 3.2 | 400 | N | 180 | HRSG | B1-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-P-14012A | HRSG #11 ABD EXTRACTION PUMP A - MOTOR | 1.1_MAIN BUILDING COMPLEX / HRSG #11 | L1, L2, L3, PE | B164-016CT0098 → B164-016CT0099 → B164-996CT0022 → M0504 → D0531-L24 → M0510 → D0517-L14 → M0501 → D0503-L35 → M0502 → D0504-L35 → M0503 → D0501-L35 → M0328 → D0324-L35 → M0329 → B161-016AC0020 → END
B1-MCC-64602 | -P20 | 02 |  | PE-L1-4C4-02 | PE-L1-4C4-02 | HRSG-U1-006 |  |  | 1 | 220 | B1-MCC-64602-P2002 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-02 | 3.2 | 400 | N | 180 | HRSG | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-P-14012B | HRSG #11 ABD EXTRACTION PUMP B - MOTOR | 1.1_MAIN BUILDING COMPLEX / HRSG #11 | L1, L2, L3, PE | B164-016ET0106 → B164-996ET0022 → M0504 → D0531-L25 → M0510 → D0517-L15 → M0501 → D0503-L36 → M0502 → D0504-L36 → M0503 → D0501-L36 → M0328 → D0324-L36 → M0329 → B161-016AC0021 → END
B1-MCC-64602 | -P20 | 03 |  | PE-L1-5C95/50-01 | PE-L1-5C95/50-01 | HRSG-U1-007 |  |  | 1 | 221 | B1-MCC-64602-P2003 | 0.6/1kV CU/XLPE/LSZH | 4C x 95sqmm + 1C X 50sqmm | PE-L1-5C95/50-01 | 50 | 400 | N | 290 | HRSG | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B1-PDP-1401 | HRSG #11 LV PANEL DISTRIBUTION BOARD | 1.1_MAIN BUILDING COMPLEX / HRSG #11 | L1, L2, L3, N, PE | B164-016ET0106 → B164-996ET0022 → M0504 → D0531-L26 → M0510 → D0517-L25 → M0501 → D0503-L37 → M0502 → D0504-L37 → M0503 → D0501-L37 → M0328 → D0324-L37 → M0329 → B114-996DT0081 → B114-016DT0082 → B114-016DT0083 → B114-016DT0084 → B114-016DT0096 → B114-016DT0097 → B114-016DT0100 → B161-016AC0003 → END
B1-UPSP-64701 | -P20 | 02 |  | PE-L1-3C150/95-01 | PE-L1-3C150/95-01 | HRSG-U1-011 | DONE(9/28) | DONE | 1 | 222 | B1-UPSP-64701-P2002 | 0.6/1kV CU/XLPE/LSZH | 2C x 150sqmm + 1C X 95sqmm | PE-L1-3C150/95-01 | 10 | 230 | U | 260 | HRSG | B1-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-UPSP-1401A | HRSG #11 UPS DISTRIBUTION BOARD (MAIN) | 1.1_MAIN BUILDING COMPLEX / HRSG #11 | L1, N, PE | B164-006HT0202 → B164-006HT0201 → B164-006HT0001 → B164-006HT0002 → B164-006HT0003 → B064-006AC0001 → M0501 → D0503-L38 → M0502 → D0504-L38 → M0503 → D0501-L38 → M0328 → D0324-L38 → M0329 → B114-996DT0081 → B114-016DT0082 → B114-016DT0083 → B114-016DT0084 → B114-016DT0096 → B114-016DT0097 → B114-016DT0100 → B161-017AC0005 → END
B1-UPSP-64702 | -P20 | 02 |  | PE-L1-3C150/95-01 | PE-L1-3C150/95-01 | HRSG-U1-011-001 |  |  | 1 | 223 | B1-UPSP-64702-P2002 | 0.6/1kV CU/XLPE/LSZH | 2C x 150sqmm + 1C X 95sqmm | PE-L1-3C150/95-01 | 10 | 230 | U | 260 | HRSG | B1-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-UPSP-1401B | HRSG #11 UPS DISTRIBUTION BOARD (BACK UP) | 1.1_MAIN BUILDING COMPLEX / HRSG #11 | L1, N, PE | B164-006HT0202 → B164-006HT0007 → B164-006HT0008 → B164-006HT0009 → B164-006HT0208 → B164-006HT0207 → B164-006HT0005 → B064-006AC0002 → M0501 → D0503-L41 → M0502 → D0504-L41 → M0503 → D0501-L41 → M0328 → D0324-L41 → M0329 → B114-997BT0046 → B114-017BT0045 → B114-017BT0044 → B114-017BT0043 → B161-017AC0006 → END
1.1_MAIN BUILDING COMPLEX / HRSG #11 | -P20 | 36 | From변경 | PE-L1-5C95/50-02 | PE-L1-5C95/50-02 | HRSG-U1-013 | B1-MCC-64602-P2004 |  | 1 | 224 | B1-MCC-64601-P2036 | 0.6/1kV CU/XLPE/LSZH | 4C x 95sqmm + 1C X 50sqmm | PE-L1-5C95/50-02 | 50 | 400 | N | 220 | HRSG | B1-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B1-PC-1404 | HRSG #11 HPU POWER DISTRIBUTION | 1.1_MAIN BUILDING COMPLEX / HRSG #11 | L1, L2, L3, N, PE | B164-016CT0098 → B164-016CT0099 → B164-996CT0022 → M0504 → D0531-L27 → M0510 → D0517-L26 → M0501 → D0503-L47 → M0502 → D0504-L47 → M0503 → D0501-L47 → M0328 → D0324-L47 → M0329 → B161-006AC0010 → B161-006AC0011 → END
B1-MCC-64601 | -P20 | 03 |  | PE-L1-4C4-26 | PE-L1-4C4-26 | HRSG-U1-016 |  |  | 1 | 225 | B1-MCC-64601-P2003 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-26 | 1.8 | 400 | N | 280 | HRSG | B1-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-14010 | HRSG #11 HP MAIN STEAM STOP VALVE - MOV | 1.1_MAIN BUILDING COMPLEX / HRSG #11 | L1, L2, L3, PE | B164-016CT0098 → B164-016CT0099 → B164-996CT0022 → M0504 → D0531-L24 → M0510 → D0517-L14 → M0501 → D0503-L35 → M0502 → D0504-L35 → M0503 → D0501-L35 → M0328 → D0324-L35 → M0329 → B114-996DT0081 → B114-016DT0082 → B114-016DT0083 → B114-016DT0084 → B114-016DT0096 → B114-016DT0097 → B161-016AC0005 → END
B1-MCC-64602 | -P20 | 05 |  | PE-L1-4C4-02 | PE-L1-4C4-02 | HRSG-U1-017 |  |  | 1 | 226 | B1-MCC-64602-P2005 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-02 | 1 | 400 | N | 280 | HRSG | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-14019 | HRSG #11 LP MAIN STEAM STOP VALVE - MOV | 1.1_MAIN BUILDING COMPLEX / HRSG #11 | L1, L2, L3, PE | B164-016ET0106 → B164-996ET0022 → M0504 → D0531-L26 → M0510 → D0517-L15 → M0501 → D0503-L37 → M0502 → D0504-L37 → M0503 → D0501-L37 → M0328 → D0324-L37 → M0329 → B114-996DT0081 → B114-016DT0082 → B114-016DT0083 → B114-016DT0084 → B114-016DT0096 → B114-016DT0097 → B161-016AC0006 → END
B1-MCC-64602 | -P20 | 06 |  | PE-L1-4C4-26 | PE-L1-4C4-26 | HRSG-U1-018 |  |  | 1 | 227 | B1-MCC-64602-P2006 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-26 | 0.1 | 380 | N | 280 | HRSG | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-14011 | HRSG #11 HP MAIN STEAM STOP BYPASS VALVE - MOV | 1.1_MAIN BUILDING COMPLEX / HRSG #11 | L1, L2, L3, PE | B164-016ET0106 → B164-996ET0022 → M0504 → D0531-L25 → M0510 → D0517-L15 → M0501 → D0503-L36 → M0502 → D0504-L36 → M0503 → D0501-L36 → M0328 → D0324-L36 → M0329 → B114-996DT0081 → B114-016DT0082 → B114-016DT0083 → B114-016DT0084 → B114-016DT0096 → B114-016DT0097 → B161-016AC0024 → END
B1-MCC-64604 | -P20 | 01 | From변경 | PE-L1-4C25/16-01 | PE-L1-4C25/16-01 | HRSG-U2-001 | B1-MCC-64604-P2001 |  | 1 | 228 | B1-MCC-64603-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 25sqmm + 1C X 16sqmm | PE-L1-4C25/16-01 | 15 | 400 | N | 360 | HRSG | B1-MCC-64603 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-P-15011A | HRSG #12 FW RECIRCULATION PUMP A - MOTOR | 1.1_MAIN BUILDING COMPLEX / HRSG #12 | L1, L2, L3, PE | B164-016BT0103 → B164-016BT0102 → B164-016BT0101 → B164-016BT0100 → B164-996BT0024 → M0504 → D0531-L26 → M0510 → D0517-L15 → M0501 → D0503-L37 → M0502 → D0504-L37 → M0503 → D0501-L37 → M0328 → D0324-L37 → M0329 → B114-996BT0046 → B114-016BT0045 → B114-016BT0044 → B114-016BT0043 → B114-016BT0042 → B114-016BT0041 → B161-016CC0018 → B161-006CC0009 → END
B1-MCC-64603 | -P20 | 01 | From변경 | PE-L1-4C25/16-01 | PE-L1-4C25/16-01 | HRSG-U2-002 | B1-MCC-64603-P2001 |  | 1 | 229 | B1-MCC-64604-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 25sqmm + 1C X 16sqmm | PE-L1-4C25/16-01 | 15 | 400 | N | 350 | HRSG | B1-MCC-64604 | 400V MCC FOR GT/HRSG#2 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-P-15011B | HRSG #12 FW RECIRCULATION PUMP B - MOTOR | 1.1_MAIN BUILDING COMPLEX / HRSG #12 | L1, L2, L3, PE | B164-016AT0118 → B164-016AT0117 → B164-016AT0116 → B164-996AT0023 → M0504 → D0531-L27 → M0510 → D0517-L21 → M0501 → D0503-L38 → M0502 → D0504-L38 → M0503 → D0501-L38 → M0328 → D0324-L38 → M0329 → B114-996CT0071 → B114-016CT0072 → B114-016CT0073 → B114-016CT0074 → B114-016CT0075 → B114-016CT0076 → B161-016CC0017 → B161-006CC0008 → END
B1-MCC-64603 | -P20 | 02 |  | PE-L1-4C4-02 | PE-L1-4C4-02 | HRSG-U2-005 |  | DONE | 1 | 230 | B1-MCC-64603-P2002 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-02 | 3.2 | 400 | N | 330 | HRSG | B1-MCC-64603 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-P-15012A | HRSG #12 ABD EXTRACTION PUMP A - MOTOR | 1.1_MAIN BUILDING COMPLEX / HRSG #12 | L1, L2, L3, PE | B164-016BT0103 → B164-016BT0102 → B164-016BT0101 → B164-016BT0100 → B164-996BT0024 → M0504 → D0531-L26 → M0510 → D0517-L16 → M0501 → D0503-L37 → M0502 → D0504-L37 → M0503 → D0501-L37 → M0328 → D0324-L37 → M0329 → B114-996BT0046 → B114-016BT0045 → B114-016BT0044 → B114-016BT0043 → B114-016BT0042 → B114-016BT0041 → B161-006CC0006 → B161-006CC0006 → B161-016CC0022 → B161-016CC0023 → END
B1-MCC-64604 | -P20 | 02 |  | PE-L1-4C4-02 | PE-L1-4C4-02 | HRSG-U2-006 |  | DONE | 1 | 231 | B1-MCC-64604-P2002 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-02 | 3.2 | 400 | N | 330 | HRSG | B1-MCC-64604 | 400V MCC FOR GT/HRSG#2 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-P-15012B | HRSG #12 ABD EXTRACTION PUMP B - MOTOR | 1.1_MAIN BUILDING COMPLEX / HRSG #12 | L1, L2, L3, PE | B164-016AT0118 → B164-016AT0117 → B164-016AT0116 → B164-996AT0023 → M0504 → D0531-L27 → M0510 → D0517-L21 → M0501 → D0503-L38 → M0502 → D0504-L38 → M0503 → D0501-L38 → M0328 → D0324-L38 → M0329 → B114-996CT0071 → B114-016CT0072 → B114-016CT0073 → B114-016CT0074 → B114-016CT0075 → B114-016CT0076 → B161-016CC0026 → B161-006CC0007 → B161-016CC0025 → B161-016CC0024 → END
B1-MCC-64604 | -P20 | 03 |  | PE-L1-5C95/50-02 | PE-L1-5C95/50-02 | HRSG-U2-007 |  |  | 1 | 232 | B1-MCC-64604-P2003 | 0.6/1kV CU/XLPE/LSZH | 4C x 95sqmm + 1C X 50sqmm | PE-L1-5C95/50-02 | 50 | 400 | N | 360 | HRSG | B1-MCC-64604 | 400V MCC FOR GT/HRSG#2 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B1-PDP-1501 | HRSG #12 LV PANEL DISTRIBUTION BOARD | 1.1_MAIN BUILDING COMPLEX / HRSG #12 | L1, L2, L3, N, PE | B164-016DT0109 → B164-016DT0108 → B164-016DT0107 → B164-996DT0024 → M0504 → D0531-L36 → M0510 → D0517-L31 → M0501 → D0503-L45 → M0502 → D0504-L45 → M0503 → D0501-L47 → M0328 → D0324-L47 → M0329 → B114-996CT0071 → B114-016CT0072 → B114-016CT0073 → B114-016CT0074 → B114-016CT0075 → B114-016CT0076 → B114-016CT0087 → B114-016CT0088 → B114-016CT0091 → B161-016CC0003 → END
B1-UPSP-64702 | -P20 | 03 |  | PE-L1-3C150/95-02 | PE-L1-3C150/95-02 | HRSG-U2-011 |  |  | 1 | 233 | B1-UPSP-64702-P2003 | 0.6/1kV CU/XLPE/LSZH | 2C x 150sqmm + 1C X 95sqmm | PE-L1-3C150/95-02 | 10 | 230 | U | 330 | HRSG | B1-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-UPSP-1501A | HRSG #12 UPS DISTRIBUTION BOARD (MAIN) | 1.1_MAIN BUILDING COMPLEX / HRSG #12 | L1, N, PE | B164-006GT0202 → B164-006GT0007 → B164-006GT0008 → B164-006GT0009 → B164-006GT0208 → B164-006GT0207 → B164-006GT0005 → B064-006AC0001 → M0501 → D0503-L38 → M0502 → D0504-L38 → M0503 → D0501-L38 → M0328 → D0324-L38 → M0329 → B114-996CT0071 → B114-016CT0072 → B114-016CT0073 → B114-016CT0074 → B114-016CT0075 → B114-016CT0076 → B114-016CT0087 → B114-016CT0088 → B114-016CT0091 → B161-017CC0005 → END
B1-UPSP-64701 | -P20 | 03 |  | PE-L1-3C150/95-02 | PE-L1-3C150/95-02 | HRSG-U2-011-001 |  |  | 1 | 234 | B1-UPSP-64701-P2003 | 0.6/1kV CU/XLPE/LSZH | 2C x 150sqmm + 1C X 95sqmm | PE-L1-3C150/95-02 | 10 | 230 | U | 300 | HRSG | B1-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-UPSP-1501B | HRSG #12 UPS DISTRIBUTION BOARD (BACK UP) | 1.1_MAIN BUILDING COMPLEX / HRSG #12 | L1, N, PE | B164-006HT0202 → B164-006HT0201 → B164-006HT0001 → B164-006HT0002 → B164-006HT0003 → B064-006AC0002 → M0501 → D0503-L37 → M0502 → D0504-L37 → M0503 → D0501-L37 → M0328 → D0324-L37 → M0329 → B114-996BT0046 → B114-016BT0045 → B114-016BT0044 → B114-016BT0043 → B114-016BT0042 → B114-016BT0041 → B161-017CC0006 → END
B1-MCC-64603 | -P20 | 03 | 재배정(10/6) | PE-L1-5C120/70-02 | PE-L1-5C120/70-05 | HRSG-U2-013 |  |  | 1 | 235 | B1-MCC-64603-P2003 | 0.6/1kV CU/XLPE/LSZH | 4C x 120sqmm + 1C X 70sqmm | PE-L1-5C120/70-05 | 50 | 400 | N | 360 | HRSG | B1-MCC-64603 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B1-PC-1504 | HRSG #12 HPU POWER DISTRIBUTION | 1.1_MAIN BUILDING COMPLEX / HRSG #12 | L1, L2, L3, N, PE | B164-016AT0094 → B164-016AT0093 → B164-016AT0092 → B164-996AT0022 → M0504 → D0531-L33 → M0510 → D0517-L15 → M0501 → D0503-L44 → M0502 → D0504-L44 → M0503 → D0501-L48 → M0328 → D0324-L48 → M0329 → B114-996CT0071 → B114-016CT0072 → B114-016CT0073 → B114-016CT0074 → B114-016CT0075 → B161-016CC0019 → B161-006CC0010 → B161-006CC0011 → END
B1-MCC-64603 | -P20 | 04 |  | PE-L1-4C4-02 | PE-L1-4C4-02 | HRSG-U2-016 |  |  | 1 | 236 | B1-MCC-64603-P2004 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-02 | 1.8 | 400 | N | 340 | HRSG | B1-MCC-64603 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-15010 | HRSG #12 HP MAIN STEAM STOP VALVE - MOV | 1.1_MAIN BUILDING COMPLEX / HRSG #12 | L1, L2, L3, PE | B164-016AT0094 → B164-016AT0093 → B164-016AT0092 → B164-996AT0022 → M0504 → D0531-L26 → M0510 → D0517-L16 → M0501 → D0503-L37 → M0502 → D0504-L37 → M0503 → D0501-L37 → M0328 → D0324-L37 → M0329 → B114-996CT0071 → B114-016CT0072 → B114-016CT0073 → B114-016CT0074 → B114-016CT0075 → B114-016CT0076 → B114-016CT0087 → B161-016CC0033 → END
B1-MCC-64604 | -P20 | 04 |  | PE-L1-4C4-03 | PE-L1-4C4-03 | HRSG-U2-017 | DONE(10/6) | DONE | 1 | 237 | B1-MCC-64604-P2004 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-03 | 1 | 400 | N | 330 | HRSG | B1-MCC-64604 | 400V MCC FOR GT/HRSG#2 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-15019 | HRSG #12 LP MAIN STEAM STOP VALVE - MOV | 1.1_MAIN BUILDING COMPLEX / HRSG #12 | L1, L2, L3, PE | B164-016AT0118 → B164-016AT0117 → B164-016AT0116 → B164-996AT0023 → M0504 → D0531-L27 → M0510 → D0517-L21 → M0501 → D0503-L38 → M0502 → D0504-L38 → M0503 → D0501-L38 → M0328 → D0324-L38 → M0329 → B114-996CT0071 → B114-016CT0072 → B114-016CT0073 → B114-016CT0074 → B114-016CT0075 → B114-016CT0076 → B114-016CT0087 → B161-016CC0032 → END
B1-MCC-64603 | -P20 | 05 |  | PE-L1-4C4-03 | PE-L1-4C4-03 | HRSG-U2-018 | DONE(10/6) | DONE | 1 | 238 | B1-MCC-64603-P2005 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-03 | 0.1 | 380 | N | 340 | HRSG | B1-MCC-64603 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-15011 | HRSG #12 HP MAIN STEAM STOP BYPASS VALVE - MOV | 1.1_MAIN BUILDING COMPLEX / HRSG #12 | L1, L2, L3, PE | B164-016AT0094 → B164-016AT0093 → B164-016AT0092 → B164-996AT0022 → M0504 → D0531-L26 → M0510 → D0517-L16 → M0501 → D0503-L37 → M0502 → D0504-L37 → M0503 → D0501-L37 → M0328 → D0324-L37 → M0329 → B114-996CT0071 → B114-016CT0072 → B114-016CT0073 → B114-016CT0074 → B114-016CT0075 → B114-016CT0076 → B114-016CT0087 → B161-016CC0034 → END
B2-MCC-64602 | -P20 | 01 |  | PE-L1-4C25/16-03 | PE-L1-4C25/16-03 | HRSG-U3-001 |  |  | 1 | 239 | B2-MCC-64602-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 25sqmm + 1C X 16sqmm | PE-L1-4C25/16-03 | 15 | 400 | N | 370 | HRSG | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-P-14011A | HRSG #21 FW RECIRCULATION PUMP A - MOTOR | 1.1_MAIN BUILDING COMPLEX / HRSG #21 | L1, L2, L3, PE | B264-016AT0045 → B264-016AT0046 → B264-016AT0209 → B264-016AT0026 → B264-016AT0027 → B264-016AT0225 → B264-996AT0011 → M0405 → D0421-L26 → M0406 → D0301-L22 → M0301 → B215-997AT0026 → B215-017AT0027 → B215-017AT0028 → B215-017AT0029 → B215-017AT0030 → B215-017AT0006 → B215-017AT0007 → B215-017AT0008 → B215-017AT0009 → B261-016CC0027 → B261-006CC0009 → END
B2-MCC-64601 | -P20 | 01 |  | PE-L1-4C25/16-03 | PE-L1-4C25/16-03 | HRSG-U3-002 |  |  | 1 | 240 | B2-MCC-64601-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 25sqmm + 1C X 16sqmm | PE-L1-4C25/16-03 | 15 | 400 | N | 360 | HRSG | B2-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-P-14011B | HRSG #21 FW RECIRCULATION PUMP B - MOTOR | 1.1_MAIN BUILDING COMPLEX / HRSG #21 | L1, L2, L3, PE | B264-016CT0024 → B264-016CT0025 → B264-016CT0026 → B264-016CT0027 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L27 → M0406 → D0301-L21 → M0301 → B215-996BT0001 → B215-016BT0002 → B215-016BT0003 → B215-016BT0004 → B215-016BT0005 → B215-016BT0031 → B215-016BT0032 → B215-016BT0033 → B215-016BT0034 → B261-016CC0026 → B261-006CC0008 → END
B2-MCC-64601 | -P20 | 02 |  | PE-L1-4C6-02 | PE-L1-4C6-02 | HRSG-U3-005 |  |  | 1 | 241 | B2-MCC-64601-P2002 | 0.6/1kV CU/XLPE/LSZH | 4C x 6sqmm | PE-L1-4C6-02 | 3.2 | 400 | N | 370 | HRSG | B2-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-P-14012A | HRSG #21 ABD EXTRACTION PUMP A - MOTOR | 1.1_MAIN BUILDING COMPLEX / HRSG #21 | L1, L2, L3, PE | B264-016CT0024 → B264-016CT0025 → B264-016CT0026 → B264-016CT0027 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L26 → M0406 → D0301-L22 → M0301 → B215-997AT0026 → B215-017AT0027 → B215-017AT0028 → B215-017AT0029 → B215-017AT0030 → B215-017AT0006 → B215-017AT0007 → B215-017AT0008 → B215-017AT0009 → B215-017AT0010 → B261-016CC0025 → B261-006CC0006 → B261-016CC0019 → B261-016CC0020 → END
B2-MCC-64602 | -P20 | 02 |  | PE-L1-4C6-02 | PE-L1-4C6-02 | HRSG-U3-006 |  |  | 1 | 242 | B2-MCC-64602-P2002 | 0.6/1kV CU/XLPE/LSZH | 4C x 6sqmm | PE-L1-4C6-02 | 3.2 | 400 | N | 400 | HRSG | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-P-14012B | HRSG #21 ABD EXTRACTION PUMP B - MOTOR | 1.1_MAIN BUILDING COMPLEX / HRSG #21 | L1, L2, L3, PE | B264-016AT0045 → B264-016AT0046 → B264-016AT0209 → B264-016AT0026 → B264-016AT0027 → B264-016AT0225 → B264-996AT0011 → M0405 → D0421-L27 → M0406 → D0301-L21 → M0301 → B215-996BT0001 → B215-016BT0002 → B215-016BT0003 → B215-016BT0004 → B215-016BT0005 → B215-016BT0031 → B215-016BT0032 → B215-016BT0033 → B215-016BT0034 → B215-016BT0035 → B261-016CC0030 → B261-006CC0007 → B261-016CC0029 → B261-016CC0021 → END
B2-MCC-64602 | -P20 | 03 |  | PE-L1-5C95/50-04 | PE-L1-5C95/50-04 | HRSG-U3-007 |  |  | 1 | 243 | B2-MCC-64602-P2003 | 0.6/1kV CU/XLPE/LSZH | 4C x 95sqmm + 1C X 50sqmm | PE-L1-5C95/50-04 | 50 | 400 | N | 320 | HRSG | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, N, PE | B2-PDP-1401 | HRSG #21 LV PANEL DISTRIBUTION BOARD | 1.1_MAIN BUILDING COMPLEX / HRSG #21 | L1, L2, L3, N, PE | B264-016AT0045 → B264-016AT0046 → B264-016AT0209 → B264-016AT0026 → B264-016AT0027 → B264-016AT0225 → B264-996AT0011 → M0405 → D0421-L33 → M0406 → D0301-L35 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B215-016AT0050 → B215-016AT0051 → B215-016AT0064 → B215-016AT0065 → B215-016AT0066 → B215-016AT0055 → B215-016AT0056 → B261-016CC0003 → END
B2-UPSP-64701 | -P20 | 02 |  | PE-L1-3C150/95-03 | PE-L1-3C150/95-03 | HRSG-U3-011 |  |  | 1 | 244 | B2-UPSP-64701-P2002 | 0.6/1kV CU/XLPE/LSZH | 2C x 150sqmm + 1C X 95sqmm | PE-L1-3C150/95-03 | 10 | 230 | U | 320 | HRSG | B2-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-UPSP-1401A | HRSG #21 UPS DISTRIBUTION BOARD (MAIN) | 1.1_MAIN BUILDING COMPLEX / HRSG #21 | L1, N, PE | B264-016DT0061 → B264-016DT0060 → B264-006AC0003 → M0405 → D0421-L32 → M0406 → D0301-L36 → M0301 → B215-996BT0001 → B215-016BT0002 → B215-016BT0003 → B215-016BT0004 → B215-016BT0005 → B215-016BT0031 → B215-016BT0032 → B215-016BT0033 → B215-016BT0034 → B261-017CC0005 → END
B2-UPSP-64702 | -P20 | 02 |  | PE-L1-3C150/95-03 | PE-L1-3C150/95-03 | HRSG-U3-011-001 |  |  | 1 | 245 | B2-UPSP-64702-P2002 | 0.6/1kV CU/XLPE/LSZH | 2C x 150sqmm + 1C X 95sqmm | PE-L1-3C150/95-03 | 10 | 230 | U | 330 | HRSG | B2-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-UPSP-1401B | HRSG #21 UPS DISTRIBUTION BOARD (BACK UP) | 1.1_MAIN BUILDING COMPLEX / HRSG #21 | L1, N, PE | B264-016ET0061 → B264-016ET0060 → B264-006AC0002 → M0405 → D0421-L33 → M0406 → D0301-L35 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B215-016AT0050 → B215-016AT0051 → B215-016AT0064 → B215-016AT0065 → B215-016AT0066 → B215-016AT0055 → B215-016AT0056 → B215-016AT0059 → B261-017CC0006 → END
B2-MCC-64601 | -P20 | 03 | From변경(9/30) 재배정 | PE-L1-5C120/70-01 | PE-L1-5C120/70-02 | HRSG-U3-013 | B2-MCC-64601-P2003 |  | 1 | 246 | B2-MCC-64602-P2043 | 0.6/1kV CU/XLPE/LSZH | 4C x 120sqmm + 1C X 70sqmm | PE-L1-5C120/70-02 | 50 | 400 | N | 380 | HRSG | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, N, PE | B2-PC-1404 | HRSG #21 HPU POWER DISTRIBUTION | 1.1_MAIN BUILDING COMPLEX / HRSG #21 | L1, L2, L3, N, PE | B264-016AT0045 → B264-016AT0046 → B264-016AT0209 → B264-016AT0026 → B264-016AT0027 → B264-016AT0225 → B264-996AT0011 → M0405 → D0421-L26 → M0406 → D0301-L22 → M0301 → B215-996BT0001 → B215-016BT0002 → B215-016BT0003 → B215-016BT0004 → B215-016BT0005 → B215-016BT0031 → B215-016BT0032 → B215-016BT0033 → B261-016CC0028 → B261-006CC0010 → B261-006CC0011 → END
B2-MCC-64601 | -P20 | 04 |  | PE-L1-4C4-22 | PE-L1-4C4-22 | HRSG-U3-016 |  |  | 1 | 247 | B2-MCC-64601-P2004 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-22 | 1.8 | 400 | N | 280 | HRSG | B2-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-14010 | HRSG #21 HP MAIN STEAM STOP VALVE - MOV | 1.1_MAIN BUILDING COMPLEX / HRSG #21 | L1, L2, L3, PE | B264-016CT0024 → B264-016CT0025 → B264-016CT0026 → B264-016CT0027 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L33 → M0406 → D0301-L35 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B215-016AT0050 → B215-016AT0051 → B215-016AT0064 → B215-016AT0065 → B215-016AT0066 → B215-016AT0055 → B261-016CC0005 → END
B2-MCC-64602 | -P20 | 04 |  | PE-L1-4C4-22 | PE-L1-4C4-22 | HRSG-U3-017 |  |  | 1 | 248 | B2-MCC-64602-P2004 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-22 | 1 | 400 | N | 300 | HRSG | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-14019 | HRSG #21 LP MAIN STEAM STOP VALVE - MOV | 1.1_MAIN BUILDING COMPLEX / HRSG #21 | L1, L2, L3, PE | B264-016AT0045 → B264-016AT0046 → B264-016AT0209 → B264-016AT0026 → B264-016AT0027 → B264-016AT0225 → B264-996AT0011 → M0405 → D0421-L33 → M0406 → D0301-L35 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B215-016AT0050 → B215-016AT0051 → B215-016AT0064 → B215-016AT0065 → B215-016AT0066 → B215-016AT0055 → B261-016CC0006 → END
B2-MCC-64602 | -P20 | 05 |  | PE-L1-4C4-22 | PE-L1-4C4-22 | HRSG-U3-018 |  |  | 1 | 249 | B2-MCC-64602-P2005 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-22 | 0.1 | 380 | N | 310 | HRSG | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-14011 | HRSG #21 HP MAIN STEAM STOP BYPASS VALVE - MOV | 1.1_MAIN BUILDING COMPLEX / HRSG #21 | L1, L2, L3, PE | B264-016AT0045 → B264-016AT0046 → B264-016AT0209 → B264-016AT0026 → B264-016AT0027 → B264-016AT0225 → B264-996AT0011 → M0405 → D0421-L33 → M0406 → D0301-L35 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B215-016AT0050 → B215-016AT0051 → B215-016AT0064 → B215-016AT0065 → B215-016AT0066 → B215-016AT0055 → B215-016AT0056 → B261-016CC0031 → END
B2-MCC-64603 | -P20 | 01 |  | PE-L1-4C16-01 | PE-L1-4C16-01 | HRSG-U4-001 |  |  | 1 | 250 | B2-MCC-64603-P2001 | 0.6/1kV CU/XLPE/LSZH | 4C x 16sqmm | PE-L1-4C16-01 | 15 | 400 | N | 300 | HRSG | B2-MCC-64603 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-P-15011A | HRSG #22 FW RECIRCULATION PUMP A - MOTOR | 1.1_MAIN BUILDING COMPLEX / HRSG #22 | L1, L2, L3, PE | B264-016AT0027 → B264-016AT0225 → B264-996AT0011 → M0405 → D0421-L26 → M0406 → D0301-L22 → M0301 → B215-996BT0001 → B215-016BT0002 → B215-016BT0003 → B215-016BT0004 → B215-016BT0005 → B215-016BT0031 → B215-016BT0032 → B261-016AC0014 → B261-006AC0009 → END
B2-MCC-64604 | -P20 | 01 |  | PE-L1-4C16-02 | PE-L1-4C16-02 | HRSG-U4-002 |  |  | 1 | 251 | B2-MCC-64604-P2001 | 0.6/1kV CU/XLPE/LSZH | 4C x 16sqmm | PE-L1-4C16-02 | 15 | 400 | N | 310 | HRSG | B2-MCC-64604 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-P-15011B | HRSG #22 FW RECIRCULATION PUMP B - MOTOR | 1.1_MAIN BUILDING COMPLEX / HRSG #22 | L1, L2, L3, PE | B264-016CT0047 → B264-016CT0048 → B264-016CT0235 → B264-016CT0029 → B264-016CT0028 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L27 → M0406 → D0301-L21 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B215-016AT0050 → B215-016AT0051 → B215-016AT0064 → B215-016AT0065 → B261-016AC0013 → B261-006AC0008 → END
B2-MCC-64603 | -P20 | 02 |  | PE-L1-4C4-22 | PE-L1-4C4-22 | HRSG-U4-005 |  |  | 1 | 252 | B2-MCC-64603-P2002 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-22 | 3.2 | 400 | N | 290 | HRSG | B2-MCC-64603 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-P-15012A | HRSG #22 ABD EXTRACTION PUMP A - MOTOR | 1.1_MAIN BUILDING COMPLEX / HRSG #22 | L1, L2, L3, PE | B264-016AT0027 → B264-016AT0225 → B264-996AT0011 → M0405 → D0421-L26 → M0406 → D0301-L22 → M0301 → B215-996BT0001 → B215-016BT0002 → B215-016BT0003 → B215-016BT0004 → B215-016BT0005 → B215-016BT0031 → B215-016BT0032 → B261-016AC0012 → B261-006AC0007 → B261-016AC0021 → B261-016AC0019 → END
B2-MCC-64604 | -P20 | 02 |  | PE-L1-4C4-22 | PE-L1-4C4-22 | HRSG-U4-006 |  |  | 1 | 253 | B2-MCC-64604-P2002 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-22 | 3.2 | 400 | N | 300 | HRSG | B2-MCC-64604 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-P-15012B | HRSG #22 ABD EXTRACTION PUMP B - MOTOR | 1.1_MAIN BUILDING COMPLEX / HRSG #22 | L1, L2, L3, PE | B264-016CT0047 → B264-016CT0048 → B264-016CT0235 → B264-016CT0029 → B264-016CT0028 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L27 → M0406 → D0301-L21 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B215-016AT0050 → B215-016AT0051 → B215-016AT0064 → B215-016AT0065 → B261-016AC0012 → B261-006AC0007 → B261-016AC0021 → B261-016AC0020 → END
B2-MCC-64604 | -P20 | 03 | From변경 | PE-L1-5C70/35-01 | PE-L1-5C70/35-01 | HRSG-U4-007 | B2-MCC-64604-P2003 |  | 1 | 254 | B2-MCC-64603-P2029 | 0.6/1kV CU/XLPE/LSZH | 4C x 70sqmm + 1C X 35sqmm | PE-L1-5C70/35-01 | 50 | 400 | N | 220 | HRSG | B2-MCC-64603 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, N, PE | B2-PDP-1501 | HRSG #22 LV PANEL DISTRIBUTION BOARD | 1.1_MAIN BUILDING COMPLEX / HRSG #22 | L1, L2, L3, N, PE | B264-016CT0027 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L34 → M0406 → D0301-L36 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B215-016AT0105 → B261-016AC0003 → END
B2-UPSP-64702 | -P20 | 03 |  | PE-L1-3C120/70-01 | PE-L1-3C120/70-01 | HRSG-U4-011 |  |  | 1 | 255 | B2-UPSP-64702-P2003 | 0.6/1kV CU/XLPE/LSZH | 2C x 120sqmm + 1C X 70sqmm | PE-L1-3C120/70-01 | 10 | 230 | U | 220 | HRSG | B2-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-UPSP-1501A | HRSG #22 UPS DISTRIBUTION BOARD (MAIN) | 1.1_MAIN BUILDING COMPLEX / HRSG #22 | L1, N, PE | B264-016ET0061 → B264-016ET0060 → B264-006AC0003 → M0405 → D0421-L31 → M0406 → D0301-L37 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B215-016AT0105 → B261-017AC0005 → END
B2-UPSP-64701 | -P20 | 03 |  | PE-L1-3C120/70-01 | PE-L1-3C120/70-01 | HRSG-U4-011-001 |  |  | 1 | 256 | B2-UPSP-64701-P2003 | 0.6/1kV CU/XLPE/LSZH | 2C x 120sqmm + 1C X 70sqmm | PE-L1-3C120/70-01 | 10 | 230 | U | 270 | HRSG | B2-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-UPSP-1501B | HRSG #22 UPS DISTRIBUTION BOARD (BACK UP) | 1.1_MAIN BUILDING COMPLEX / HRSG #22 | L1, N, PE | B264-016DT0061 → B264-016DT0060 → B264-006AC0002 → M0405 → D0421-L33 → M0406 → D0301-L35 → M0301 → B215-996BT0001 → B215-016BT0002 → B215-016BT0003 → B215-016BT0004 → B215-016BT0005 → B215-016BT0031 → B261-017AC0006 → END
B2-MCC-64603 | -P20 | 03 | 재배정 미배정Drum사용으로 추가 발주 필요 | PE-L1-5C120/70-05 | PE-L1-5C120/70-08 | HRSG-U4-013 |  |  | 1 | 257 | B2-MCC-64603-P2003 | 0.6/1kV CU/XLPE/LSZH | 4C x 120sqmm + 1C X 70sqmm | PE-L1-5C120/70-08 | 50 | 400 | N | 350 | HRSG | B2-MCC-64603 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, N, PE | B2-PC-1504 | HRSG #22 HPU POWER DISTRIBUTION | 1.1_MAIN BUILDING COMPLEX / HRSG #22 | L1, L2, L3, N, PE | B264-016CT0027 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L31 → M0406 → D0301-L37 → M0301 → B215-996BT0001 → B215-016BT0002 → B215-016BT0003 → B215-016BT0004 → B215-016BT0005 → B215-016BT0031 → B215-016BT0032 → B215-016BT0033 → B261-016AC0015 → B261-006AC0010 → B261-006AC0011 → END
B2-MCC-64603 | -P20 | 04 |  | PE-L1-4C4-22 | PE-L1-4C4-22 | HRSG-U4-016 |  |  | 1 | 258 | B2-MCC-64603-P2004 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-22 | 1.8 | 400 | N | 210 | HRSG | B2-MCC-64603 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-15010 | HRSG #22 HP MAIN STEAM STOP VALVE - MOV | 1.1_MAIN BUILDING COMPLEX / HRSG #22 | L1, L2, L3, PE | B264-016CT0027 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L32 → M0406 → D0301-L36 → M0301 → B215-996BT0001 → B215-016BT0002 → B215-016BT0003 → B215-016BT0004 → B261-016AC0029 → END
B2-MCC-64604 | -P20 | 04 |  | PE-L1-4C4-22 | PE-L1-4C4-22 | HRSG-U4-017 |  |  | 1 | 259 | B2-MCC-64604-P2004 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-22 | 1 | 400 | N | 230 | HRSG | B2-MCC-64604 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-15019 | HRSG #22 LP MAIN STEAM STOP VALVE - MOV | 1.1_MAIN BUILDING COMPLEX / HRSG #22 | L1, L2, L3, PE | B264-016CT0047 → B264-016CT0209 → B264-016CT0026 → B264-016CT0027 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L31 → M0406 → D0301-L37 → M0301 → B215-996BT0001 → B215-016BT0002 → B215-016BT0003 → B215-016BT0004 → B261-016AC0028 → END
B2-MCC-64603 | -P20 | 05 |  | PE-L1-4C4-23 | PE-L1-4C4-23 | HRSG-U4-018 |  |  | 1 | 260 | B2-MCC-64603-P2005 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-23 | 0.1 | 380 | N | 210 | HRSG | B2-MCC-64603 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-15011 | HRSG #22 HP MAIN STEAM STOP BYPASS VALVE - MOV | 1.1_MAIN BUILDING COMPLEX / HRSG #22 | L1, L2, L3, PE | B264-016CT0027 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L32 → M0406 → D0301-L36 → M0301 → B215-996BT0001 → B215-016BT0002 → B215-016BT0003 → B215-016BT0004 → B261-016AC0030 → END
B1-SWG-69601 | -P20 | 01 |  | PE-L1-4C95/50-11 | PE-L1-4C95/50-11 | ACC-B1-001 |  |  | 1 | 261 | B1-SWG-69601-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-11 | 160 | 400 | N | 250 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16111 | ACC STREET 1 FAN 1 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006CT0015 → B169-006CT0030 → B169-006CT0001 → B169-006CT0002 → B169-006CT0003 → B169-006CT0045 → D0113-L23 → M0113 → D0115-L13 → M0115 → B116-916ET0006 → B116-016ET0006 → B116-926ET0006 → B116-026ET0006 → B116-036ET0006 → B116-036ET0015 → B116-036ET0017 → END
B1-SWG-69601 | -P20 | 02 |  | PE-L1-4C95/50-11 | PE-L1-4C95/50-11 |  |  |  | 1 | 262 | B1-SWG-69601-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-11 | 160 | 400 | N | 250 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16111 | ACC STREET 1 FAN 1 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006CT0015 → B169-006CT0030 → B169-006CT0001 → B169-006CT0002 → B169-006CT0003 → B169-006CT0045 → D0113-L23 → M0113 → D0115-L13 → M0115 → B116-916ET0006 → B116-016ET0006 → B116-926ET0006 → B116-026ET0006 → B116-036ET0006 → B116-036ET0015 → B116-036ET0017 → END
B1-SWG-69601 | -P20 | 03 |  | PE-L1-4C95/50-11 | PE-L1-4C95/50-11 | ACC-B1-002 |  |  | 1 | 263 | B1-SWG-69601-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-11 | 160 | 400 | N | 240 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16112 | ACC STREET 1 FAN 2 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006CT0015 → B169-006CT0030 → B169-006CT0001 → B169-006CT0002 → B169-006CT0003 → B169-006CT0045 → D0113-L24 → M0113 → D0115-L14 → M0115 → B116-916ET0006 → B116-016ET0006 → B116-926ET0006 → B116-026ET0006 → B116-036ET0006 → B116-036ET0015 → END
B1-SWG-69601 | -P20 | 04 |  | PE-L1-4C95/50-20 | PE-L1-4C95/50-20 |  |  |  | 1 | 264 | B1-SWG-69601-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-20 | 160 | 400 | N | 240 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16112 | ACC STREET 1 FAN 2 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006CT0015 → B169-006CT0030 → B169-006CT0001 → B169-006CT0002 → B169-006CT0003 → B169-006CT0045 → D0113-L24 → M0113 → D0115-L14 → M0115 → B116-916ET0006 → B116-016ET0006 → B116-926ET0006 → B116-026ET0006 → B116-036ET0006 → B116-036ET0015 → END
B1-SWG-69601 | -P20 | 05 |  | PE-L1-4C95/50-21 | PE-L1-4C95/50-21 | ACC-B1-003 |  |  | 1 | 265 | B1-SWG-69601-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-21 | 160 | 400 | N | 230 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16113 | ACC STREET 1 FAN 3 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006CT0015 → B169-006CT0030 → B169-006CT0001 → B169-006CT0002 → B169-006CT0003 → B169-006CT0045 → D0113-L31 → M0113 → D0115-L15 → M0115 → B116-916ET0006 → B116-016ET0006 → B116-926ET0006 → B116-026ET0006 → B116-036ET0006 → B116-036ET0015 → END
B1-SWG-69601 | -P20 | 06 |  | PE-L1-4C95/50-19 | PE-L1-4C95/50-19 |  |  |  | 1 | 266 | B1-SWG-69601-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-19 | 160 | 400 | N | 230 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16113 | ACC STREET 1 FAN 3 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006CT0015 → B169-006CT0030 → B169-006CT0001 → B169-006CT0002 → B169-006CT0003 → B169-006CT0045 → D0113-L31 → M0113 → D0115-L15 → M0115 → B116-916ET0006 → B116-016ET0006 → B116-926ET0006 → B116-026ET0006 → B116-036ET0006 → B116-036ET0015 → END
B1-SWG-69601 | -P20 | 07 |  | PE-L1-4C95/50-23 | PE-L1-4C95/50-23 | ACC-B1-004 |  |  | 1 | 267 | B1-SWG-69601-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-23 | 160 | 400 | N | 260 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16114 | ACC STREET 1 FAN 4 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006CT0015 → B169-006CT0030 → B169-006CT0001 → B169-006CT0002 → B169-006CT0003 → B169-006CT0045 → D0113-L21 → M0113 → D0112-L24 → M0114 → D0116-L12 → M0116 → B116-916FT0005 → B116-016FT0005 → B116-926FT0005 → B116-026FT0005 → B116-036FT0005 → B116-036ET0015 → END
B1-SWG-69601 | -P20 | 08 |  | PE-L1-4C95/50-23 | PE-L1-4C95/50-23 |  |  |  | 1 | 268 | B1-SWG-69601-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-23 | 160 | 400 | N | 260 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16114 | ACC STREET 1 FAN 4 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006CT0015 → B169-006CT0030 → B169-006CT0001 → B169-006CT0002 → B169-006CT0003 → B169-006CT0045 → D0113-L21 → M0113 → D0112-L24 → M0114 → D0116-L12 → M0116 → B116-916FT0005 → B116-016FT0005 → B116-926FT0005 → B116-026FT0005 → B116-036FT0005 → B116-036ET0015 → END
B1-SWG-69601 | -P20 | 09 |  | PE-L1-4C95/50-23 | PE-L1-4C95/50-23 | ACC-B1-005 |  |  | 1 | 269 | B1-SWG-69601-P2009 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-23 | 160 | 400 | N | 270 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16115 | ACC STREET 1 FAN 5 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006CT0015 → B169-006CT0030 → B169-006CT0001 → B169-006CT0002 → B169-006CT0003 → B169-006CT0045 → D0113-L21 → M0113 → D0112-L15 → M0114 → D0116-L15 → M0116 → B116-916FT0005 → B116-016FT0005 → B116-926FT0005 → B116-026FT0005 → B116-036FT0005 → B116-036ET0015 → END
B1-SWG-69601 | -P20 | 10 |  | PE-L1-4C95/50-32 | PE-L1-4C95/50-32 |  |  |  | 1 | 270 | B1-SWG-69601-P2010 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-32 | 160 | 400 | N | 270 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16115 | ACC STREET 1 FAN 5 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006CT0015 → B169-006CT0030 → B169-006CT0001 → B169-006CT0002 → B169-006CT0003 → B169-006CT0045 → D0113-L21 → M0113 → D0112-L15 → M0114 → D0116-L15 → M0116 → B116-916FT0005 → B116-016FT0005 → B116-926FT0005 → B116-026FT0005 → B116-036FT0005 → B116-036ET0015 → END
B1-SWG-69601 | -P20 | 11 |  | PE-L1-4C95/50-20 | PE-L1-4C95/50-20 | ACC-B1-006 |  |  | 1 | 271 | B1-SWG-69601-P2011 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-20 | 160 | 400 | N | 280 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16116 | ACC STREET 1 FAN 6 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006BT0031 → B169-006BT0009 → B169-006BT0010 → B169-006BT0044 → D0113-L22 → M0113 → D0112-L22 → M0114 → D0116-L15 → M0116 → B116-916FT0005 → B116-016FT0005 → B116-926FT0005 → B116-026FT0005 → B116-036FT0005 → B116-036ET0015 → B116-036ET0016 → END
B1-SWG-69601 | -P20 | 12 |  | PE-L1-4C95/50-20 | PE-L1-4C95/50-20 |  |  |  | 1 | 272 | B1-SWG-69601-P2012 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-20 | 160 | 400 | N | 280 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16116 | ACC STREET 1 FAN 6 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006BT0031 → B169-006BT0009 → B169-006BT0010 → B169-006BT0044 → D0113-L22 → M0113 → D0112-L22 → M0114 → D0116-L15 → M0116 → B116-916FT0005 → B116-016FT0005 → B116-926FT0005 → B116-026FT0005 → B116-036FT0005 → B116-036ET0015 → B116-036ET0016 → END
B1-SWG-69601 | -P20 | 13 |  | PE-L1-4C95/50-05 | PE-L1-4C95/50-05 | ACC-B1-007 |  |  | 1 | 273 | B1-SWG-69601-P2013 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-05 | 160 | 400 | N | 250 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16121 | ACC STREET 2 FAN 1 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006BT0031 → B169-006BT0009 → B169-006BT0010 → B169-006BT0044 → D0113-L22 → M0113 → D0115-L12 → M0115 → B116-916GT0008 → B116-016GT0008 → B116-926GT0008 → B116-026GT0008 → B116-036GT0008 → B116-036GT0018 → B116-036GT0020 → END
B1-SWG-69601 | -P20 | 14 |  | PE-L1-4C95/50-05 | PE-L1-4C95/50-05 |  |  |  | 1 | 274 | B1-SWG-69601-P2014 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-05 | 160 | 400 | N | 250 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16121 | ACC STREET 2 FAN 1 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006BT0031 → B169-006BT0009 → B169-006BT0010 → B169-006BT0044 → D0113-L22 → M0113 → D0115-L12 → M0115 → B116-916GT0008 → B116-016GT0008 → B116-926GT0008 → B116-026GT0008 → B116-036GT0008 → B116-036GT0018 → B116-036GT0020 → END
B1-SWG-69601 | -P20 | 15 |  | PE-L1-4C95/50-05 | PE-L1-4C95/50-05 | ACC-B1-008 |  |  | 1 | 275 | B1-SWG-69601-P2015 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-05 | 160 | 400 | N | 240 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16122 | ACC STREET 2 FAN 2 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006BT0031 → B169-006BT0009 → B169-006BT0010 → B169-006BT0044 → D0113-L23 → M0113 → D0115-L23 → M0115 → B116-916GT0008 → B116-016GT0008 → B116-926GT0008 → B116-026GT0008 → B116-036GT0008 → B116-036GT0018 → END
B1-SWG-69601 | -P20 | 16 |  | PE-L1-4C95/50-13 | PE-L1-4C95/50-13 |  |  |  | 1 | 276 | B1-SWG-69601-P2016 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-13 | 160 | 400 | N | 240 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16122 | ACC STREET 2 FAN 2 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006BT0031 → B169-006BT0009 → B169-006BT0010 → B169-006BT0044 → D0113-L23 → M0113 → D0115-L23 → M0115 → B116-916GT0008 → B116-016GT0008 → B116-926GT0008 → B116-026GT0008 → B116-036GT0008 → B116-036GT0018 → END
B1-SWG-69601 | -P20 | 17 |  | PE-L1-4C95/50-13 | PE-L1-4C95/50-13 | ACC-B1-009 |  |  | 1 | 277 | B1-SWG-69601-P2017 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-13 | 160 | 400 | N | 280 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16123 | ACC STREET 2 FAN 3 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006BT0016 → B169-006BT0017 → B169-006BT0018 → B169-006BT0054 → B169-006BT0005 → B169-006BT0006 → B169-006BT0047 → D0114-L23 → M0114 → D0112-L23 → M0113 → D0115-L13 → M0115 → B116-916GT0008 → B116-016GT0008 → B116-926GT0008 → B116-026GT0008 → B116-036GT0008 → B116-036GT0018 → END
B1-SWG-69601 | -P20 | 18 |  | PE-L1-4C95/50-13 | PE-L1-4C95/50-13 |  |  |  | 1 | 278 | B1-SWG-69601-P2018 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-13 | 160 | 400 | N | 280 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16123 | ACC STREET 2 FAN 3 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006BT0016 → B169-006BT0017 → B169-006BT0018 → B169-006BT0054 → B169-006BT0005 → B169-006BT0006 → B169-006BT0047 → D0114-L23 → M0114 → D0112-L23 → M0113 → D0115-L13 → M0115 → B116-916GT0008 → B116-016GT0008 → B116-926GT0008 → B116-026GT0008 → B116-036GT0008 → B116-036GT0018 → END
B1-SWG-69601 | -P20 | 19 |  | PE-L1-4C95/50-17 | PE-L1-4C95/50-17 | ACC-B1-010 |  |  | 1 | 279 | B1-SWG-69601-P2019 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-17 | 160 | 400 | N | 260 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16124 | ACC STREET 2 FAN 4 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006BT0016 → B169-006BT0017 → B169-006BT0018 → B169-006BT0054 → B169-006BT0005 → B169-006BT0006 → B169-006BT0047 → D0114-L24 → M0114 → D0116-L23 → M0116 → B116-916HT0007 → B116-016HT0007 → B116-926HT0007 → B116-026HT0007 → B116-036HT0007 → B116-036GT0018 → END
B1-SWG-69601 | -P20 | 20 |  | PE-L1-4C95/50-17 | PE-L1-4C95/50-17 |  |  |  | 1 | 280 | B1-SWG-69601-P2020 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-17 | 160 | 400 | N | 260 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16124 | ACC STREET 2 FAN 4 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006BT0016 → B169-006BT0017 → B169-006BT0018 → B169-006BT0054 → B169-006BT0005 → B169-006BT0006 → B169-006BT0047 → D0114-L24 → M0114 → D0116-L23 → M0116 → B116-916HT0007 → B116-016HT0007 → B116-926HT0007 → B116-026HT0007 → B116-036HT0007 → B116-036GT0018 → END
B1-SWG-69601 | -P20 | 21 |  | PE-L1-4C95/50-17 | PE-L1-4C95/50-17 | ACC-B1-011 |  |  | 1 | 281 | B1-SWG-69601-P2021 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-17 | 160 | 400 | N | 270 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16125 | ACC STREET 2 FAN 5 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006BT0016 → B169-006BT0017 → B169-006BT0018 → B169-006BT0054 → B169-006BT0005 → B169-006BT0006 → B169-006BT0047 → D0114-L21 → M0114 → D0116-L13 → M0116 → B116-916HT0007 → B116-016HT0007 → B116-926HT0007 → B116-026HT0007 → B116-036HT0007 → B116-036GT0018 → END
B1-SWG-69601 | -P20 | 22 |  | PE-L1-4C95/50-24 | PE-L1-4C95/50-24 |  |  |  | 1 | 282 | B1-SWG-69601-P2022 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-24 | 160 | 400 | N | 270 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16125 | ACC STREET 2 FAN 5 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006BT0016 → B169-006BT0017 → B169-006BT0018 → B169-006BT0054 → B169-006BT0005 → B169-006BT0006 → B169-006BT0047 → D0114-L21 → M0114 → D0116-L13 → M0116 → B116-916HT0007 → B116-016HT0007 → B116-926HT0007 → B116-026HT0007 → B116-036HT0007 → B116-036GT0018 → END
B1-SWG-69601 | -P20 | 23 |  | PE-L1-4C95/50-21 | PE-L1-4C95/50-21 | ACC-B1-012 |  |  | 1 | 283 | B1-SWG-69601-P2023 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-21 | 160 | 400 | N | 280 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16126 | ACC STREET 2 FAN 6 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006BT0016 → B169-006BT0017 → B169-006BT0018 → B169-006BT0054 → B169-006BT0005 → B169-006BT0006 → B169-006BT0047 → D0114-L22 → M0114 → D0116-L13 → M0116 → B116-916HT0007 → B116-016HT0007 → B116-926HT0007 → B116-026HT0007 → B116-036HT0007 → B116-036GT0018 → B116-036GT0019 → END
B1-SWG-69601 | -P20 | 24 |  | PE-L1-4C95/50-21 | PE-L1-4C95/50-21 |  |  |  | 1 | 284 | B1-SWG-69601-P2024 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-21 | 160 | 400 | N | 280 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16126 | ACC STREET 2 FAN 6 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006BT0016 → B169-006BT0017 → B169-006BT0018 → B169-006BT0054 → B169-006BT0005 → B169-006BT0006 → B169-006BT0047 → D0114-L22 → M0114 → D0116-L13 → M0116 → B116-916HT0007 → B116-016HT0007 → B116-926HT0007 → B116-026HT0007 → B116-036HT0007 → B116-036GT0018 → B116-036GT0019 → END
B1-SWG-69603 | -P20 | 01 |  | PE-L1-4C95/50-31 | PE-L1-4C95/50-31 | ACC-B1-013 |  |  | 1 | 285 | B1-SWG-69603-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-31 | 160 | 400 | N | 180 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16131 | ACC STREET 3 FAN 1 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006DT0003 → B169-006DT0045 → D0113-L33 → M0113 → D0115-L11 → M0115 → B116-916AT0002 → B116-016AT0002 → B116-926AT0002 → B116-026AT0002 → B116-036AT0002 → B116-036AT0009 → B116-036AT0011 → END
B1-SWG-69603 | -P20 | 02 |  | PE-L1-4C95/50-31 | PE-L1-4C95/50-31 |  |  |  | 1 | 286 | B1-SWG-69603-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-31 | 160 | 400 | N | 180 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16131 | ACC STREET 3 FAN 1 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006DT0003 → B169-006DT0045 → D0113-L33 → M0113 → D0115-L11 → M0115 → B116-916AT0002 → B116-016AT0002 → B116-926AT0002 → B116-026AT0002 → B116-036AT0002 → B116-036AT0009 → B116-036AT0011 → END
B1-SWG-69603 | -P20 | 03 |  | PE-L1-4C95/50-24 | PE-L1-4C95/50-24 | ACC-B1-014 |  |  | 1 | 287 | B1-SWG-69603-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-24 | 160 | 400 | N | 160 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16132 | ACC STREET 3 FAN 2 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006DT0003 → B169-006DT0045 → D0113-L33 → M0113 → D0115-L11 → M0115 → B116-916AT0002 → B116-016AT0002 → B116-926AT0002 → B116-026AT0002 → B116-036AT0002 → B116-036AT0009 → END
B1-SWG-69603 | -P20 | 04 |  | PE-L1-4C95/50-30 | PE-L1-4C95/50-30 |  |  |  | 1 | 288 | B1-SWG-69603-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-30 | 160 | 400 | N | 160 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16132 | ACC STREET 3 FAN 2 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006DT0003 → B169-006DT0045 → D0113-L33 → M0113 → D0115-L11 → M0115 → B116-916AT0002 → B116-016AT0002 → B116-926AT0002 → B116-026AT0002 → B116-036AT0002 → B116-036AT0009 → END
B1-SWG-69603 | -P20 | 05 |  | PE-L1-4C95/50-22 | PE-L1-4C95/50-22 | ACC-B1-015 |  |  | 1 | 289 | B1-SWG-69603-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-22 | 160 | 400 | N | 160 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16133 | ACC STREET 3 FAN 3 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006DT0003 → B169-006DT0045 → D0113-L34 → M0113 → D0115-L23 → M0115 → B116-916AT0002 → B116-016AT0002 → B116-926AT0002 → B116-026AT0002 → B116-036AT0002 → B116-036AT0009 → END
B1-SWG-69603 | -P20 | 06 |  | PE-L1-4C95/50-22 | PE-L1-4C95/50-22 |  |  |  | 1 | 290 | B1-SWG-69603-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-22 | 160 | 400 | N | 160 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16133 | ACC STREET 3 FAN 3 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006DT0003 → B169-006DT0045 → D0113-L34 → M0113 → D0115-L23 → M0115 → B116-916AT0002 → B116-016AT0002 → B116-926AT0002 → B116-026AT0002 → B116-036AT0002 → B116-036AT0009 → END
B1-SWG-69603 | -P20 | 07 |  | PE-L1-4C95/50-26 | PE-L1-4C95/50-26 | ACC-B1-016 |  |  | 1 | 291 | B1-SWG-69603-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-26 | 160 | 400 | N | 190 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16134 | ACC STREET 3 FAN 4 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006DT0003 → B169-006DT0045 → D0113-L34 → M0113 → D0112-L22 → M0114 → D0116-L22 → M0116 → B116-916BT0001 → B116-016BT0001 → B116-926BT0001 → B116-026BT0001 → B116-036BT0001 → B116-036AT0009 → END
B1-SWG-69603 | -P20 | 08 |  | PE-L1-4C95/50-26 | PE-L1-4C95/50-26 |  |  |  | 1 | 292 | B1-SWG-69603-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-26 | 160 | 400 | N | 190 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16134 | ACC STREET 3 FAN 4 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006DT0003 → B169-006DT0045 → D0113-L34 → M0113 → D0112-L22 → M0114 → D0116-L22 → M0116 → B116-916BT0001 → B116-016BT0001 → B116-926BT0001 → B116-026BT0001 → B116-036BT0001 → B116-036AT0009 → END
B1-SWG-69603 | -P20 | 09 |  | PE-L1-4C95/50-01 | PE-L1-4C95/50-01 | ACC-B1-017 |  |  | 1 | 293 | B1-SWG-69603-P2009 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-01 | 160 | 400 | N | 190 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16135 | ACC STREET 3 FAN 5 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006DT0003 → B169-006DT0045 → D0113-L35 → M0113 → D0112-L21 → M0114 → D0116-L22 → M0116 → B116-916BT0001 → B116-016BT0001 → B116-926BT0001 → B116-026BT0001 → B116-036BT0001 → B116-036AT0009 → END → 0
B1-SWG-69603 | -P20 | 10 |  | PE-L1-4C95/50-01 | PE-L1-4C95/50-01 |  |  |  | 1 | 294 | B1-SWG-69603-P2010 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-01 | 160 | 400 | N | 190 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16135 | ACC STREET 3 FAN 5 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006DT0003 → B169-006DT0045 → D0113-L35 → M0113 → D0112-L21 → M0114 → D0116-L14 → M0116 → B116-916BT0001 → B116-016BT0001 → B116-926BT0001 → B116-026BT0001 → B116-036BT0001 → B116-036AT0009 → END
B1-SWG-69603 | -P20 | 11 |  | PE-L1-4C95/50-01 | PE-L1-4C95/50-01 | ACC-B1-018 |  |  | 1 | 295 | B1-SWG-69603-P2011 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-01 | 160 | 400 | N | 210 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16136 | ACC STREET 3 FAN 6 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006ET0003 → B169-006ET0045 → D0113-L35 → M0113 → D0112-L21 → M0114 → D0116-L14 → M0116 → B116-916BT0001 → B116-016BT0001 → B116-926BT0001 → B116-026BT0001 → B116-036BT0001 → B116-036AT0009 → B116-036AT0010 → END
B1-SWG-69603 | -P20 | 12 |  | PE-L1-4C95/50-01 | PE-L1-4C95/50-01 |  |  |  | 1 | 296 | B1-SWG-69603-P2012 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-01 | 160 | 400 | N | 210 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16136 | ACC STREET 3 FAN 6 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006ET0003 → B169-006ET0045 → D0113-L35 → M0113 → D0112-L21 → M0114 → D0116-L14 → M0116 → B116-916BT0001 → B116-016BT0001 → B116-926BT0001 → B116-026BT0001 → B116-036BT0001 → B116-036AT0009 → B116-036AT0010 → END
B1-SWG-69603 | -P20 | 13 |  | PE-L1-4C95/50-09 | PE-L1-4C95/50-09 | ACC-B1-019 |  |  | 1 | 297 | B1-SWG-69603-P2013 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-09 | 160 | 400 | N | 180 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16141 | ACC STREET 4 FAN 1 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006ET0003 → B169-006ET0045 → D0113-L41 → M0113 → D0115-L21 → M0115 → B116-916DT0004 → B116-016DT0004 → B116-926DT0004 → B116-026DT0004 → B116-036DT0004 → B116-036CT0012 → B116-036CT0014 → END
B1-SWG-69603 | -P20 | 14 |  | PE-L1-4C95/50-09 | PE-L1-4C95/50-09 |  |  |  | 1 | 298 | B1-SWG-69603-P2014 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-09 | 160 | 400 | N | 180 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16141 | ACC STREET 4 FAN 1 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006ET0003 → B169-006ET0045 → D0113-L41 → M0113 → D0115-L21 → M0115 → B116-916DT0004 → B116-016DT0004 → B116-926DT0004 → B116-026DT0004 → B116-036DT0004 → B116-036CT0012 → B116-036CT0014 → END
B1-SWG-69603 | -P20 | 15 |  | PE-L1-4C95/50-09 | PE-L1-4C95/50-09 | ACC-B1-020 |  |  | 1 | 299 | B1-SWG-69603-P2015 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-09 | 160 | 400 | N | 170 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16142 | ACC STREET 4 FAN 2 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006ET0003 → B169-006ET0045 → D0113-L41 → M0113 → D0115-L14 → M0115 → B116-916DT0004 → B116-016DT0004 → B116-926DT0004 → B116-026DT0004 → B116-036DT0004 → B116-036CT0012 → END
B1-SWG-69603 | -P20 | 16 |  | PE-L1-4C95/50-09 | PE-L1-4C95/50-09 |  |  |  | 1 | 300 | B1-SWG-69603-P2016 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-09 | 160 | 400 | N | 170 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16142 | ACC STREET 4 FAN 2 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006ET0003 → B169-006ET0045 → D0113-L41 → M0113 → D0115-L14 → M0115 → B116-916DT0004 → B116-016DT0004 → B116-926DT0004 → B116-026DT0004 → B116-036DT0004 → B116-036CT0012 → END
B1-SWG-69603 | -P20 | 17 |  | PE-L1-4C95/50-26 | PE-L1-4C95/50-26 | ACC-B1-021 |  |  | 1 | 301 | B1-SWG-69603-P2017 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-26 | 160 | 400 | N | 160 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16143 | ACC STREET 4 FAN 3 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006ET0003 → B169-006ET0045 → D0113-L42 → M0113 → D0115-L21 → M0115 → B116-916DT0004 → B116-016DT0004 → B116-926DT0004 → B116-026DT0004 → B116-036DT0004 → B116-036CT0012 → END
B1-SWG-69603 | -P20 | 18 |  | PE-L1-4C95/50-26 | PE-L1-4C95/50-26 |  |  |  | 1 | 302 | B1-SWG-69603-P2018 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-26 | 160 | 400 | N | 160 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16143 | ACC STREET 4 FAN 3 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006ET0003 → B169-006ET0045 → D0113-L42 → M0113 → D0115-L21 → M0115 → B116-916DT0004 → B116-016DT0004 → B116-926DT0004 → B116-026DT0004 → B116-036DT0004 → B116-036CT0012 → END
B1-SWG-69603 | -P20 | 19 |  | PE-L1-4C95/50-27 | PE-L1-4C95/50-27 | ACC-B1-022 |  |  | 1 | 303 | B1-SWG-69603-P2019 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-27 | 160 | 400 | N | 190 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16144 | ACC STREET 4 FAN 4 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006ET0003 → B169-006ET0045 → D0113-L42 → M0113 → D0112-L24 → M0114 → D0116-L11 → M0116 → B116-916CT0003 → B116-016CT0003 → B116-926CT0003 → B116-026CT0003 → B116-036CT0003 → B116-036CT0012 → END
B1-SWG-69603 | -P20 | 20 |  | PE-L1-4C95/50-27 | PE-L1-4C95/50-27 |  |  |  | 1 | 304 | B1-SWG-69603-P2020 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-27 | 160 | 400 | N | 190 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16144 | ACC STREET 4 FAN 4 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006ET0003 → B169-006ET0045 → D0113-L42 → M0113 → D0112-L24 → M0114 → D0116-L11 → M0116 → B116-916CT0003 → B116-016CT0003 → B116-926CT0003 → B116-026CT0003 → B116-036CT0003 → B116-036CT0012 → END
B1-SWG-69603 | -P20 | 21 |  | PE-L1-4C95/50-27 | PE-L1-4C95/50-27 | ACC-B1-023 |  |  | 1 | 305 | B1-SWG-69603-P2021 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-27 | 160 | 400 | N | 190 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16145 | ACC STREET 4 FAN 5 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006BT0031 → B169-006BT0009 → B169-006BT0010 → B169-006BT0044 → D0113-L43 → M0113 → D0115-L22 → M0115 → B116-916CT0003 → B116-016CT0003 → B116-926CT0003 → B116-026CT0003 → B116-036CT0003 → B116-036CT0012 → END
B1-SWG-69603 | -P20 | 22 |  | PE-L1-4C95/50-28 | PE-L1-4C95/50-28 |  |  |  | 1 | 306 | B1-SWG-69603-P2022 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-28 | 160 | 400 | N | 190 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16145 | ACC STREET 4 FAN 5 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006BT0031 → B169-006BT0009 → B169-006BT0010 → B169-006BT0044 → D0113-L43 → M0113 → D0115-L22 → M0115 → B116-916CT0003 → B116-016CT0003 → B116-926CT0003 → B116-026CT0003 → B116-036CT0003 → B116-036CT0012 → END
B1-SWG-69603 | -P20 | 23 |  | PE-L1-4C95/50-28 | PE-L1-4C95/50-28 | ACC-B1-024 |  |  | 1 | 307 | B1-SWG-69603-P2023 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-28 | 160 | 400 | N | 200 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16146 | ACC STREET 4 FAN 6 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006BT0031 → B169-006BT0009 → B169-006BT0010 → B169-006BT0044 → D0113-L43 → M0113 → D0115-L22 → M0115 → B116-916CT0003 → B116-016CT0003 → B116-926CT0003 → B116-026CT0003 → B116-036CT0003 → B116-036CT0012 → B116-036CT0013 → END
B1-SWG-69603 | -P20 | 24 |  | PE-L1-4C95/50-28 | PE-L1-4C95/50-28 |  |  |  | 1 | 308 | B1-SWG-69603-P2024 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-28 | 160 | 400 | N | 200 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-C(M)-16146 | ACC STREET 4 FAN 6 MOTOR | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006BT0031 → B169-006BT0009 → B169-006BT0010 → B169-006BT0044 → D0113-L43 → M0113 → D0115-L22 → M0115 → B116-916CT0003 → B116-016CT0003 → B116-926CT0003 → B116-026CT0003 → B116-036CT0003 → B116-036CT0012 → B116-036CT0013 → END
B1-SWG-69601 | -P20 | 25 |  | PE-L1-3C4-03 | PE-L1-3C4-03 | ACC-B1-025 |  |  | 1 | 309 | B1-SWG-69601-P2025 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-03 | 0.2 | 230 | N | 250 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(MH)-16111 | ACC STREET 1 FAN 1 MOTOR SPACE HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006CT0015 → B169-006CT0030 → B169-006CT0001 → B169-006CT0002 → B169-006CT0003 → B169-006CT0045 → D0113-L23 → M0113 → D0115-L13 → M0115 → B116-916ET0006 → B116-016ET0006 → B116-926ET0006 → B116-026ET0006 → B116-036ET0006 → B116-036ET0015 → B116-036ET0017 → END
B1-SWG-69601 | -P20 | 26 |  | PE-L1-3C4-03 | PE-L1-3C4-03 | ACC-B1-026 |  |  | 1 | 310 | B1-SWG-69601-P2026 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-03 | 0.2 | 230 | N | 240 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(MH)-16112 | ACC STREET 1 FAN 2 MOTOR SPACE HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006CT0015 → B169-006CT0030 → B169-006CT0001 → B169-006CT0002 → B169-006CT0003 → B169-006CT0045 → D0113-L24 → M0113 → D0115-L14 → M0115 → B116-916ET0006 → B116-016ET0006 → B116-926ET0006 → B116-026ET0006 → B116-036ET0006 → B116-036ET0015 → END
B1-SWG-69601 | -P20 | 27 |  | PE-L1-3C4-03 | PE-L1-3C4-03 | ACC-B1-027 |  |  | 1 | 311 | B1-SWG-69601-P2027 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-03 | 0.2 | 230 | N | 230 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(MH)-16113 | ACC STREET 1 FAN 3 MOTOR SPACE HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006CT0015 → B169-006CT0030 → B169-006CT0001 → B169-006CT0002 → B169-006CT0003 → B169-006CT0045 → D0113-L31 → M0113 → D0115-L15 → M0115 → B116-916ET0006 → B116-016ET0006 → B116-926ET0006 → B116-026ET0006 → B116-036ET0006 → B116-036ET0015 → END
B1-SWG-69601 | -P20 | 28 |  | PE-L1-3C4-03 | PE-L1-3C4-03 | ACC-B1-028 |  |  | 1 | 312 | B1-SWG-69601-P2028 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-03 | 0.2 | 230 | N | 260 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(MH)-16114 | ACC STREET 1 FAN 4 MOTOR SPACE HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006CT0015 → B169-006CT0030 → B169-006CT0001 → B169-006CT0002 → B169-006CT0003 → B169-006CT0045 → D0113-L32 → M0113 → D0112-L24 → M0114 → D0116-L14 → M0116 → B116-916FT0005 → B116-016FT0005 → B116-926FT0005 → B116-026FT0005 → B116-036FT0005 → B116-036ET0015 → END
B1-SWG-69601 | -P20 | 29 |  | PE-L1-3C4-03 | PE-L1-3C4-03 | ACC-B1-029 |  |  | 1 | 313 | B1-SWG-69601-P2029 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-03 | 0.2 | 230 | N | 270 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(MH)-16115 | ACC STREET 1 FAN 5 MOTOR SPACE HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006CT0015 → B169-006CT0030 → B169-006CT0001 → B169-006CT0002 → B169-006CT0003 → B169-006CT0045 → D0113-L31 → M0113 → D0112-L25 → M0114 → D0116-L14 → M0116 → B116-916FT0005 → B116-016FT0005 → B116-926FT0005 → B116-026FT0005 → B116-036FT0005 → B116-036ET0015 → END
B1-SWG-69601 | -P20 | 30 |  | PE-L1-3C4-03 | PE-L1-3C4-03 | ACC-B1-030 |  |  | 1 | 314 | B1-SWG-69601-P2030 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-03 | 0.2 | 230 | N | 280 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(MH)-16116 | ACC STREET 1 FAN 6 MOTOR SPACE HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006BT0031 → B169-006BT0009 → B169-006BT0010 → B169-006BT0044 → D0113-L31 → M0113 → D0112-L25 → M0114 → D0116-L14 → M0116 → B116-916FT0005 → B116-016FT0005 → B116-926FT0005 → B116-026FT0005 → B116-036FT0005 → B116-036ET0015 → B116-036ET0016 → END
B1-SWG-69601 | -P20 | 31 |  | PE-L1-3C4-03 | PE-L1-3C4-03 | ACC-B1-031 |  |  | 1 | 315 | B1-SWG-69601-P2031 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-03 | 0.2 | 230 | N | 250 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(MH)-16121 | ACC STREET 2 FAN 1 MOTOR SPACE HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006BT0031 → B169-006BT0009 → B169-006BT0010 → B169-006BT0044 → D0113-L32 → M0113 → D0115-L21 → M0115 → B116-916GT0008 → B116-016GT0008 → B116-926GT0008 → B116-026GT0008 → B116-036GT0008 → B116-036GT0018 → B116-036GT0020 → END
B1-SWG-69601 | -P20 | 32 | 재배정 | PE-L1-3C4-06 | PE-L1-3C4-14 | ACC-B1-032 |  |  | 1 | 316 | B1-SWG-69601-P2032 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-14 | 0.2 | 230 | N | 240 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(MH)-16122 | ACC STREET 2 FAN 2 MOTOR SPACE HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006BT0031 → B169-006BT0009 → B169-006BT0010 → B169-006BT0044 → D0113-L32 → M0113 → D0115-L21 → M0115 → B116-916GT0008 → B116-016GT0008 → B116-926GT0008 → B116-026GT0008 → B116-036GT0008 → B116-036GT0018 → END
B1-SWG-69601 | -P20 | 33 |  | PE-L1-3C4-02 | PE-L1-3C4-02 | ACC-B1-033 |  |  | 1 | 317 | B1-SWG-69601-P2033 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-02 | 0.2 | 230 | N | 280 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(MH)-16123 | ACC STREET 2 FAN 3 MOTOR SPACE HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006BT0016 → B169-006BT0017 → B169-006BT0018 → B169-006BT0054 → B169-006BT0005 → B169-006BT0006 → B169-006BT0047 → D0114-L21 → M0114 → D0112-L21 → M0113 → D0115-L21 → M0115 → B116-916GT0008 → B116-016GT0008 → B116-926GT0008 → B116-026GT0008 → B116-036GT0008 → B116-036GT0018 → END
B1-SWG-69601 | -P20 | 34 |  | PE-L1-3C4-02 | PE-L1-3C4-02 | ACC-B1-034 |  |  | 1 | 318 | B1-SWG-69601-P2034 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-02 | 0.2 | 230 | N | 260 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(MH)-16124 | ACC STREET 2 FAN 4 MOTOR SPACE HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006BT0016 → B169-006BT0017 → B169-006BT0018 → B169-006BT0054 → B169-006BT0005 → B169-006BT0006 → B169-006BT0047 → D0114-L24 → M0114 → D0116-L21 → M0116 → B116-916HT0007 → B116-016HT0007 → B116-926HT0007 → B116-026HT0007 → B116-036HT0007 → B116-036GT0018 → END
B1-SWG-69601 | -P20 | 35 |  | PE-L1-3C4-02 | PE-L1-3C4-02 | ACC-B1-035 |  |  | 1 | 319 | B1-SWG-69601-P2035 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-02 | 0.2 | 230 | N | 270 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(MH)-16125 | ACC STREET 2 FAN 5 MOTOR SPACE HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006BT0016 → B169-006BT0017 → B169-006BT0018 → B169-006BT0054 → B169-006BT0005 → B169-006BT0006 → B169-006BT0047 → D0114-L21 → M0114 → D0116-L21 → M0116 → B116-916HT0007 → B116-016HT0007 → B116-926HT0007 → B116-026HT0007 → B116-036HT0007 → B116-036GT0018 → END
B1-SWG-69601 | -P20 | 36 |  | PE-L1-3C4-02 | PE-L1-3C4-02 | ACC-B1-036 |  |  | 1 | 320 | B1-SWG-69601-P2036 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-02 | 0.2 | 230 | N | 280 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(MH)-16126 | ACC STREET 2 FAN 6 MOTOR SPACE HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006BT0016 → B169-006BT0017 → B169-006BT0018 → B169-006BT0054 → B169-006BT0005 → B169-006BT0006 → B169-006BT0047 → D0114-L22 → M0114 → D0116-L21 → M0116 → B116-916HT0007 → B116-016HT0007 → B116-926HT0007 → B116-026HT0007 → B116-036HT0007 → B116-036GT0018 → B116-036GT0019 → END
B1-SWG-69603 | -P20 | 25 | 재배정 | PE-L1-3C4-04 | PE-L1-3C4-16 | ACC-B1-037 |  |  | 1 | 321 | B1-SWG-69603-P2025 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-16 | 0.2 | 230 | N | 180 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(MH)-16131 | ACC STREET 3 FAN 1 MOTOR SPACE HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006DT0003 → B169-006DT0045 → D0113-L33 → M0113 → D0115-L11 → M0115 → B116-916AT0002 → B116-016AT0002 → B116-926AT0002 → B116-026AT0002 → B116-036AT0002 → B116-036AT0009 → B116-036AT0011 → END
B1-SWG-69603 | -P20 | 26 |  | PE-L1-3C4-02 | PE-L1-3C4-02 | ACC-B1-038 |  |  | 1 | 322 | B1-SWG-69603-P2026 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-02 | 0.2 | 230 | N | 160 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(MH)-16132 | ACC STREET 3 FAN 2 MOTOR SPACE HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006DT0003 → B169-006DT0045 → D0113-L33 → M0113 → D0115-L11 → M0115 → B116-916AT0002 → B116-016AT0002 → B116-926AT0002 → B116-026AT0002 → B116-036AT0002 → B116-036AT0009 → END
B1-SWG-69603 | -P20 | 27 |  | PE-L1-3C4-02 | PE-L1-3C4-02 | ACC-B1-039 |  |  | 1 | 323 | B1-SWG-69603-P2027 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-02 | 0.2 | 230 | N | 160 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(MH)-16133 | ACC STREET 3 FAN 3 MOTOR SPACE HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006DT0003 → B169-006DT0045 → D0113-L34 → M0113 → D0115-L23 → M0115 → B116-916AT0002 → B116-016AT0002 → B116-926AT0002 → B116-026AT0002 → B116-036AT0002 → B116-036AT0009 → END
B1-SWG-69603 | -P20 | 28 |  | PE-L1-3C4-02 | PE-L1-3C4-02 | ACC-B1-040 |  |  | 1 | 324 | B1-SWG-69603-P2028 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-02 | 0.2 | 230 | N | 190 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(MH)-16134 | ACC STREET 3 FAN 4 MOTOR SPACE HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006DT0003 → B169-006DT0045 → D0113-L34 → M0113 → D0112-L22 → M0114 → D0116-L13 → M0116 → B116-916BT0001 → B116-016BT0001 → B116-926BT0001 → B116-026BT0001 → B116-036BT0001 → B116-036AT0009 → END
B1-SWG-69603 | -P20 | 29 |  | PE-L1-3C4-02 | PE-L1-3C4-02 | ACC-B1-041 |  |  | 1 | 325 | B1-SWG-69603-P2029 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-02 | 0.2 | 230 | N | 190 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(MH)-16135 | ACC STREET 3 FAN 5 MOTOR SPACE HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006DT0003 → B169-006DT0045 → D0113-L35 → M0113 → D0112-L21 → M0114 → D0116-L15 → M0116 → B116-916BT0001 → B116-016BT0001 → B116-926BT0001 → B116-026BT0001 → B116-036BT0001 → B116-036AT0009 → END
B1-SWG-69603 | -P20 | 30 |  | PE-L1-3C4-02 | PE-L1-3C4-02 | ACC-B1-042 |  |  | 1 | 326 | B1-SWG-69603-P2030 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-02 | 0.2 | 230 | N | 210 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(MH)-16136 | ACC STREET 3 FAN 6 MOTOR SPACE HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006ET0003 → B169-006ET0045 → D0113-L35 → M0113 → D0112-L21 → M0114 → D0116-L15 → M0116 → B116-916BT0001 → B116-016BT0001 → B116-926BT0001 → B116-026BT0001 → B116-036BT0001 → B116-036AT0009 → B116-036AT0010 → END
B1-SWG-69603 | -P20 | 31 | 재배정 | PE-L1-3C4-04 | PE-L1-3C4-16 | ACC-B1-043 |  |  | 1 | 327 | B1-SWG-69603-P2031 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-16 | 0.2 | 230 | N | 180 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(MH)-16141 | ACC STREET 4 FAN 1 MOTOR SPACE HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006ET0003 → B169-006ET0045 → D0113-L41 → M0113 → D0115-L14 → M0115 → B116-916DT0004 → B116-016DT0004 → B116-926DT0004 → B116-026DT0004 → B116-036DT0004 → B116-036CT0012 → B116-036CT0014 → END
B1-SWG-69603 | -P20 | 32 | 재배정 | PE-L1-3C4-04 | PE-L1-3C4-16 | ACC-B1-044 |  |  | 1 | 328 | B1-SWG-69603-P2032 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-16 | 0.2 | 230 | N | 170 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(MH)-16142 | ACC STREET 4 FAN 2 MOTOR SPACE HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006ET0003 → B169-006ET0045 → D0113-L41 → M0113 → D0115-L14 → M0115 → B116-916DT0004 → B116-016DT0004 → B116-926DT0004 → B116-026DT0004 → B116-036DT0004 → B116-036CT0012 → END
B1-SWG-69603 | -P20 | 33 | 재배정 | PE-L1-3C4-04 | PE-L1-3C4-16 | ACC-B1-045 |  |  | 1 | 329 | B1-SWG-69603-P2033 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-16 | 0.2 | 230 | N | 160 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(MH)-16143 | ACC STREET 4 FAN 3 MOTOR SPACE HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006ET0003 → B169-006ET0045 → D0113-L42 → M0113 → D0115-L21 → M0115 → B116-916DT0004 → B116-016DT0004 → B116-926DT0004 → B116-026DT0004 → B116-036DT0004 → B116-036CT0012 → END
B1-SWG-69603 | -P20 | 34 | 재배정 | PE-L1-3C4-04 | PE-L1-3C4-16 | ACC-B1-046 |  |  | 1 | 330 | B1-SWG-69603-P2034 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-16 | 0.2 | 230 | N | 190 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(MH)-16144 | ACC STREET 4 FAN 4 MOTOR SPACE HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006ET0003 → B169-006ET0045 → D0113-L42 → M0113 → D0112-L24 → M0114 → D0116-L22 → M0116 → B116-916CT0003 → B116-016CT0003 → B116-926CT0003 → B116-026CT0003 → B116-036CT0003 → B116-036CT0012 → END
B1-SWG-69603 | -P20 | 35 | 재배정 | PE-L1-3C4-04 | PE-L1-3C4-16 | ACC-B1-047 |  |  | 1 | 331 | B1-SWG-69603-P2035 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-16 | 0.2 | 230 | N | 190 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(MH)-16145 | ACC STREET 4 FAN 5 MOTOR SPACE HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006BT0031 → B169-006BT0009 → B169-006BT0010 → B169-006BT0044 → D0113-L43 → M0113 → D0115-L22 → M0115 → B116-916CT0003 → B116-016CT0003 → B116-926CT0003 → B116-026CT0003 → B116-036CT0003 → B116-036CT0012 → END
B1-SWG-69603 | -P20 | 36 | 재배정 | PE-L1-3C4-04 | PE-L1-3C4-16 | ACC-B1-048 |  |  | 1 | 332 | B1-SWG-69603-P2036 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-16 | 0.2 | 230 | N | 200 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(MH)-16146 | ACC STREET 4 FAN 6 MOTOR SPACE HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006BT0031 → B169-006BT0009 → B169-006BT0010 → B169-006BT0044 → D0113-L43 → M0113 → D0115-L22 → M0115 → B116-916CT0003 → B116-016CT0003 → B116-926CT0003 → B116-026CT0003 → B116-036CT0003 → B116-036CT0012 → B116-036CT0013 → END
B1-DB-69601 | -P20 | 01 |  | PE-L1-3C6-01 | PE-L1-3C6-01 | ACC-B1-048-003 |  |  | 1 | 333 | B1-DB-69601-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-01 | 1 | 230 | N | 230 | AIR COOLED CONDENSER | B1-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(GH)-16111 | ACC STREET 1 FAN 1 GEARBOX OIL HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006CT0015 → B169-006CT0030 → B169-006CT0001 → B169-006CT0002 → B169-006CT0003 → B169-006CT0045 → D0113-L23 → M0113 → D0115-L13 → M0115 → B116-916ET0006 → B116-016ET0006 → B116-926ET0006 → B116-026ET0006 → B116-036ET0006 → B116-036ET0015 → B116-036ET0017 → END
B1-DB-69601 | -P20 | 02 |  | PE-L1-3C6-01 | PE-L1-3C6-01 | ACC-B1-048-004 |  |  | 1 | 334 | B1-DB-69601-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-01 | 1 | 230 | N | 220 | AIR COOLED CONDENSER | B1-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(GH)-16112 | ACC STREET 1 FAN 2 GEARBOX OIL HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006CT0015 → B169-006CT0030 → B169-006CT0001 → B169-006CT0002 → B169-006CT0003 → B169-006CT0045 → D0113-L24 → M0113 → D0115-L14 → M0115 → B116-916ET0006 → B116-016ET0006 → B116-926ET0006 → B116-026ET0006 → B116-036ET0006 → B116-036ET0015 → END
B1-DB-69601 | -P20 | 03 |  | PE-L1-3C6-01 | PE-L1-3C6-01 | ACC-B1-048-005 |  |  | 1 | 335 | B1-DB-69601-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-01 | 1 | 230 | N | 210 | AIR COOLED CONDENSER | B1-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(GH)-16113 | ACC STREET 1 FAN 3 GEARBOX OIL HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006CT0015 → B169-006CT0030 → B169-006CT0001 → B169-006CT0002 → B169-006CT0003 → B169-006CT0045 → D0113-L31 → M0113 → D0115-L15 → M0115 → B116-916ET0006 → B116-016ET0006 → B116-926ET0006 → B116-026ET0006 → B116-036ET0006 → B116-036ET0015 → END
B1-DB-69601 | -P20 | 04 |  | PE-L1-3C6-01 | PE-L1-3C6-01 | ACC-B1-048-006 |  |  | 1 | 336 | B1-DB-69601-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-01 | 1 | 230 | N | 235 | AIR COOLED CONDENSER | B1-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(GH)-16114 | ACC STREET 1 FAN 4 GEARBOX OIL HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006CT0015 → B169-006CT0030 → B169-006CT0001 → B169-006CT0002 → B169-006CT0003 → B169-006CT0045 → D0113-L32 → M0113 → D0112-L21 → M0114 → D0116-L14 → M0116 → B116-916FT0005 → B116-016FT0005 → B116-926FT0005 → B116-026FT0005 → B116-036FT0005 → B116-036ET0015 → END
B1-DB-69601 | -P20 | 05 |  | PE-L1-3C6-02 | PE-L1-3C6-02 | ACC-B1-048-007 |  |  | 1 | 337 | B1-DB-69601-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-02 | 1 | 230 | N | 250 | AIR COOLED CONDENSER | B1-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(GH)-16115 | ACC STREET 1 FAN 5 GEARBOX OIL HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006CT0015 → B169-006CT0030 → B169-006CT0001 → B169-006CT0002 → B169-006CT0003 → B169-006CT0045 → D0113-L31 → M0113 → D0112-L25 → M0114 → D0116-L14 → M0116 → B116-916FT0005 → B116-016FT0005 → B116-926FT0005 → B116-026FT0005 → B116-036FT0005 → B116-036ET0015 → END
B1-DB-69601 | -P20 | 06 |  | PE-L1-3C6-04 | PE-L1-3C6-04 | ACC-B1-048-008 |  |  | 1 | 338 | B1-DB-69601-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-04 | 1 | 230 | N | 250 | AIR COOLED CONDENSER | B1-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(GH)-16116 | ACC STREET 1 FAN 6 GEARBOX OIL HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006BT0031 → B169-006BT0009 → B169-006BT0010 → B169-006BT0044 → D0113-L31 → M0113 → D0112-L25 → M0114 → D0116-L14 → M0116 → B116-916FT0005 → B116-016FT0005 → B116-926FT0005 → B116-026FT0005 → B116-036FT0005 → B116-036ET0015 → B116-036ET0016 → END
B1-DB-69601 | -P20 | 07 |  | PE-L1-3C6-01 | PE-L1-3C6-01 | ACC-B1-048-009 |  |  | 1 | 339 | B1-DB-69601-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-01 | 1 | 230 | N | 205 | AIR COOLED CONDENSER | B1-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(GH)-16121 | ACC STREET 2 FAN 1 GEARBOX OIL HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006BT0031 → B169-006BT0009 → B169-006BT0010 → B169-006BT0044 → D0113-L32 → M0113 → D0115-L21 → M0115 → B116-916GT0008 → B116-016GT0008 → B116-926GT0008 → B116-026GT0008 → B116-036GT0008 → B116-036GT0018 → B116-036GT0020 → END
B1-DB-69601 | -P20 | 08 |  | PE-L1-3C6-02 | PE-L1-3C6-02 | ACC-B1-048-010 |  |  | 1 | 340 | B1-DB-69601-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-02 | 1 | 230 | N | 200 | AIR COOLED CONDENSER | B1-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(GH)-16122 | ACC STREET 2 FAN 2 GEARBOX OIL HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006BT0031 → B169-006BT0009 → B169-006BT0010 → B169-006BT0044 → D0113-L32 → M0113 → D0115-L21 → M0115 → B116-916GT0008 → B116-016GT0008 → B116-926GT0008 → B116-026GT0008 → B116-036GT0008 → B116-036GT0018 → END
B1-DB-69601 | -P20 | 09 |  | PE-L1-3C6-02 | PE-L1-3C6-02 | ACC-B1-048-011 |  |  | 1 | 341 | B1-DB-69601-P2009 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-02 | 1 | 230 | N | 220 | AIR COOLED CONDENSER | B1-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(GH)-16123 | ACC STREET 2 FAN 3 GEARBOX OIL HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006BT0017 → B169-006BT0018 → B169-006BT0054 → B169-006BT0005 → B169-006BT0006 → B169-006BT0047 → D0114-L21 → M0114 → D0112-L21 → M0113 → D0115-L21 → M0115 → B116-916GT0008 → B116-016GT0008 → B116-926GT0008 → B116-026GT0008 → B116-036GT0008 → B116-036GT0018 → END
B1-DB-69601 | -P20 | 10 |  | PE-L1-3C6-04 | PE-L1-3C6-04 | ACC-B1-048-012 |  |  | 1 | 342 | B1-DB-69601-P2010 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-04 | 1 | 230 | N | 200 | AIR COOLED CONDENSER | B1-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(GH)-16124 | ACC STREET 2 FAN 4 GEARBOX OIL HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006BT0017 → B169-006BT0018 → B169-006BT0054 → B169-006BT0005 → B169-006BT0006 → B169-006BT0047 → D0114-L24 → M0114 → D0116-L21 → M0116 → B116-916HT0007 → B116-016HT0007 → B116-926HT0007 → B116-026HT0007 → B116-036HT0007 → B116-036GT0018 → END
B1-DB-69601 | -P20 | 11 |  | PE-L1-3C6-04 | PE-L1-3C6-04 | ACC-B1-048-013 |  |  | 1 | 343 | B1-DB-69601-P2011 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-04 | 1 | 230 | N | 210 | AIR COOLED CONDENSER | B1-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(GH)-16125 | ACC STREET 2 FAN 5 GEARBOX OIL HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006BT0017 → B169-006BT0018 → B169-006BT0054 → B169-006BT0005 → B169-006BT0006 → B169-006BT0047 → D0114-L21 → M0114 → D0116-L21 → M0116 → B116-916HT0007 → B116-016HT0007 → B116-926HT0007 → B116-026HT0007 → B116-036HT0007 → B116-036GT0018 → END
B1-DB-69601 | -P20 | 12 |  | PE-L1-3C6-02 | PE-L1-3C6-02 | ACC-B1-048-014 |  |  | 1 | 344 | B1-DB-69601-P2012 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-02 | 1 | 230 | N | 220 | AIR COOLED CONDENSER | B1-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(GH)-16126 | ACC STREET 2 FAN 6 GEARBOX OIL HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006BT0017 → B169-006BT0018 → B169-006BT0054 → B169-006BT0005 → B169-006BT0006 → B169-006BT0047 → D0114-L22 → M0114 → D0116-L21 → M0116 → B116-916HT0007 → B116-016HT0007 → B116-926HT0007 → B116-026HT0007 → B116-036HT0007 → B116-036GT0018 → B116-036GT0019 → END
B1-DB-69603 | -P20 | 01 |  | PE-L1-3C6-04 | PE-L1-3C6-04 | ACC-B1-048-015 |  |  | 1 | 345 | B1-DB-69603-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-04 | 1 | 230 | N | 170 | AIR COOLED CONDENSER | B1-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(GH)-16131 | ACC STREET 3 FAN 1 GEARBOX OIL HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006DT0045 → D0113-L44 → M0113 → D0115-L23 → M0115 → B116-916AT0002 → B116-016AT0002 → B116-926AT0002 → B116-026AT0002 → B116-036AT0002 → B116-036AT0009 → B116-036AT0011 → END
B1-DB-69603 | -P20 | 02 |  | PE-L1-3C6-04 | PE-L1-3C6-04 | ACC-B1-048-016 |  |  | 1 | 346 | B1-DB-69603-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-04 | 1 | 230 | N | 160 | AIR COOLED CONDENSER | B1-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(GH)-16132 | ACC STREET 3 FAN 2 GEARBOX OIL HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006DT0045 → D0113-L44 → M0113 → D0115-L23 → M0115 → B116-916AT0002 → B116-016AT0002 → B116-926AT0002 → B116-026AT0002 → B116-036AT0002 → B116-036AT0009 → END
B1-DB-69603 | -P20 | 03 |  | PE-L1-3C6-04 | PE-L1-3C6-04 | ACC-B1-048-017 |  |  | 1 | 347 | B1-DB-69603-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-04 | 1 | 230 | N | 150 | AIR COOLED CONDENSER | B1-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(GH)-16133 | ACC STREET 3 FAN 3 GEARBOX OIL HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006DT0045 → D0113-L44 → M0113 → D0115-L23 → M0115 → B116-916AT0002 → B116-016AT0002 → B116-926AT0002 → B116-026AT0002 → B116-036AT0002 → B116-036AT0009 → END
B1-DB-69603 | -P20 | 04 |  | PE-L1-3C6-04 | PE-L1-3C6-04 | ACC-B1-048-018 |  |  | 1 | 348 | B1-DB-69603-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-04 | 1 | 230 | N | 180 | AIR COOLED CONDENSER | B1-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(GH)-16134 | ACC STREET 3 FAN 4 GEARBOX OIL HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006DT0045 → D0113-L44 → M0113 → D0112-L22 → M0114 → D0116-L14 → M0116 → B116-916BT0001 → B116-016BT0001 → B116-926BT0001 → B116-026BT0001 → B116-036BT0001 → B116-036AT0009 → END
B1-DB-69603 | -P20 | 05 |  | PE-L1-3C6-04 | PE-L1-3C6-04 | ACC-B1-048-019 |  |  | 1 | 349 | B1-DB-69603-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-04 | 1 | 230 | N | 190 | AIR COOLED CONDENSER | B1-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(GH)-16135 | ACC STREET 3 FAN 5 GEARBOX OIL HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006DT0045 → D0113-L44 → M0113 → D0112-L22 → M0114 → D0116-L14 → M0116 → B116-916BT0001 → B116-016BT0001 → B116-926BT0001 → B116-026BT0001 → B116-036BT0001 → B116-036AT0009 → END
B1-DB-69603 | -P20 | 06 |  | PE-L1-3C6-04 | PE-L1-3C6-04 | ACC-B1-048-020 |  |  | 1 | 350 | B1-DB-69603-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-04 | 1 | 230 | N | 200 | AIR COOLED CONDENSER | B1-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(GH)-16136 | ACC STREET 3 FAN 6 GEARBOX OIL HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006ET0045 → D0113-L44 → M0113 → D0112-L22 → M0114 → D0116-L14 → M0116 → B116-916BT0001 → B116-016BT0001 → B116-926BT0001 → B116-026BT0001 → B116-036BT0001 → B116-036AT0009 → B116-036AT0010 → END
B1-DB-69603 | -P20 | 07 |  | PE-L1-3C6-04 | PE-L1-3C6-04 | ACC-B1-048-021 |  |  | 1 | 351 | B1-DB-69603-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-04 | 1 | 230 | N | 160 | AIR COOLED CONDENSER | B1-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(GH)-16141 | ACC STREET 4 FAN 1 GEARBOX OIL HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006ET0003 → B169-006ET0045 → D0113-L44 → M0113 → D0115-L23 → M0115 → B116-916DT0004 → B116-016DT0004 → B116-926DT0004 → B116-026DT0004 → B116-036DT0004 → B116-036CT0012 → B116-036CT0014 → END
B1-DB-69603 | -P20 | 08 |  | PE-L1-3C6-03 | PE-L1-3C6-03 | ACC-B1-048-022 |  |  | 1 | 352 | B1-DB-69603-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-03 | 1 | 230 | N | 150 | AIR COOLED CONDENSER | B1-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(GH)-16142 | ACC STREET 4 FAN 2 GEARBOX OIL HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006ET0003 → B169-006ET0045 → D0113-L44 → M0113 → D0115-L23 → M0115 → B116-916DT0004 → B116-016DT0004 → B116-926DT0004 → B116-026DT0004 → B116-036DT0004 → B116-036CT0012 → END
B1-DB-69603 | -P20 | 09 |  | PE-L1-3C6-03 | PE-L1-3C6-03 | ACC-B1-048-023 |  |  | 1 | 353 | B1-DB-69603-P2009 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-03 | 1 | 230 | N | 130 | AIR COOLED CONDENSER | B1-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(GH)-16143 | ACC STREET 4 FAN 3 GEARBOX OIL HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006ET0003 → B169-006ET0045 → D0113-L44 → M0113 → D0115-L23 → M0115 → B116-916DT0004 → B116-016DT0004 → B116-926DT0004 → B116-026DT0004 → B116-036DT0004 → B116-036CT0012 → END
B1-DB-69603 | -P20 | 10 |  | PE-L1-3C6-03 | PE-L1-3C6-03 | ACC-B1-048-024 |  |  | 1 | 354 | B1-DB-69603-P2010 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-03 | 1 | 230 | N | 160 | AIR COOLED CONDENSER | B1-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(GH)-16144 | ACC STREET 4 FAN 4 GEARBOX OIL HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006ET0003 → B169-006ET0045 → D0113-L44 → M0113 → D0112-L22 → M0114 → D0116-L14 → M0116 → B116-916CT0003 → B116-016CT0003 → B116-926CT0003 → B116-026CT0003 → B116-036CT0003 → B116-036CT0012 → END
B1-DB-69603 | -P20 | 11 |  | PE-L1-3C6-03 | PE-L1-3C6-03 | ACC-B1-048-025 |  |  | 1 | 355 | B1-DB-69603-P2011 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-03 | 1 | 230 | N | 170 | AIR COOLED CONDENSER | B1-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(GH)-16145 | ACC STREET 4 FAN 5 GEARBOX OIL HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006BT0031 → B169-006BT0009 → B169-006BT0010 → B169-006BT0044 → D0113-L44 → M0113 → D0115-L23 → M0115 → B116-916CT0003 → B116-016CT0003 → B116-926CT0003 → B116-026CT0003 → B116-036CT0003 → B116-036CT0012 → END
B1-DB-69603 | -P20 | 12 |  | PE-L1-3C6-03 | PE-L1-3C6-03 | ACC-B1-048-026 |  |  | 1 | 356 | B1-DB-69603-P2012 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-03 | 1 | 230 | N | 180 | AIR COOLED CONDENSER | B1-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-C(GH)-16146 | ACC STREET 4 FAN 6 GEARBOX OIL HEATER | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, N, PE | B169-006BT0031 → B169-006BT0009 → B169-006BT0010 → B169-006BT0044 → D0113-L44 → M0113 → D0115-L23 → M0115 → B116-916CT0003 → B116-016CT0003 → B116-926CT0003 → B116-026CT0003 → B116-036CT0003 → B116-036CT0012 → B116-036CT0013 → END
B1-SWG-69603 | -P20 | 37 |  | PE-L1-4C95/50-18 | PE-L1-4C95/50-18 | ACC-B1-048-001 |  |  | 1 | 357 | B1-SWG-69603-P2037 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-18 | 185 | 400 | N | 40 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-P(M)-16070 | ACC LRVP A MOTOR | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-006AT0009 → B169-006AT0010 → B169-006AT0011 → B016-006AC0005 → END
B1-SWG-69603 | -P20 | 38 |  | PE-L1-4C95/50-18 | PE-L1-4C95/50-18 |  |  |  | 1 | 358 | B1-SWG-69603-P2038 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-18 | 185 | 400 | N | 40 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-P(M)-16070 | ACC LRVP A MOTOR | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-006AT0009 → B169-006AT0010 → B169-006AT0011 → B016-006AC0006 → END
B1-SWG-69603 | -P20 | 39 | 재배정 | PE-L1-3C4-06 | PE-L1-3C4-14 | ACC-B1-048-002 |  |  | 1 | 359 | B1-SWG-69603-P2039 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-14 | 1.16 | 230 | N | 40 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-P(MH)-16070 | ACC LRVP A MOTOR SPACE HEATER | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0009 → B169-006AT0010 → B169-006AT0011 → B016-007AC0003 → END
B1-SWG-69603 | -P20 | 40 |  | PE-L1-4C95/50-18 | PE-L1-4C95/50-18 | ACC-B1-049 |  |  | 1 | 360 | B1-SWG-69603-P2040 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-18 | 185 | 400 | N | 60 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-P(M)-16080 | ACC LRVP B MOTOR | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-007AT0002 → B169-007AT0003 → B169-007AT0004 → B169-007AT0005 → B169-007AT0006 → B016-006AC0003 → END
B1-SWG-69603 | -P20 | 41 |  | PE-L1-4C95/50-18 | PE-L1-4C95/50-18 |  |  |  | 1 | 361 | B1-SWG-69603-P2041 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-18 | 185 | 400 | N | 60 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-P(M)-16080 | ACC LRVP B MOTOR | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-007AT0002 → B169-007AT0003 → B169-007AT0004 → B169-007AT0005 → B169-007AT0006 → B016-006AC0004 → END
B1-SWG-69603 | -P20 | 42 |  | PE-L1-3C4-06 | PE-L1-3C4-06 | ACC-B1-050 |  |  | 1 | 362 | B1-SWG-69603-P2042 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-06 | 0.16 | 230 | N | 60 | AIR COOLED CONDENSER | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-P(MH)-16080 | ACC LRVP B MOTOR SPACE HEATER | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0009 → B169-006AT0010 → B169-006AT0011 → B169-006AT0012 → B169-006AT0013 → B016-007AC0002 → END
B1-SWG-69601 | -P20 | 37 |  | PE-L1-4C95/50-18 | PE-L1-4C95/50-18 | ACC-B1-051 |  |  | 1 | 363 | B1-SWG-69601-P2037 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-18 | 185 | 400 | N | 80 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-P(M)-16090 | ACC LRVP C MOTOR | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-006AT0016 → B169-006AT0017 → B169-006AT0018 → B169-006AT0019 → B169-006AT0020 → B169-006AT0021 → B169-006AT0039 → B016-006AC0001 → END
B1-SWG-69601 | -P20 | 38 |  | PE-L1-4C95/50-18 | PE-L1-4C95/50-18 |  |  |  | 1 | 364 | B1-SWG-69601-P2038 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-18 | 185 | 400 | N | 80 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-P(M)-16090 | ACC LRVP C MOTOR | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-006AT0016 → B169-006AT0017 → B169-006AT0018 → B169-006AT0019 → B169-006AT0020 → B169-006AT0021 → B169-006AT0039 → B016-006AC0002 → END
B1-SWG-69601 | -P20 | 39 | 재배정 | PE-L1-3C4-04 | PE-L1-3C4-16 | ACC-B1-052 |  |  | 1 | 365 | B1-SWG-69601-P2039 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-16 | 0.16 | 230 | N | 80 | AIR COOLED CONDENSER | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-P(MH)-16090 | ACC LRVP C MOTOR SPACE HEATER | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0016 → B169-006AT0017 → B169-006AT0018 → B169-006AT0019 → B169-006AT0020 → B169-006AT0021 → B169-006AT0039 → B016-007AC0001 → END
B1-MCC-69603 | -P20 | 01 |  | PE-L1-4C4-03 | PE-L1-4C4-03 | ACC-B1-052-001 |  |  | 1 | 366 | B1-MCC-69603-P2001 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-03 | 1 | 400 | N | 50 | AIR COOLED CONDENSER | B1-MCC-69603 | 400V MCC FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-MOV-16075 | ACC LRVP A COOLING WATER INLET MOV | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-006AT0009 → B169-006AT0010 → B169-006AT0011 → B016-017AC0011 → B016-006AC0018 → END
B1-MCC-69603 | -P20 | 02 |  | PE-L1-4C4-03 | PE-L1-4C4-03 | ACC-B1-052-002 |  |  | 1 | 367 | B1-MCC-69603-P2002 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-03 | 1 | 400 | N | 70 | AIR COOLED CONDENSER | B1-MCC-69603 | 400V MCC FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-MOV-16085 | ACC LRVP B COOLING WATER INLET MOV | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-006AT0009 → B169-006AT0010 → B169-006AT0011 → B169-006AT0012 → B169-006AT0013 → B016-017AC0010 → B016-006AC0017 → END
B1-MCC-69601 | -P20 | 01 |  | PE-L1-4C4-03 | PE-L1-4C4-03 | ACC-B1-052-003 |  |  | 1 | 368 | B1-MCC-69601-P2001 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-03 | 1 | 400 | N | 90 | AIR COOLED CONDENSER | B1-MCC-69601 | 400V MCC FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-MOV-16095 | ACC LRVP C COOLING WATER INLET MOV | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-006AT0016 → B169-006AT0017 → B169-006AT0018 → B169-006AT0019 → B169-006AT0020 → B169-006AT0021 → B169-006AT0039 → B016-017AC0007 → B016-006AC0016 → END
B1-MCC-69603 | -P20 | 03 |  | PE-L1-4C4-03 | PE-L1-4C4-03 | ACC-B1-052-004 |  |  | 1 | 369 | B1-MCC-69603-P2003 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-03 | 0.3 | 400 | N | 50 | AIR COOLED CONDENSER | B1-MCC-69603 | 400V MCC FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-MOV-16073 | ACC LRVP A MOTIVE LINE MOV | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-006AT0009 → B169-006AT0010 → B169-006AT0011 → B016-017AC0012 → B016-006AC0018 → END
B1-MCC-69603 | -P20 | 04 |  | PE-L1-4C4-03 | PE-L1-4C4-03 | ACC-B1-052-005 |  |  | 1 | 370 | B1-MCC-69603-P2004 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-03 | 0.3 | 400 | N | 70 | AIR COOLED CONDENSER | B1-MCC-69603 | 400V MCC FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-MOV-16083 | ACC LRVP B MOTIVE LINE MOV | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-006AT0009 → B169-006AT0010 → B169-006AT0011 → B169-006AT0012 → B169-006AT0013 → B016-017AC0009 → B016-006AC0017 → END
B1-MCC-69601 | -P20 | 02 |  | PE-L1-4C4-03 | PE-L1-4C4-03 | ACC-B1-052-006 |  |  | 1 | 371 | B1-MCC-69601-P2002 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-03 | 0.3 | 400 | N | 90 | AIR COOLED CONDENSER | B1-MCC-69601 | 400V MCC FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-MOV-16093 | ACC LRVP C MOTIVE LINE MOV | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-006AT0016 → B169-006AT0017 → B169-006AT0018 → B169-006AT0019 → B169-006AT0020 → B169-006AT0021 → B169-006AT0039 → B016-017AC0006 → B016-006AC0016 → END
B1-MCC-64602 | -P20 | 07 |  | PE-L1-4C35/25-01 | PE-L1-4C35/25-01 | ACC-B1-053 |  |  | 1 | 372 | B1-MCC-64602-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 35sqmm + 1C X 25sqmm | PE-L1-4C35/25-01 | 18.5 | 400 | N | 380 | AIR COOLED CONDENSER | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-P(M)-16021 | STEAM TURBINE EXHAUST DUCT DRAIN PUMP A | 1.1_MAIN BUILDING COMPLEX (BELOW ACCDUCT NEARYBY ST) | L1, L2, L3, PE | B164-016ET0106 → B164-996ET0022 → M0504 → D0531-L26 → M0510 → D0517-L15 → M0501 → D0503-L37 → M0502 → D0504-L37 → M0503 → D0501-L37 → M0328 → D0324-L37 → M0329 → B114-997AT0021 → B114-017AT0020 → B114-017AT0019 → B114-017AT0018 → B114-017AT0017 → B114-017AT0016 → B114-017AT0015 → B114-017AT0014 → B113-016BC0032 → B113-006AC0002 → B113-016AC0001 → B113-016AC0003 → END
B1-MCC-64601 | -P20 | 04 |  | PE-L1-4C35/25-01 | PE-L1-4C35/25-01 | ACC-B1-054 |  |  | 1 | 373 | B1-MCC-64601-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 35sqmm + 1C X 25sqmm | PE-L1-4C35/25-01 | 18.5 | 400 | N | 380 | AIR COOLED CONDENSER | B1-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-P(M)-16022 | STEAM TURBINE EXHAUST DUCT DRAIN PUMP B | 1.1_MAIN BUILDING COMPLEX (BELOW ACCDUCT NEARYBY ST) | L1, L2, L3, PE | B164-016CT0098 → B164-016CT0099 → B164-996CT0022 → M0504 → D0531-L27 → M0510 → D0517-L26 → M0501 → D0503-L38 → M0502 → D0504-L38 → M0503 → D0501-L38 → M0328 → D0324-L38 → M0329 → B114-996BT0046 → B114-016BT0045 → B114-016BT0044 → B114-016BT0043 → B114-016BT0042 → B114-016BT0041 → B114-016BT0040 → B114-016BT0039 → B113-016BC0033 → B113-006AC0003 → B113-016AC0002 → B113-016AC0004 → END
B1-MCC-69603 | -P20 | 05 |  | PE-L1-4C6-01 | PE-L1-4C6-01 | ACC-B1-058 |  |  | 1 | 374 | B1-MCC-69603-P2005 | 0.6/1kV CU/XLPE/LSZH | 4C x 6sqmm | PE-L1-4C6-01 | 5 | 400 | N | 300 | AIR COOLED CONDENSER | B1-MCC-69603 | 400V MCC FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-HO(M)-16001 | ACC ELECTRICAL HOIST FOR MAINTENANCE | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006CT0001 → B169-006CT0002 → B169-006CT0003 → B169-006CT0045 → D0113-L44 → M0113 → D0112-L25 → M0114 → D0116-L14 → M0116 → B116-916FT0005 → B116-016FT0005 → B116-926FT0005 → B116-026FT0005 → B116-036FT0005 → B116-036ET0015 → B116-036ET0016 → B116-036CC0006 → B116-936CC0006 → END
B1-MCC-69601 | -P20 | 03 |  | PE-L1-5C25/16-01 | PE-L1-5C25/16-01 | ACC-B1-059 |  |  | 1 | 375 | B1-MCC-69601-P2003 | 0.6/1kV CU/XLPE/LSZH | 4C x 25sqmm + 1C X 16sqmm | PE-L1-5C25/16-01 | 15 | 400 | N | 220 | AIR COOLED CONDENSER | B1-MCC-69601 | 400V MCC FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, N, PE | B1-HTP-16601 | ACC HEAT TRACING PANEL | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, N, PE | B169-006BT0016 → B169-006BT0031 → B169-006BT0009 → B169-006BT0010 → B169-006BT0044 → D0113-L23 → M0113 → D0115-L15 → M0115 → B116-916DT0004 → B116-016DT0004 → B116-926DT0004 → B116-026DT0004 → B116-036DT0004 → B116-036CT0012 → B116-036CT0014 → B116-936CT0021 → B116-026CT0021 → B116-926CT0021 → B116-016CT0021 → END
B1-MCC-69603 | -P20 | 06 |  | PE-L1-5C50/25-01 | PE-L1-5C50/25-01 | ACC-B1-059-001 |  |  | 1 | 376 | B1-MCC-69603-P2006 | 0.6/1kV CU/XLPE/LSZH | 4C x 50sqmm + 1C X 25sqmm | PE-L1-5C50/25-01 | 15 | 400 | N | 240 | AIR COOLED CONDENSER | B1-MCC-69603 | 400V MCC FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, N, PE | B1-LP-16601 | ACC LIGHTING PANEL | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, N, PE | B169-006AT0009 → B169-006AT0010 → B169-006AT0044 → D0113-L31 → M0113 → D0112-L25 → M0114 → D0116-L22 → M0116 → B116-916DT0004 → B116-016DT0004 → B116-926DT0004 → B116-026DT0004 → B116-036DT0004 → B116-036CT0012 → B116-036CT0014 → END
B1-MCC-69603 | -P20 | 07 |  | PE-L1-5C95/50-05 | PE-L1-5C95/50-05 | ACC-B1-059-002 |  |  | 1 | 377 | B1-MCC-69603-P2007 | 0.6/1kV CU/XLPE/LSZH | 4C x 95sqmm + 1C X 50sqmm | PE-L1-5C95/50-05 | 37 | 400 | N | 250 | AIR COOLED CONDENSER | B1-MCC-69603 | 400V MCC FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, N, PE | B1-RP-16601 | ACC POWER SOCKET PANEL | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, N, PE | B169-006CT0001 → B169-006CT0002 → B169-006CT0003 → B169-006CT0045 → D0113-L31 → M0113 → D0112-L25 → M0114 → D0116-L15 → M0116 → B116-916DT0004 → B116-016DT0004 → B116-926DT0004 → B116-026DT0004 → B116-036DT0004 → B116-036CT0012 → B116-036CT0014 → END
B1-MCC-69603 | -P20 | 08 |  | PE-L1-4C4-03 | PE-L1-4C4-03 | ACC-B1-061 |  |  | 1 | 378 | B1-MCC-69603-P2008 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-03 | 1 | 400 | N | 330 | AIR COOLED CONDENSER | B1-MCC-69603 | 400V MCC FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-MOV-16001 | ACC VACUUM BREAKER MOV A | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006CT0001 → B169-006CT0002 → B169-006CT0003 → B169-006CT0045 → D0113-L21 → M0113 → D0115-L11 → M0115 → B116-916DT0004 → B116-016DT0004 → B116-926DT0004 → B116-026DT0004 → B116-036DT0004 → B116-036CT0012 → B116-036CT0014 → B116-936CT0022 → B116-036CT0022 → B116-026CT0022 → B116-926CT0022 → B116-026CT0023 → B116-926CT0024 → B116-026CT0024 → B116-926CC0003 → END
B1-MCC-69603 | -P20 | 09 |  | PE-L1-4C4-03 | PE-L1-4C4-03 | ACC-B1-061-001 |  |  | 1 | 379 | B1-MCC-69603-P2009 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-03 | 1 | 400 | N | 330 | AIR COOLED CONDENSER | B1-MCC-69603 | 400V MCC FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-MOV-16002 | ACC VACUUM BREAKER MOV B | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006CT0001 → B169-006CT0002 → B169-006CT0003 → B169-006CT0045 → D0113-L44 → M0113 → D0115-L23 → M0115 → B116-916DT0004 → B116-016DT0004 → B116-926DT0004 → B116-026DT0004 → B116-036DT0004 → B116-036CT0012 → B116-036CT0014 → B116-936CT0022 → B116-036CT0022 → B116-026CT0022 → B116-926CT0022 → B116-026CT0023 → B116-926CT0024 → B116-026CT0024 → B116-926CC0004 → END
B1-MCC-69601 | -P20 | 04 |  | PE-L1-4C4-03 | PE-L1-4C4-03 | ACC-B1-064 |  |  | 1 | 380 | B1-MCC-69601-P2004 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-03 | 1 | 400 | N | 80 | AIR COOLED CONDENSER | B1-MCC-69601 | 400V MCC FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-MOV-16071 | ACC LRVP A AIR INLET MOV | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-006AT0017 → B169-006AT0018 → B169-006AT0019 → B169-006AT0033 → B169-006AT0012 → B016-017AC0013 → B016-006AC0018 → END
B1-MCC-69601 | -P20 | 05 |  | PE-L1-4C4-03 | PE-L1-4C4-03 | ACC-B1-065 |  |  | 1 | 381 | B1-MCC-69601-P2005 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-03 | 1 | 400 | N | 70 | AIR COOLED CONDENSER | B1-MCC-69601 | 400V MCC FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-MOV-16081 | ACC LRVP B AIR INLET MOV | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-006AT0017 → B169-006AT0018 → B169-006AT0019 → B169-006AT0033 → B169-006AT0013 → B016-017AC0008 → B016-006AC0017 → END
B1-MCC-69601 | -P20 | 06 |  | PE-L1-4C4-03 | PE-L1-4C4-03 | ACC-B1-066 |  |  | 1 | 382 | B1-MCC-69601-P2006 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-03 | 1 | 400 | N | 90 | AIR COOLED CONDENSER | B1-MCC-69601 | 400V MCC FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-MOV-16091 | ACC LRVP C AIR INLET MOV | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-006AT0016 → B169-006AT0017 → B169-006AT0018 → B169-006AT0019 → B169-006AT0020 → B169-006AT0021 → B169-006AT0039 → B016-017AC0005 → B016-006AC0016 → END
B1-MCC-69601 | -P20 | 07 |  | PE-L1-4C4-04 | PE-L1-4C4-04 | ACC-B1-067 |  |  | 1 | 383 | B1-MCC-69601-P2007 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-04 | 1 | 400 | N | 250 | AIR COOLED CONDENSER | B1-MCC-69601 | 400V MCC FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-MOV-16005 | ACC QUICK AIR TAKEOFF MOV | 2.1_AIR COOLED CONDENSER (ACC) #1 | L1, L2, L3, PE | B169-006BT0016 → B169-006BT0031 → B169-006BT0009 → B169-006BT0010 → B169-006BT0044 → D0113-L21 → M0113 → D0115-L11 → M0115 → B116-916DT0004 → B116-016DT0004 → B116-926DT0004 → B116-026DT0004 → B116-036DT0004 → B116-036CT0012 → B116-036CT0014 → B116-936CT0022 → B116-036CT0022 → B116-026CT0022 → B116-926CT0022 → B116-026CT0023 → B116-026CC0002 → END
B2-SWG-69601 | -P20 | 01 |  | PE-L1-4C95/50-03 | PE-L1-4C95/50-03 | ACC-B2-001 |  |  | 1 | 384 | B2-SWG-69601-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-03 | 160 | 400 | N | 180 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16111 | ACC STREET 1 FAN 1 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006BT0025 → B269-006BT0048 → D0106-L23 → M0107 → D0108-L22 → M0109 → B216-916DT0004 → B216-016DT0004 → B216-926DT0004 → B216-026DT0004 → B216-036DT0004 → B216-036CT0012 → B216-036CT0014 → END
B2-SWG-69601 | -P20 | 02 |  | PE-L1-4C95/50-03 | PE-L1-4C95/50-03 |  |  |  | 1 | 385 | B2-SWG-69601-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-03 | 160 | 400 | N | 180 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16111 | ACC STREET 1 FAN 1 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006BT0025 → B269-006BT0048 → D0106-L23 → M0107 → D0108-L22 → M0109 → B216-916DT0004 → B216-016DT0004 → B216-926DT0004 → B216-026DT0004 → B216-036DT0004 → B216-036CT0012 → B216-036CT0014 → END
B2-SWG-69601 | -P20 | 03 |  | PE-L1-4C95/50-10 | PE-L1-4C95/50-10 | ACC-B2-002 |  |  | 1 | 386 | B2-SWG-69601-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-10 | 160 | 400 | N | 160 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16112 | ACC STREET 1 FAN 2 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006BT0025 → B269-006BT0048 → D0106-L21 → M0107 → D0108-L11 → M0109 → B216-916DT0004 → B216-016DT0004 → B216-926DT0004 → B216-026DT0004 → B216-036DT0004 → B216-036CT0012 → END
B2-SWG-69601 | -P20 | 04 |  | PE-L1-4C95/50-10 | PE-L1-4C95/50-10 |  |  |  | 1 | 387 | B2-SWG-69601-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-10 | 160 | 400 | N | 160 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16112 | ACC STREET 1 FAN 2 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006BT0025 → B269-006BT0048 → D0106-L21 → M0107 → D0108-L11 → M0109 → B216-916DT0004 → B216-016DT0004 → B216-926DT0004 → B216-026DT0004 → B216-036DT0004 → B216-036CT0012 → END
B2-SWG-69601 | -P20 | 05 |  | PE-L1-4C95/50-10 | PE-L1-4C95/50-10 | ACC-B2-003 |  |  | 1 | 388 | B2-SWG-69601-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-10 | 160 | 400 | N | 160 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16113 | ACC STREET 1 FAN 3 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006BT0025 → B269-006BT0048 → D0106-L23 → M0107 → D0108-L22 → M0109 → B216-916DT0004 → B216-016DT0004 → B216-926DT0004 → B216-026DT0004 → B216-036DT0004 → B216-036CT0012 → END
B2-SWG-69601 | -P20 | 06 |  | PE-L1-4C95/50-10 | PE-L1-4C95/50-10 |  |  |  | 1 | 389 | B2-SWG-69601-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-10 | 160 | 400 | N | 160 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16113 | ACC STREET 1 FAN 3 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006BT0025 → B269-006BT0048 → D0106-L22 → M0107 → D0108-L12 → M0109 → B216-916DT0004 → B216-016DT0004 → B216-926DT0004 → B216-026DT0004 → B216-036DT0004 → B216-036CT0012 → END
B2-SWG-69601 | -P20 | 07 |  | PE-L1-4C95/50-02 | PE-L1-4C95/50-02 | ACC-B2-004 |  |  | 1 | 390 | B2-SWG-69601-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-02 | 160 | 400 | N | 160 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16114 | ACC STREET 1 FAN 4 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006BT0025 → B269-006BT0048 → D0106-L22 → M0107 → D0108-L12 → M0109 → B216-916CT0003 → B216-016CT0003 → B216-926CT0003 → B216-026CT0003 → B216-036CT0003 → B216-036CT0012 → END
B2-SWG-69601 | -P20 | 08 |  | PE-L1-4C95/50-02 | PE-L1-4C95/50-02 |  |  |  | 1 | 391 | B2-SWG-69601-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-02 | 160 | 400 | N | 160 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16114 | ACC STREET 1 FAN 4 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006BT0025 → B269-006BT0048 → D0106-L22 → M0107 → D0108-L12 → M0109 → B216-916CT0003 → B216-016CT0003 → B216-926CT0003 → B216-026CT0003 → B216-036CT0003 → B216-036CT0012 → END
B2-SWG-69601 | -P20 | 09 |  | PE-L1-4C95/50-03 | PE-L1-4C95/50-03 | ACC-B2-005 |  |  | 1 | 392 | B2-SWG-69601-P2009 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-03 | 160 | 400 | N | 170 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16115 | ACC STREET 1 FAN 5 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006BT0026 → B269-006BT0027 → B269-006BT0051 → D0107-L33 → M0108 → D0109-L23 → M0110 → B216-916CT0003 → B216-016CT0003 → B216-926CT0003 → B216-026CT0003 → B216-036CT0003 → B216-036CT0012 → END
B2-SWG-69601 | -P20 | 10 |  | PE-L1-4C95/50-03 | PE-L1-4C95/50-03 |  |  |  | 1 | 393 | B2-SWG-69601-P2010 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-03 | 160 | 400 | N | 170 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16115 | ACC STREET 1 FAN 5 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006BT0026 → B269-006BT0027 → B269-006BT0051 → D0107-L33 → M0108 → D0109-L23 → M0110 → B216-916CT0003 → B216-016CT0003 → B216-926CT0003 → B216-026CT0003 → B216-036CT0003 → B216-036CT0012 → END
B2-SWG-69601 | -P20 | 11 |  | PE-L1-4C95/50-12 | PE-L1-4C95/50-12 | ACC-B2-006 |  |  | 1 | 394 | B2-SWG-69601-P2011 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-12 | 160 | 400 | N | 180 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16116 | ACC STREET 1 FAN 6 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006BT0026 → B269-006BT0027 → B269-006BT0051 → D0107-L33 → M0108 → D0109-L23 → M0110 → B216-916CT0003 → B216-016CT0003 → B216-926CT0003 → B216-026CT0003 → B216-036CT0003 → B216-036CT0012 → B216-036CT0013 → END
B2-SWG-69601 | -P20 | 12 |  | PE-L1-4C95/50-12 | PE-L1-4C95/50-12 |  |  |  | 1 | 395 | B2-SWG-69601-P2012 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-12 | 160 | 400 | N | 180 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16116 | ACC STREET 1 FAN 6 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006BT0026 → B269-006BT0027 → B269-006BT0051 → D0107-L33 → M0108 → D0109-L23 → M0110 → B216-916CT0003 → B216-016CT0003 → B216-926CT0003 → B216-026CT0003 → B216-036CT0003 → B216-036CT0012 → B216-036CT0013 → END
B2-SWG-69601 | -P20 | 13 | 현장포설일정 변경으로 인한 Drum 재배정(7/28) | PE-L1-5C95/50-03 | PE-L1-5C95/50-03 | ACC-B2-007 |  |  | 1 | 396 | B2-SWG-69601-P2013 | 0.6/1kV CU/XLPE/LSZH | 4C x 95sqmm + 1C X 50sqmm | PE-L1-5C95/50-03 | 160 | 400 | N | 210 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16121 | ACC STREET 2 FAN 1 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006BT0026 → B269-006BT0027 → B269-006BT0051 → D0107-L34 → M0108 → D0105-L25 → M0107 → D0108-L23 → M0109 → B216-916AT0002 → B216-016AT0002 → B216-926AT0002 → B216-026AT0002 → B216-036AT0002 → B216-036AT0009 → B216-036AT0011 → END
B2-SWG-69601 | -P20 | 14 | 현장포설일정 변경으로 인한 Drum 재배정(7/28) | PE-L1-5C95/50-03 | PE-L1-5C95/50-03 |  |  |  | 1 | 397 | B2-SWG-69601-P2014 | 0.6/1kV CU/XLPE/LSZH | 4C x 95sqmm + 1C X 50sqmm | PE-L1-5C95/50-03 | 160 | 400 | N | 210 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16121 | ACC STREET 2 FAN 1 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006BT0026 → B269-006BT0027 → B269-006BT0051 → D0107-L34 → M0108 → D0105-L25 → M0107 → D0108-L23 → M0109 → B216-916AT0002 → B216-016AT0002 → B216-926AT0002 → B216-026AT0002 → B216-036AT0002 → B216-036AT0009 → B216-036AT0011 → END
B2-SWG-69601 | -P20 | 15 |  | PE-L1-4C95/50-28 | PE-L1-4C95/50-28 | ACC-B2-008 |  |  | 1 | 398 | B2-SWG-69601-P2015 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-28 | 160 | 400 | N | 200 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16122 | ACC STREET 2 FAN 2 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006BT0026 → B269-006BT0027 → B269-006BT0051 → D0107-L34 → M0108 → D0105-L25 → M0107 → D0108-L23 → M0109 → B216-916AT0002 → B216-016AT0002 → B216-926AT0002 → B216-026AT0002 → B216-036AT0002 → B216-036AT0009 → END
B2-SWG-69601 | -P20 | 16 |  | PE-L1-4C95/50-29 | PE-L1-4C95/50-29 |  |  |  | 1 | 399 | B2-SWG-69601-P2016 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-29 | 160 | 400 | N | 200 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16122 | ACC STREET 2 FAN 2 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006BT0026 → B269-006BT0027 → B269-006BT0051 → D0107-L34 → M0108 → D0105-L25 → M0107 → D0108-L23 → M0109 → B216-916AT0002 → B216-016AT0002 → B216-926AT0002 → B216-026AT0002 → B216-036AT0002 → B216-036AT0009 → END
B2-SWG-69601 | -P20 | 17 |  | PE-L1-4C95/50-06 | PE-L1-4C95/50-06 | ACC-B2-009 |  |  | 1 | 400 | B2-SWG-69601-P2017 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-06 | 160 | 400 | N | 190 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16123 | ACC STREET 2 FAN 3 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006BT0026 → B269-006BT0027 → B269-006BT0051 → D0107-L35 → M0108 → D0105-L15 → M0107 → D0108-L15 → M0109 → B216-916AT0002 → B216-016AT0002 → B216-926AT0002 → B216-026AT0002 → B216-036AT0002 → B216-036AT0009 → END
B2-SWG-69601 | -P20 | 18 |  | PE-L1-4C95/50-07 | PE-L1-4C95/50-07 |  |  |  | 1 | 401 | B2-SWG-69601-P2018 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-07 | 160 | 400 | N | 190 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16123 | ACC STREET 2 FAN 3 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006BT0026 → B269-006BT0027 → B269-006BT0051 → D0107-L35 → M0108 → D0105-L15 → M0107 → D0108-L15 → M0109 → B216-916AT0002 → B216-016AT0002 → B216-926AT0002 → B216-026AT0002 → B216-036AT0002 → B216-036AT0009 → END
B2-SWG-69601 | -P20 | 19 |  | PE-L1-4C95/50-12 | PE-L1-4C95/50-12 | ACC-B2-010 |  |  | 1 | 402 | B2-SWG-69601-P2019 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-12 | 160 | 400 | N | 150 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16124 | ACC STREET 2 FAN 4 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006CT0027 → B269-006CT0051 → D0107-L42 → M0108 → D0109-L11 → M0110 → B216-916BT0001 → B216-016BT0001 → B216-926BT0001 → B216-026BT0001 → B216-036BT0001 → B216-036AT0009 → END
B2-SWG-69601 | -P20 | 20 |  | PE-L1-4C95/50-12 | PE-L1-4C95/50-12 |  |  |  | 1 | 403 | B2-SWG-69601-P2020 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-12 | 160 | 400 | N | 150 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16124 | ACC STREET 2 FAN 4 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006CT0027 → B269-006CT0051 → D0107-L42 → M0108 → D0109-L11 → M0110 → B216-916BT0001 → B216-016BT0001 → B216-926BT0001 → B216-026BT0001 → B216-036BT0001 → B216-036AT0009 → END
B2-SWG-69601 | -P20 | 21 |  | PE-L1-4C95/50-04 | PE-L1-4C95/50-04 | ACC-B2-011 |  |  | 1 | 404 | B2-SWG-69601-P2021 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-04 | 160 | 400 | N | 170 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16125 | ACC STREET 2 FAN 5 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006CT0027 → B269-006CT0051 → D0107-L41 → M0108 → D0109-L21 → M0110 → B216-916BT0001 → B216-016BT0001 → B216-926BT0001 → B216-026BT0001 → B216-036BT0001 → B216-036AT0009 → END
B2-SWG-69601 | -P20 | 22 |  | PE-L1-4C95/50-04 | PE-L1-4C95/50-04 |  |  |  | 1 | 405 | B2-SWG-69601-P2022 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-04 | 160 | 400 | N | 170 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16125 | ACC STREET 2 FAN 5 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006CT0027 → B269-006CT0051 → D0107-L41 → M0108 → D0109-L21 → M0110 → B216-916BT0001 → B216-016BT0001 → B216-926BT0001 → B216-026BT0001 → B216-036BT0001 → B216-036AT0009 → END
B2-SWG-69601 | -P20 | 23 |  | PE-L1-4C95/50-04 | PE-L1-4C95/50-04 | ACC-B2-012 |  |  | 1 | 406 | B2-SWG-69601-P2023 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-04 | 160 | 400 | N | 180 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16126 | ACC STREET 2 FAN 6 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006CT0027 → B269-006CT0051 → D0107-L41 → M0108 → D0109-L21 → M0110 → B216-916BT0001 → B216-016BT0001 → B216-926BT0001 → B216-026BT0001 → B216-036BT0001 → B216-036AT0009 → B216-036AT0010 → END
B2-SWG-69601 | -P20 | 24 |  | PE-L1-4C95/50-04 | PE-L1-4C95/50-04 |  |  |  | 1 | 407 | B2-SWG-69601-P2024 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-04 | 160 | 400 | N | 180 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16126 | ACC STREET 2 FAN 6 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006CT0027 → B269-006CT0051 → D0107-L41 → M0108 → D0109-L21 → M0110 → B216-916BT0001 → B216-016BT0001 → B216-926BT0001 → B216-026BT0001 → B216-036BT0001 → B216-036AT0009 → B216-036AT0010 → END
B2-SWG-69603 | -P20 | 01 |  | PE-L1-4C95/50-06 | PE-L1-4C95/50-06 | ACC-B2-013 |  |  | 1 | 408 | B2-SWG-69603-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-06 | 160 | 400 | N | 250 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16131 | ACC STREET 3 FAN 1 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006DT0036 → B269-006DT0050 → D0107-L24 → M0108 → D0105-L22 → M0107 → D0108-L21 → M0109 → B216-916GT0008 → B216-016GT0008 → B216-926GT0008 → B216-026GT0008 → B216-036GT0008 → B216-036GT0018 → B216-036GT0020 → END
B2-SWG-69603 | -P20 | 02 |  | PE-L1-4C95/50-06 | PE-L1-4C95/50-06 |  |  |  | 1 | 409 | B2-SWG-69603-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-06 | 160 | 400 | N | 250 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16131 | ACC STREET 3 FAN 1 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006DT0036 → B269-006DT0050 → D0107-L34 → M0108 → D0105-L22 → M0107 → D0108-L21 → M0109 → B216-916GT0008 → B216-016GT0008 → B216-926GT0008 → B216-026GT0008 → B216-036GT0008 → B216-036GT0018 → B216-036GT0020 → END
B2-SWG-69603 | -P20 | 03 |  | PE-L1-4C95/50-07 | PE-L1-4C95/50-07 | ACC-B2-014 |  |  | 1 | 410 | B2-SWG-69603-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-07 | 160 | 400 | N | 240 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16132 | ACC STREET 3 FAN 2 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006DT0036 → B269-006DT0050 → D0107-L21 → M0108 → D0105-L15 → M0107 → D0108-L11 → M0109 → B216-916GT0008 → B216-016GT0008 → B216-926GT0008 → B216-026GT0008 → B216-036GT0008 → B216-036GT0018 → END
B2-SWG-69603 | -P20 | 04 |  | PE-L1-4C95/50-07 | PE-L1-4C95/50-07 |  |  |  | 1 | 411 | B2-SWG-69603-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-07 | 160 | 400 | N | 240 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16132 | ACC STREET 3 FAN 2 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006DT0036 → B269-006DT0050 → D0107-L21 → M0108 → D0105-L15 → M0107 → D0108-L11 → M0109 → B216-916GT0008 → B216-016GT0008 → B216-926GT0008 → B216-026GT0008 → B216-036GT0008 → B216-036GT0018 → END
B2-SWG-69603 | -P20 | 05 |  | PE-L1-4C95/50-29 | PE-L1-4C95/50-29 | ACC-B2-015 |  |  | 1 | 412 | B2-SWG-69603-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-29 | 160 | 400 | N | 230 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16133 | ACC STREET 3 FAN 3 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006DT0036 → B269-006DT0050 → D0107-L22 → M0108 → D0105-L24 → M0107 → D0108-L12 → M0109 → B216-916GT0008 → B216-016GT0008 → B216-926GT0008 → B216-026GT0008 → B216-036GT0008 → B216-036GT0018 → END
B2-SWG-69603 | -P20 | 06 |  | PE-L1-4C95/50-29 | PE-L1-4C95/50-29 |  |  |  | 1 | 413 | B2-SWG-69603-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-29 | 160 | 400 | N | 230 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16133 | ACC STREET 3 FAN 3 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006DT0036 → B269-006DT0050 → D0107-L22 → M0108 → D0105-L24 → M0107 → D0108-L12 → M0109 → B216-916GT0008 → B216-016GT0008 → B216-926GT0008 → B216-026GT0008 → B216-036GT0008 → B216-036GT0018 → END
B2-SWG-69603 | -P20 | 07 |  | PE-L1-4C95/50-30 | PE-L1-4C95/50-30 | ACC-B2-016 |  |  | 1 | 414 | B2-SWG-69603-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-30 | 160 | 400 | N | 210 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16134 | ACC STREET 3 FAN 4 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006DT0036 → B269-006DT0050 → D0107-L23 → M0108 → D0109-L13 → M0110 → B216-916HT0007 → B216-016HT0007 → B216-926HT0007 → B216-026HT0007 → B216-036HT0007 → B216-036GT0018 → END
B2-SWG-69603 | -P20 | 08 |  | PE-L1-4C95/50-30 | PE-L1-4C95/50-30 |  |  |  | 1 | 415 | B2-SWG-69603-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-30 | 160 | 400 | N | 210 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16134 | ACC STREET 3 FAN 4 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006DT0036 → B269-006DT0050 → D0107-L23 → M0108 → D0109-L13 → M0110 → B216-916HT0007 → B216-016HT0007 → B216-926HT0007 → B216-026HT0007 → B216-036HT0007 → B216-036GT0018 → END
B2-SWG-69603 | -P20 | 09 |  | PE-L1-4C95/50-30 | PE-L1-4C95/50-30 | ACC-B2-017 |  |  | 1 | 416 | B2-SWG-69603-P2009 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-30 | 160 | 400 | N | 220 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16135 | ACC STREET 3 FAN 5 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006DT0036 → B269-006DT0050 → D0107-L31 → M0108 → D0109-L11 → M0110 → B216-916HT0007 → B216-016HT0007 → B216-926HT0007 → B216-026HT0007 → B216-036HT0007 → B216-036GT0018 → END
B2-SWG-69603 | -P20 | 10 |  | PE-L1-4C95/50-31 | PE-L1-4C95/50-31 |  |  |  | 1 | 417 | B2-SWG-69603-P2010 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-31 | 160 | 400 | N | 220 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16135 | ACC STREET 3 FAN 5 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006DT0036 → B269-006DT0050 → D0107-L31 → M0108 → D0109-L11 → M0110 → B216-916HT0007 → B216-016HT0007 → B216-926HT0007 → B216-026HT0007 → B216-036HT0007 → B216-036GT0018 → END
B2-SWG-69603 | -P20 | 11 |  | PE-L1-4C95/50-31 | PE-L1-4C95/50-31 | ACC-B2-018 |  |  | 1 | 418 | B2-SWG-69603-P2011 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-31 | 160 | 400 | N | 220 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16136 | ACC STREET 3 FAN 6 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006ET0035 → B269-006ET0051 → D0107-L25 → M0108 → D0109-L15 → M0110 → B216-916HT0007 → B216-016HT0007 → B216-926HT0007 → B216-026HT0007 → B216-036HT0007 → B216-036GT0018 → B216-036GT0019 → END
B2-SWG-69603 | -P20 | 12 |  | PE-L1-4C95/50-33 | PE-L1-4C95/50-33 |  |  |  | 1 | 419 | B2-SWG-69603-P2012 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-33 | 160 | 400 | N | 220 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16136 | ACC STREET 3 FAN 6 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006ET0035 → B269-006ET0051 → D0107-L25 → M0108 → D0109-L15 → M0110 → B216-916HT0007 → B216-016HT0007 → B216-926HT0007 → B216-026HT0007 → B216-036HT0007 → B216-036GT0018 → B216-036GT0019 → END
B2-SWG-69603 | -P20 | 13 |  | PE-L1-4C95/50-14 | PE-L1-4C95/50-14 | ACC-B2-019 |  |  | 1 | 420 | B2-SWG-69603-P2013 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-14 | 160 | 400 | N | 260 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16141 | ACC STREET 4 FAN 1 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006ET0035 → B269-006ET0051 → D0107-L24 → M0108 → D0105-L21 → M0107 → D0108-L21 → M0109 → B216-916ET0006 → B216-016ET0006 → B216-926ET0006 → B216-026ET0006 → B216-036ET0006 → B216-036ET0015 → B216-036ET0017 → END
B2-SWG-69603 | -P20 | 14 |  | PE-L1-4C95/50-14 | PE-L1-4C95/50-14 |  |  |  | 1 | 421 | B2-SWG-69603-P2014 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-14 | 160 | 400 | N | 260 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16141 | ACC STREET 4 FAN 1 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006ET0035 → B269-006ET0051 → D0107-L24 → M0108 → D0105-L21 → M0107 → D0108-L15 → M0109 → B216-916ET0006 → B216-016ET0006 → B216-926ET0006 → B216-026ET0006 → B216-036ET0006 → B216-036ET0015 → B216-036ET0017 → END
B2-SWG-69603 | -P20 | 15 |  | PE-L1-4C95/50-33 | PE-L1-4C95/50-33 | ACC-B2-020 |  |  | 1 | 422 | B2-SWG-69603-P2015 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-33 | 160 | 400 | N | 250 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16142 | ACC STREET 4 FAN 2 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006ET0035 → B269-006ET0051 → D0107-L21 → M0108 → D0105-L21 → M0107 → D0108-L15 → M0109 → B216-916ET0006 → B216-016ET0006 → B216-926ET0006 → B216-026ET0006 → B216-036ET0006 → B216-036ET0015 → END
B2-SWG-69603 | -P20 | 16 |  | PE-L1-4C95/50-32 | PE-L1-4C95/50-32 |  |  |  | 1 | 423 | B2-SWG-69603-P2016 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-32 | 160 | 400 | N | 250 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16142 | ACC STREET 4 FAN 2 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006ET0035 → B269-006ET0051 → D0107-L21 → M0108 → D0105-L21 → M0107 → D0108-L15 → M0109 → B216-916ET0006 → B216-016ET0006 → B216-926ET0006 → B216-026ET0006 → B216-036ET0006 → B216-036ET0015 → END
B2-SWG-69603 | -P20 | 17 |  | PE-L1-4C95/50-22 | PE-L1-4C95/50-22 | ACC-B2-021 |  |  | 1 | 424 | B2-SWG-69603-P2017 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-22 | 160 | 400 | N | 220 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16143 | ACC STREET 4 FAN 3 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006ET0035 → B269-006ET0051 → D0107-L32 → M0108 → D0105-L23 → M0110 → B216-916ET0006 → B216-016ET0006 → B216-926ET0006 → B216-026ET0006 → B216-036ET0006 → B216-036ET0015 → END
B2-SWG-69603 | -P20 | 18 |  | PE-L1-4C95/50-22 | PE-L1-4C95/50-22 |  |  |  | 1 | 425 | B2-SWG-69603-P2018 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-22 | 160 | 400 | N | 220 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16143 | ACC STREET 4 FAN 3 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006ET0035 → B269-006ET0051 → D0107-L32 → M0108 → D0105-L23 → M0110 → B216-916ET0006 → B216-016ET0006 → B216-926ET0006 → B216-026ET0006 → B216-036ET0006 → B216-036ET0015 → END
B2-SWG-69603 | -P20 | 19 |  | PE-L1-4C95/50-27 | PE-L1-4C95/50-27 | ACC-B2-022 |  |  | 1 | 426 | B2-SWG-69603-P2019 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-27 | 160 | 400 | N | 210 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16144 | ACC STREET 4 FAN 4 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006ET0035 → B269-006ET0051 → D0107-L23 → M0108 → D0109-L13 → M0110 → B216-916FT0005 → B216-016FT0005 → B216-926FT0005 → B216-026FT0005 → B216-036FT0005 → B216-036ET0015 → END
B2-SWG-69603 | -P20 | 20 |  | PE-L1-4C95/50-32 | PE-L1-4C95/50-32 |  |  |  | 1 | 427 | B2-SWG-69603-P2020 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-32 | 160 | 400 | N | 210 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16144 | ACC STREET 4 FAN 4 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006ET0035 → B269-006ET0051 → D0107-L23 → M0108 → D0109-L13 → M0110 → B216-916FT0005 → B216-016FT0005 → B216-926FT0005 → B216-026FT0005 → B216-036FT0005 → B216-036ET0015 → END
B2-SWG-69603 | -P20 | 21 |  | PE-L1-4C95/50-25 | PE-L1-4C95/50-25 | ACC-B2-023 |  |  | 1 | 428 | B2-SWG-69603-P2021 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-25 | 160 | 400 | N | 240 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16145 | ACC STREET 4 FAN 5 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006CT0013 → B269-006CT0034 → B269-006CT0027 → B269-006CT0051 → D0107-L24 → M0108 → D0109-L14 → M0110 → B216-916FT0005 → B216-016FT0005 → B216-926FT0005 → B216-026FT0005 → B216-036FT0005 → B216-036ET0015 → END
B2-SWG-69603 | -P20 | 22 |  | PE-L1-4C95/50-25 | PE-L1-4C95/50-25 |  |  |  | 1 | 429 | B2-SWG-69603-P2022 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-25 | 160 | 400 | N | 240 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16145 | ACC STREET 4 FAN 5 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006CT0013 → B269-006CT0034 → B269-006CT0027 → B269-006CT0051 → D0107-L24 → M0108 → D0109-L14 → M0110 → B216-916FT0005 → B216-016FT0005 → B216-926FT0005 → B216-026FT0005 → B216-036FT0005 → B216-036ET0015 → END
B2-SWG-69603 | -P20 | 23 |  | PE-L1-4C95/50-24 | PE-L1-4C95/50-24 | ACC-B2-024 |  |  | 1 | 430 | B2-SWG-69603-P2023 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-24 | 160 | 400 | N | 250 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16146 | ACC STREET 4 FAN 6 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006CT0013 → B269-006CT0034 → B269-006CT0027 → B269-006CT0051 → D0107-L25 → M0108 → D0109-L15 → M0110 → B216-916FT0005 → B216-016FT0005 → B216-926FT0005 → B216-026FT0005 → B216-036FT0005 → B216-036ET0015 → B216-036ET0016 → END
B2-SWG-69603 | -P20 | 24 |  | PE-L1-4C95/50-25 | PE-L1-4C95/50-25 |  |  |  | 1 | 431 | B2-SWG-69603-P2024 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-25 | 160 | 400 | N | 250 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-C(M)-16146 | ACC STREET 4 FAN 6 MOTOR | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006CT0013 → B269-006CT0034 → B269-006CT0027 → B269-006CT0051 → D0107-L25 → M0108 → D0109-L15 → M0110 → B216-916FT0005 → B216-016FT0005 → B216-926FT0005 → B216-026FT0005 → B216-036FT0005 → B216-036ET0015 → B216-036ET0016 → END
B2-SWG-69601 | -P20 | 25 |  | PE-L1-3C4-24 | PE-L1-3C4-24 | ACC-B2-025 |  |  | 1 | 432 | B2-SWG-69601-P2025 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-24 | 0.2 | 230 | N | 180 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(MH)-16111 | ACC STREET 1 FAN 1 MOTOR SPACE HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006BT0025 → B269-006BT0048 → D0106-L23 → M0107 → D0108-L13 → M0109 → B216-916DT0004 → B216-016DT0004 → B216-926DT0004 → B216-026DT0004 → B216-036DT0004 → B216-036CT0012 → B216-036CT0014 → END
B2-SWG-69601 | -P20 | 26 |  | PE-L1-3C4-24 | PE-L1-3C4-24 | ACC-B2-026 |  |  | 1 | 433 | B2-SWG-69601-P2026 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-24 | 0.2 | 230 | N | 160 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(MH)-16112 | ACC STREET 1 FAN 2 MOTOR SPACE HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006BT0025 → B269-006BT0048 → D0106-L23 → M0107 → D0108-L13 → M0109 → B216-916DT0004 → B216-016DT0004 → B216-926DT0004 → B216-026DT0004 → B216-036DT0004 → B216-036CT0012 → END
B2-SWG-69601 | -P20 | 27 |  | PE-L1-3C4-24 | PE-L1-3C4-24 | ACC-B2-027 |  |  | 1 | 434 | B2-SWG-69601-P2027 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-24 | 0.2 | 230 | N | 160 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(MH)-16113 | ACC STREET 1 FAN 3 MOTOR SPACE HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006BT0025 → B269-006BT0048 → D0106-L24 → M0107 → D0108-L14 → M0109 → B216-916DT0004 → B216-016DT0004 → B216-926DT0004 → B216-026DT0004 → B216-036DT0004 → B216-036CT0012 → END
B2-SWG-69601 | -P20 | 28 |  | PE-L1-3C4-25 | PE-L1-3C4-25 | ACC-B2-028 |  |  | 1 | 435 | B2-SWG-69601-P2028 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-25 | 0.2 | 230 | N | 160 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(MH)-16114 | ACC STREET 1 FAN 4 MOTOR SPACE HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006BT0025 → B269-006BT0048 → D0106-L24 → M0107 → D0108-L14 → M0109 → B216-916CT0003 → B216-016CT0003 → B216-926CT0003 → B216-026CT0003 → B216-036CT0003 → B216-036CT0012 → END
B2-SWG-69601 | -P20 | 29 |  | PE-L1-3C4-25 | PE-L1-3C4-25 | ACC-B2-029 |  |  | 1 | 436 | B2-SWG-69601-P2029 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-25 | 0.2 | 230 | N | 170 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(MH)-16115 | ACC STREET 1 FAN 5 MOTOR SPACE HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006BT0026 → B269-006BT0027 → B269-006BT0051 → D0107-L42 → M0108 → D0109-L22 → M0110 → B216-916CT0003 → B216-016CT0003 → B216-926CT0003 → B216-026CT0003 → B216-036CT0003 → B216-036CT0012 → END
B2-SWG-69601 | -P20 | 30 |  | PE-L1-3C4-25 | PE-L1-3C4-25 | ACC-B2-030 |  |  | 1 | 437 | B2-SWG-69601-P2030 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-25 | 0.2 | 230 | N | 180 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(MH)-16116 | ACC STREET 1 FAN 6 MOTOR SPACE HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006BT0026 → B269-006BT0027 → B269-006BT0051 → D0107-L42 → M0108 → D0109-L22 → M0110 → B216-916CT0003 → B216-016CT0003 → B216-926CT0003 → B216-026CT0003 → B216-036CT0003 → B216-036CT0012 → B216-036CT0013 → END
B2-SWG-69601 | -P20 | 31 |  | PE-L1-3C4-14 | PE-L1-3C4-14 | ACC-B2-031 |  |  | 1 | 438 | B2-SWG-69601-P2031 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-14 | 0.2 | 230 | N | 220 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(MH)-16121 | ACC STREET 2 FAN 1 MOTOR SPACE HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006BT0026 → B269-006BT0027 → B269-006BT0051 → D0107-L43 → M0108 → D0105-L23 → M0107 → D0108-L13 → M0109 → B216-916AT0002 → B216-016AT0002 → B216-926AT0002 → B216-026AT0002 → B216-036AT0002 → B216-036AT0009 → B216-036AT0011 → END
B2-SWG-69601 | -P20 | 32 |  | PE-L1-3C4-29 | PE-L1-3C4-29 | ACC-B2-032 |  |  | 1 | 439 | B2-SWG-69601-P2032 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-29 | 0.2 | 230 | N | 200 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(MH)-16122 | ACC STREET 2 FAN 2 MOTOR SPACE HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006BT0026 → B269-006BT0027 → B269-006BT0051 → D0107-L43 → M0108 → D0105-L23 → M0107 → D0108-L13 → M0109 → B216-916AT0002 → B216-016AT0002 → B216-926AT0002 → B216-026AT0002 → B216-036AT0002 → B216-036AT0009 → END
B2-SWG-69601 | -P20 | 33 |  | PE-L1-3C4-25 | PE-L1-3C4-25 | ACC-B2-033 |  |  | 1 | 440 | B2-SWG-69601-P2033 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-25 | 0.2 | 230 | N | 190 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(MH)-16123 | ACC STREET 2 FAN 3 MOTOR SPACE HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006BT0026 → B269-006BT0027 → B269-006BT0051 → D0107-L43 → M0108 → D0105-L23 → M0107 → D0108-L13 → M0109 → B216-916AT0002 → B216-016AT0002 → B216-926AT0002 → B216-026AT0002 → B216-036AT0002 → B216-036AT0009 → END
B2-SWG-69601 | -P20 | 34 |  | PE-L1-3C4-19 | PE-L1-3C4-19 | ACC-B2-034 |  |  | 1 | 441 | B2-SWG-69601-P2034 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-19 | 0.2 | 230 | N | 150 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(MH)-16124 | ACC STREET 2 FAN 4 MOTOR SPACE HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006CT0027 → B269-006CT0051 → D0107-L43 → M0108 → D0109-L23 → M0110 → B216-916BT0001 → B216-016BT0001 → B216-926BT0001 → B216-026BT0001 → B216-036BT0001 → B216-036AT0009 → END
B2-SWG-69601 | -P20 | 35 |  | PE-L1-3C4-06 | PE-L1-3C4-06 | ACC-B2-035 |  |  | 1 | 442 | B2-SWG-69601-P2035 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-06 | 0.2 | 230 | N | 170 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(MH)-16125 | ACC STREET 2 FAN 5 MOTOR SPACE HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006CT0027 → B269-006CT0051 → D0107-L43 → M0108 → D0109-L23 → M0110 → B216-916BT0001 → B216-016BT0001 → B216-926BT0001 → B216-026BT0001 → B216-036BT0001 → B216-036AT0009 → END
B2-SWG-69601 | -P20 | 36 |  | PE-L1-3C4-19 | PE-L1-3C4-19 | ACC-B2-036 |  |  | 1 | 443 | B2-SWG-69601-P2036 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-19 | 0.2 | 230 | N | 180 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(MH)-16126 | ACC STREET 2 FAN 6 MOTOR SPACE HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006CT0027 → B269-006CT0051 → D0107-L43 → M0108 → D0109-L23 → M0110 → B216-916BT0001 → B216-016BT0001 → B216-926BT0001 → B216-026BT0001 → B216-036BT0001 → B216-036AT0009 → B216-036AT0010 → END
B2-SWG-69603 | -P20 | 25 |  | PE-L1-3C4-07 | PE-L1-3C4-07 | ACC-B2-037 |  |  | 1 | 444 | B2-SWG-69603-P2025 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-07 | 0.2 | 230 | N | 250 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(MH)-16131 | ACC STREET 3 FAN 1 MOTOR SPACE HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006DT0036 → B269-006DT0050 → D0107-L31 → M0108 → D0105-L15 → M0107 → D0108-L11 → M0109 → B216-916GT0008 → B216-016GT0008 → B216-926GT0008 → B216-026GT0008 → B216-036GT0008 → B216-036GT0018 → B216-036GT0020 → END
B2-SWG-69603 | -P20 | 26 |  | PE-L1-3C4-19 | PE-L1-3C4-19 | ACC-B2-038 |  |  | 1 | 445 | B2-SWG-69603-P2026 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-19 | 0.2 | 230 | N | 240 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(MH)-16132 | ACC STREET 3 FAN 2 MOTOR SPACE HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006DT0036 → B269-006DT0050 → D0107-L31 → M0108 → D0105-L15 → M0107 → D0108-L11 → M0109 → B216-916GT0008 → B216-016GT0008 → B216-926GT0008 → B216-026GT0008 → B216-036GT0008 → B216-036GT0018 → END
B2-SWG-69603 | -P20 | 27 |  | PE-L1-3C4-19 | PE-L1-3C4-19 | ACC-B2-039 |  |  | 1 | 446 | B2-SWG-69603-P2027 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-19 | 0.2 | 230 | N | 230 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(MH)-16133 | ACC STREET 3 FAN 3 MOTOR SPACE HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006DT0036 → B269-006DT0050 → D0107-L31 → M0108 → D0105-L15 → M0107 → D0108-L11 → M0109 → B216-916GT0008 → B216-016GT0008 → B216-926GT0008 → B216-026GT0008 → B216-036GT0008 → B216-036GT0018 → END
B2-SWG-69603 | -P20 | 28 |  | PE-L1-3C4-07 | PE-L1-3C4-07 | ACC-B2-040 |  |  | 1 | 447 | B2-SWG-69603-P2028 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-07 | 0.2 | 230 | N | 210 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(MH)-16134 | ACC STREET 3 FAN 4 MOTOR SPACE HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006DT0036 → B269-006DT0050 → D0107-L31 → M0108 → D0109-L21 → M0110 → B216-916HT0007 → B216-016HT0007 → B216-926HT0007 → B216-026HT0007 → B216-036HT0007 → B216-036GT0018 → END
B2-SWG-69603 | -P20 | 29 |  | PE-L1-3C4-14 | PE-L1-3C4-14 | ACC-B2-041 |  |  | 1 | 448 | B2-SWG-69603-P2029 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-14 | 0.2 | 230 | N | 220 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(MH)-16135 | ACC STREET 3 FAN 5 MOTOR SPACE HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006DT0036 → B269-006DT0050 → D0107-L31 → M0108 → D0109-L21 → M0110 → B216-916HT0007 → B216-016HT0007 → B216-926HT0007 → B216-026HT0007 → B216-036HT0007 → B216-036GT0018 → END
B2-SWG-69603 | -P20 | 30 |  | PE-L1-3C4-19 | PE-L1-3C4-19 | ACC-B2-042 |  |  | 1 | 449 | B2-SWG-69603-P2030 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-19 | 0.2 | 230 | N | 220 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(MH)-16136 | ACC STREET 3 FAN 6 MOTOR SPACE HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006ET0035 → B269-006ET0051 → D0107-L31 → M0108 → D0109-L11 → M0110 → B216-916HT0007 → B216-016HT0007 → B216-926HT0007 → B216-026HT0007 → B216-036HT0007 → B216-036GT0018 → B216-036GT0019 → END
B2-SWG-69603 | -P20 | 31 |  | PE-L1-3C4-07 | PE-L1-3C4-07 | ACC-B2-043 |  |  | 1 | 450 | B2-SWG-69603-P2031 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-07 | 0.2 | 230 | N | 260 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(MH)-16141 | ACC STREET 4 FAN 1 MOTOR SPACE HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006ET0035 → B269-006ET0051 → D0107-L32 → M0108 → D0105-L24 → M0107 → D0108-L22 → M0109 → B216-916ET0006 → B216-016ET0006 → B216-926ET0006 → B216-026ET0006 → B216-036ET0006 → B216-036ET0015 → B216-036ET0017 → END
B2-SWG-69603 | -P20 | 32 |  | PE-L1-3C4-20 | PE-L1-3C4-20 | ACC-B2-044 |  |  | 1 | 451 | B2-SWG-69603-P2032 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-20 | 0.2 | 230 | N | 250 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(MH)-16142 | ACC STREET 4 FAN 2 MOTOR SPACE HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006ET0035 → B269-006ET0051 → D0107-L32 → M0108 → D0105-L24 → M0107 → D0108-L22 → M0109 → B216-916ET0006 → B216-016ET0006 → B216-926ET0006 → B216-026ET0006 → B216-036ET0006 → B216-036ET0015 → END
B2-SWG-69603 | -P20 | 33 |  | PE-L1-3C4-20 | PE-L1-3C4-20 | ACC-B2-045 |  |  | 1 | 452 | B2-SWG-69603-P2033 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-20 | 0.2 | 230 | N | 210 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(MH)-16143 | ACC STREET 4 FAN 3 MOTOR SPACE HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006ET0035 → B269-006ET0051 → D0107-L32 → M0108 → D0109-L22 → M0110 → B216-916ET0006 → B216-016ET0006 → B216-926ET0006 → B216-026ET0006 → B216-036ET0006 → B216-036ET0015 → END
B2-SWG-69603 | -P20 | 34 |  | PE-L1-3C4-20 | PE-L1-3C4-20 | ACC-B2-046 |  |  | 1 | 453 | B2-SWG-69603-P2034 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-20 | 0.2 | 230 | N | 210 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(MH)-16144 | ACC STREET 4 FAN 4 MOTOR SPACE HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006ET0035 → B269-006ET0051 → D0107-L32 → M0108 → D0109-L22 → M0110 → B216-916FT0005 → B216-016FT0005 → B216-926FT0005 → B216-026FT0005 → B216-036FT0005 → B216-036ET0015 → END
B2-SWG-69603 | -P20 | 35 |  | PE-L1-3C4-20 | PE-L1-3C4-20 | ACC-B2-047 |  |  | 1 | 454 | B2-SWG-69603-P2035 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-20 | 0.2 | 230 | N | 240 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(MH)-16145 | ACC STREET 4 FAN 5 MOTOR SPACE HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006CT0013 → B269-006CT0034 → B269-006CT0027 → B269-006CT0051 → D0107-L32 → M0108 → D0109-L22 → M0110 → B216-916FT0005 → B216-016FT0005 → B216-926FT0005 → B216-026FT0005 → B216-036FT0005 → B216-036ET0015 → END
B2-SWG-69603 | -P20 | 36 |  | PE-L1-3C4-20 | PE-L1-3C4-20 | ACC-B2-048 |  |  | 1 | 455 | B2-SWG-69603-P2036 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-20 | 0.2 | 230 | N | 250 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(MH)-16146 | ACC STREET 4 FAN 6 MOTOR SPACE HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006CT0013 → B269-006CT0034 → B269-006CT0027 → B269-006CT0051 → D0107-L32 → M0108 → D0109-L22 → M0110 → B216-916FT0005 → B216-016FT0005 → B216-926FT0005 → B216-026FT0005 → B216-036FT0005 → B216-036ET0015 → B216-036ET0016 → END
B2-DB-69601 | -P20 | 01 |  | PE-L1-3C6-03 | PE-L1-3C6-03 | ACC-B2-052-019 |  |  | 1 | 456 | B2-DB-69601-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-03 | 1 | 230 | N | 160 | AIR COOLED CONDENSER | B2-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(GH)-16111 | ACC STREET 1 FAN 1 GEARBOX OIL HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006BT0025 → B269-006BT0048 → D0106-L23 → M0107 → D0108-L13 → M0109 → B216-916DT0004 → B216-016DT0004 → B216-926DT0004 → B216-026DT0004 → B216-036DT0004 → B216-036CT0012 → B216-036CT0014 → END
B2-DB-69601 | -P20 | 02 |  | PE-L1-3C6-03 | PE-L1-3C6-03 | ACC-B2-052-020 |  |  | 1 | 457 | B2-DB-69601-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-03 | 1 | 230 | N | 150 | AIR COOLED CONDENSER | B2-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(GH)-16112 | ACC STREET 1 FAN 2 GEARBOX OIL HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006BT0025 → B269-006BT0048 → D0106-L23 → M0107 → D0108-L13 → M0109 → B216-916DT0004 → B216-016DT0004 → B216-926DT0004 → B216-026DT0004 → B216-036DT0004 → B216-036CT0012 → END
B2-DB-69601 | -P20 | 03 |  | PE-L1-3C6-06 | PE-L1-3C6-06 | ACC-B2-052-021 |  |  | 1 | 458 | B2-DB-69601-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-06 | 1 | 230 | N | 130 | AIR COOLED CONDENSER | B2-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(GH)-16113 | ACC STREET 1 FAN 3 GEARBOX OIL HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006BT0025 → B269-006BT0048 → D0106-L24 → M0107 → D0108-L14 → M0109 → B216-916DT0004 → B216-016DT0004 → B216-926DT0004 → B216-026DT0004 → B216-036DT0004 → B216-036CT0012 → END
B2-DB-69601 | -P20 | 04 |  | PE-L1-3C6-06 | PE-L1-3C6-06 | ACC-B2-052-022 |  |  | 1 | 459 | B2-DB-69601-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-06 | 1 | 230 | N | 130 | AIR COOLED CONDENSER | B2-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(GH)-16114 | ACC STREET 1 FAN 4 GEARBOX OIL HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006BT0025 → B269-006BT0048 → D0106-L24 → M0107 → D0108-L14 → M0109 → B216-916CT0003 → B216-016CT0003 → B216-926CT0003 → B216-026CT0003 → B216-036CT0003 → B216-036CT0012 → END
B2-DB-69601 | -P20 | 05 |  | PE-L1-3C6-03 | PE-L1-3C6-03 | ACC-B2-052-023 |  |  | 1 | 460 | B2-DB-69601-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-03 | 1 | 230 | N | 160 | AIR COOLED CONDENSER | B2-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(GH)-16115 | ACC STREET 1 FAN 5 GEARBOX OIL HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006BT0026 → B269-006BT0027 → B269-006BT0051 → D0107-L42 → M0108 → D0109-L22 → M0110 → B216-916CT0003 → B216-016CT0003 → B216-926CT0003 → B216-026CT0003 → B216-036CT0003 → B216-036CT0012 → END
B2-DB-69601 | -P20 | 06 |  | PE-L1-3C6-06 | PE-L1-3C6-06 | ACC-B2-052-024 |  |  | 1 | 461 | B2-DB-69601-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-06 | 1 | 230 | N | 170 | AIR COOLED CONDENSER | B2-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(GH)-16116 | ACC STREET 1 FAN 6 GEARBOX OIL HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006BT0026 → B269-006BT0027 → B269-006BT0051 → D0107-L42 → M0108 → D0109-L22 → M0110 → B216-916CT0003 → B216-016CT0003 → B216-926CT0003 → B216-026CT0003 → B216-036CT0003 → B216-036CT0012 → B216-036CT0013 → END
B2-DB-69601 | -P20 | 07 |  | PE-L1-3C6-06 | PE-L1-3C6-06 | ACC-B2-052-001 |  |  | 1 | 462 | B2-DB-69601-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-06 | 1 | 230 | N | 210 | AIR COOLED CONDENSER | B2-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(GH)-16121 | ACC STREET 2 FAN 1 GEARBOX OIL HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006BT0026 → B269-006BT0027 → B269-006BT0051 → D0107-L43 → M0108 → D0105-L23 → M0107 → D0108-L13 → M0109 → B216-916AT0002 → B216-016AT0002 → B216-926AT0002 → B216-026AT0002 → B216-036AT0002 → B216-036AT0009 → B216-036AT0011 → END
B2-DB-69601 | -P20 | 08 |  | PE-L1-3C6-06 | PE-L1-3C6-06 | ACC-B2-052-002 |  |  | 1 | 463 | B2-DB-69601-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-06 | 1 | 230 | N | 200 | AIR COOLED CONDENSER | B2-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(GH)-16122 | ACC STREET 2 FAN 2 GEARBOX OIL HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006BT0026 → B269-006BT0027 → B269-006BT0051 → D0107-L43 → M0108 → D0105-L23 → M0107 → D0108-L13 → M0109 → B216-916AT0002 → B216-016AT0002 → B216-926AT0002 → B216-026AT0002 → B216-036AT0002 → B216-036AT0009 → END
B2-DB-69601 | -P20 | 09 |  | PE-L1-3C6-06 | PE-L1-3C6-06 | ACC-B2-052-003 |  |  | 1 | 464 | B2-DB-69601-P2009 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-06 | 1 | 230 | N | 180 | AIR COOLED CONDENSER | B2-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(GH)-16123 | ACC STREET 2 FAN 3 GEARBOX OIL HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006BT0026 → B269-006BT0027 → B269-006BT0051 → D0107-L43 → M0108 → D0105-L23 → M0107 → D0108-L13 → M0109 → B216-916AT0002 → B216-016AT0002 → B216-926AT0002 → B216-026AT0002 → B216-036AT0002 → B216-036AT0009 → END
B2-DB-69601 | -P20 | 10 |  | PE-L1-3C6-06 | PE-L1-3C6-06 | ACC-B2-052-004 |  |  | 1 | 465 | B2-DB-69601-P2010 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-06 | 1 | 230 | N | 150 | AIR COOLED CONDENSER | B2-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(GH)-16124 | ACC STREET 2 FAN 4 GEARBOX OIL HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006CT0027 → B269-006CT0051 → D0107-L43 → M0108 → D0109-L23 → M0110 → B216-916BT0001 → B216-016BT0001 → B216-926BT0001 → B216-026BT0001 → B216-036BT0001 → B216-036AT0009 → END
B2-DB-69601 | -P20 | 11 |  | PE-L1-3C6-06 | PE-L1-3C6-06 | ACC-B2-052-005 |  |  | 1 | 466 | B2-DB-69601-P2011 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-06 | 1 | 230 | N | 160 | AIR COOLED CONDENSER | B2-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(GH)-16125 | ACC STREET 2 FAN 5 GEARBOX OIL HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006CT0027 → B269-006CT0051 → D0107-L43 → M0108 → D0109-L23 → M0110 → B216-916BT0001 → B216-016BT0001 → B216-926BT0001 → B216-026BT0001 → B216-036BT0001 → B216-036AT0009 → END
B2-DB-69601 | -P20 | 12 |  | PE-L1-3C6-06 | PE-L1-3C6-06 | ACC-B2-052-006 |  |  | 1 | 467 | B2-DB-69601-P2012 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-06 | 1 | 230 | N | 170 | AIR COOLED CONDENSER | B2-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(GH)-16126 | ACC STREET 2 FAN 6 GEARBOX OIL HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006CT0027 → B269-006CT0051 → D0107-L43 → M0108 → D0109-L23 → M0110 → B216-916BT0001 → B216-016BT0001 → B216-926BT0001 → B216-026BT0001 → B216-036BT0001 → B216-036AT0009 → B216-036AT0010 → END
B2-DB-69603 | -P20 | 01 |  | PE-L1-3C6-06 | PE-L1-3C6-06 | ACC-B2-052-007 |  |  | 1 | 468 | B2-DB-69603-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-06 | 1 | 230 | N | 220 | AIR COOLED CONDENSER | B2-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(GH)-16131 | ACC STREET 3 FAN 1 GEARBOX OIL HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006DT0036 → B269-006DT0050 → D0107-L31 → M0108 → D0105-L15 → M0107 → D0108-L21 → M0109 → B216-916GT0008 → B216-016GT0008 → B216-926GT0008 → B216-026GT0008 → B216-036GT0008 → B216-036GT0018 → B216-036GT0020 → END
B2-DB-69603 | -P20 | 02 |  | PE-L1-3C6-06 | PE-L1-3C6-06 | ACC-B2-052-008 |  |  | 1 | 469 | B2-DB-69603-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-06 | 1 | 230 | N | 210 | AIR COOLED CONDENSER | B2-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(GH)-16132 | ACC STREET 3 FAN 2 GEARBOX OIL HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006DT0036 → B269-006DT0050 → D0107-L31 → M0108 → D0105-L15 → M0107 → D0108-L21 → M0109 → B216-916GT0008 → B216-016GT0008 → B216-926GT0008 → B216-026GT0008 → B216-036GT0008 → B216-036GT0018 → END
B2-DB-69603 | -P20 | 03 |  | PE-L1-3C6-07 | PE-L1-3C6-07 | ACC-B2-052-009 |  |  | 1 | 470 | B2-DB-69603-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-07 | 1 | 230 | N | 190 | AIR COOLED CONDENSER | B2-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(GH)-16133 | ACC STREET 3 FAN 3 GEARBOX OIL HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006DT0036 → B269-006DT0050 → D0107-L31 → M0108 → D0105-L15 → M0107 → D0108-L21 → M0109 → B216-916GT0008 → B216-016GT0008 → B216-926GT0008 → B216-026GT0008 → B216-036GT0008 → B216-036GT0018 → END
B2-DB-69603 | -P20 | 04 |  | PE-L1-3C6-07 | PE-L1-3C6-07 | ACC-B2-052-010 |  |  | 1 | 471 | B2-DB-69603-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-07 | 1 | 230 | N | 160 | AIR COOLED CONDENSER | B2-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(GH)-16134 | ACC STREET 3 FAN 4 GEARBOX OIL HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006DT0036 → B269-006DT0050 → D0107-L31 → M0108 → D0109-L21 → M0110 → B216-916HT0007 → B216-016HT0007 → B216-926HT0007 → B216-026HT0007 → B216-036HT0007 → B216-036GT0018 → END
B2-DB-69603 | -P20 | 05 |  | PE-L1-3C6-07 | PE-L1-3C6-07 | ACC-B2-052-011 |  |  | 1 | 472 | B2-DB-69603-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-07 | 1 | 230 | N | 180 | AIR COOLED CONDENSER | B2-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(GH)-16135 | ACC STREET 3 FAN 5 GEARBOX OIL HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006DT0036 → B269-006DT0050 → D0107-L31 → M0108 → D0109-L21 → M0110 → B216-916HT0007 → B216-016HT0007 → B216-926HT0007 → B216-026HT0007 → B216-036HT0007 → B216-036GT0018 → END
B2-DB-69603 | -P20 | 06 |  | PE-L1-3C6-07 | PE-L1-3C6-07 | ACC-B2-052-012 |  |  | 1 | 473 | B2-DB-69603-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-07 | 1 | 230 | N | 190 | AIR COOLED CONDENSER | B2-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(GH)-16136 | ACC STREET 3 FAN 6 GEARBOX OIL HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006ET0035 → B269-006ET0051 → D0107-L31 → M0108 → D0109-L21 → M0110 → B216-916HT0007 → B216-016HT0007 → B216-926HT0007 → B216-026HT0007 → B216-036HT0007 → B216-036GT0018 → B216-036GT0019 → END
B2-DB-69603 | -P20 | 07 |  | PE-L1-3C6-07 | PE-L1-3C6-07 | ACC-B2-052-013 |  |  | 1 | 474 | B2-DB-69603-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-07 | 1 | 230 | N | 230 | AIR COOLED CONDENSER | B2-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(GH)-16141 | ACC STREET 4 FAN 1 GEARBOX OIL HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006ET0035 → B269-006ET0051 → D0107-L32 → M0108 → D0105-L24 → M0107 → D0108-L22 → M0109 → B216-916ET0006 → B216-016ET0006 → B216-926ET0006 → B216-026ET0006 → B216-036ET0006 → B216-036ET0015 → B216-036ET0017 → END
B2-DB-69603 | -P20 | 08 |  | PE-L1-3C6-07 | PE-L1-3C6-07 | ACC-B2-052-014 |  |  | 1 | 475 | B2-DB-69603-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-07 | 1 | 230 | N | 210 | AIR COOLED CONDENSER | B2-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(GH)-16142 | ACC STREET 4 FAN 2 GEARBOX OIL HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006ET0035 → B269-006ET0051 → D0107-L32 → M0108 → D0105-L24 → M0107 → D0108-L22 → M0109 → B216-916ET0006 → B216-016ET0006 → B216-926ET0006 → B216-026ET0006 → B216-036ET0006 → B216-036ET0015 → END
B2-DB-69603 | -P20 | 09 |  | PE-L1-3C6-07 | PE-L1-3C6-07 | ACC-B2-052-015 |  |  | 1 | 476 | B2-DB-69603-P2009 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-07 | 1 | 230 | N | 180 | AIR COOLED CONDENSER | B2-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(GH)-16143 | ACC STREET 4 FAN 3 GEARBOX OIL HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006ET0035 → B269-006ET0051 → D0107-L32 → M0108 → D0109-L12 → M0110 → B216-916ET0006 → B216-016ET0006 → B216-926ET0006 → B216-026ET0006 → B216-036ET0006 → B216-036ET0015 → END
B2-DB-69603 | -P20 | 10 |  | PE-L1-3C6-07 | PE-L1-3C6-07 | ACC-B2-052-016 |  |  | 1 | 477 | B2-DB-69603-P2010 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-07 | 1 | 230 | N | 180 | AIR COOLED CONDENSER | B2-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(GH)-16144 | ACC STREET 4 FAN 4 GEARBOX OIL HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006ET0035 → B269-006ET0051 → D0107-L32 → M0108 → D0109-L12 → M0110 → B216-916FT0005 → B216-016FT0005 → B216-926FT0005 → B216-026FT0005 → B216-036FT0005 → B216-036ET0015 → END
B2-DB-69603 | -P20 | 11 |  | PE-L1-3C6-07 | PE-L1-3C6-07 | ACC-B2-052-017 |  |  | 1 | 478 | B2-DB-69603-P2011 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-07 | 1 | 230 | N | 210 | AIR COOLED CONDENSER | B2-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(GH)-16145 | ACC STREET 4 FAN 5 GEARBOX OIL HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006CT0013 → B269-006CT0034 → B269-006CT0027 → B269-006CT0051 → D0107-L32 → M0108 → D0109-L15 → M0110 → B216-916FT0005 → B216-016FT0005 → B216-926FT0005 → B216-026FT0005 → B216-036FT0005 → B216-036ET0015 → END
B2-DB-69603 | -P20 | 12 |  | PE-L1-3C6-07 | PE-L1-3C6-07 | ACC-B2-052-018 |  |  | 1 | 479 | B2-DB-69603-P2012 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-07 | 1 | 230 | N | 220 | AIR COOLED CONDENSER | B2-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-C(GH)-16146 | ACC STREET 4 FAN 6 GEARBOX OIL HEATER | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, N, PE | B269-006CT0013 → B269-006CT0034 → B269-006CT0027 → B269-006CT0051 → D0107-L32 → M0108 → D0109-L15 → M0110 → B216-916FT0005 → B216-016FT0005 → B216-926FT0005 → B216-026FT0005 → B216-036FT0005 → B216-036ET0015 → B216-036ET0016 → END
B2-SWG-69603 | -P20 | 37 |  | PE-L1-4C95/50-19 | PE-L1-4C95/50-19 | ACC-B2-048-001 |  |  | 1 | 480 | B2-SWG-69603-P2037 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-19 | 185 | 400 | N | 40 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-P(M)-16070 | ACC LRVP A MOTOR | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-006AT0013 → B169-006AT0033 → B169-006AT0019 → B016-006BC0005 → END
B2-SWG-69603 | -P20 | 38 |  | PE-L1-4C95/50-19 | PE-L1-4C95/50-19 |  |  |  | 1 | 481 | B2-SWG-69603-P2038 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-19 | 185 | 400 | N | 40 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-P(M)-16070 | ACC LRVP A MOTOR | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-006AT0013 → B169-006AT0033 → B169-006AT0019 → B016-006BC0006 → END
B2-SWG-69603 | -P20 | 39 | 재배정 | PE-L1-3C4-15 | PE-L1-3C4-28 | ACC-B2-048-002 |  |  | 1 | 482 | B2-SWG-69603-P2039 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-28 | 0.16 | 230 | N | 40 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-P(MH)-16070 | ACC LRVP A MOTOR SPACE HEATER | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0013 → B169-006AT0033 → B169-006AT0019 → B016-007BC0003 → END
B2-SWG-69603 | -P20 | 40 |  | PE-L1-4C95/50-19 | PE-L1-4C95/50-19 | ACC-B2-049 |  |  | 1 | 483 | B2-SWG-69603-P2040 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-19 | 185 | 400 | N | 30 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-P(M)-16080 | ACC LRVP B MOTOR | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B269-006CT0013 → B269-006CT0034 → B016-006BC0003 → END
B2-SWG-69603 | -P20 | 41 |  | PE-L1-4C95/50-19 | PE-L1-4C95/50-19 |  |  |  | 1 | 484 | B2-SWG-69603-P2041 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-19 | 185 | 400 | N | 30 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-P(M)-16080 | ACC LRVP B MOTOR | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B269-006CT0013 → B269-006CT0034 → B016-006BC0004 → END
B2-SWG-69603 | -P20 | 42 |  | PE-L1-3C4-15 | PE-L1-3C4-15 | ACC-B2-050 |  |  | 1 | 485 | B2-SWG-69603-P2042 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 0.16 | 230 | N | 40 | AIR COOLED CONDENSER | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-P(MH)-16080 | ACC LRVP B MOTOR SPACE HEATER | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0013 → B169-006AT0033 → B169-006AT0020 → B016-007BC0002 → END
B2-SWG-69601 | -P20 | 37 |  | PE-L1-4C95/50-19 | PE-L1-4C95/50-19 | ACC-B2-051 |  |  | 1 | 486 | B2-SWG-69601-P2037 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-19 | 185 | 400 | N | 40 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-P(M)-16090 | ACC LRVP C MOTOR | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-006AT0020 → B169-006AT0021 → B016-006BC0001 → END
B2-SWG-69601 | -P20 | 38 |  | PE-L1-4C95/50-19 | PE-L1-4C95/50-19 |  |  |  | 1 | 487 | B2-SWG-69601-P2038 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-19 | 185 | 400 | N | 40 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-P(M)-16090 | ACC LRVP C MOTOR | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-006AT0020 → B169-006AT0021 → B016-006BC0002 → END
B2-SWG-69601 | -P20 | 39 |  | PE-L1-3C4-15 | PE-L1-3C4-15 | ACC-B2-052 |  |  | 1 | 488 | B2-SWG-69601-P2039 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 0.16 | 230 | N | 40 | AIR COOLED CONDENSER | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-P(MH)-16090 | ACC LRVP C MOTOR SPACE HEATER | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0020 → B169-006AT0021 → B016-007BC0001 → END
B2-MCC-64602 | -P20 | 06 |  | PE-L1-4C35/25-02 | PE-L1-4C35/25-02 | ACC-B2-053 |  |  | 1 | 489 | B2-MCC-64602-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 35sqmm + 1C X 25sqmm | PE-L1-4C35/25-02 | 18.5 | 400 | N | 420 | AIR COOLED CONDENSER | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-P(M)-16021 | STEAM TURBINE EXHAUST DUCT DRAIN PUMP A | 1.1_MAIN BUILDING COMPLEX (BELOW ACCDUCT NEARYBY ST) | L1, L2, L3, PE | B264-016AT0045 → B264-016AT0046 → B264-016AT0209 → B264-016AT0026 → B264-016AT0027 → B264-016AT0225 → B264-996AT0011 → M0405 → D0421-L31 → M0406 → D0301-L37 → M0301 → B215-997AT0026 → B215-017AT0027 → B215-017AT0028 → B215-017AT0029 → B215-017AT0030 → B215-017AT0006 → B215-017AT0007 → B215-017AT0008 → B215-017AT0009 → B215-017AT0010 → B215-017AT0011 → B213-016BC0032 → B213-006AC0002 → B213-016AC0001 → B213-016AC0003 → END
B2-MCC-64601 | -P20 | 05 |  | PE-L1-4C35/25-02 | PE-L1-4C35/25-02 | ACC-B2-054 |  |  | 1 | 490 | B2-MCC-64601-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 35sqmm + 1C X 25sqmm | PE-L1-4C35/25-02 | 18.5 | 400 | N | 440 | AIR COOLED CONDENSER | B2-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-P(M)-16022 | STEAM TURBINE EXHAUST DUCT DRAIN PUMP B | 1.1_MAIN BUILDING COMPLEX (BELOW ACCDUCT NEARYBY ST) | L1, L2, L3, PE | B264-016CT0024 → B264-016CT0025 → B264-016CT0026 → B264-016CT0027 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L32 → M0406 → D0301-L36 → M0301 → B215-996BT0001 → B215-016BT0002 → B215-016BT0003 → B215-016BT0004 → B215-016BT0005 → B215-016BT0031 → B215-016BT0032 → B215-016BT0033 → B215-016BT0034 → B215-016BT0035 → B215-016BT0036 → B215-016BT0103 → B215-016BT0104 → B213-016BC0033 → B213-006AC0003 → B213-016AC0002 → B213-016AC0004 → END
B2-MCC-69603 | -P20 | 01 |  | PE-L1-4C6-02 | PE-L1-4C6-02 | ACC-B2-058 |  |  | 1 | 491 | B2-MCC-69603-P2001 | 0.6/1kV CU/XLPE/LSZH | 4C x 6sqmm | PE-L1-4C6-02 | 5 | 400 | N | 240 | AIR COOLED CONDENSER | B2-MCC-69603 | 400V MCC FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-HO(M)-16001 | ACC ELECTRICAL HOIST FOR MAINTENANCE | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006CT0034 → B269-006CT0027 → B269-006CT0051 → D0107-L42 → M0108 → D0105-L22 → M0107 → D0108-L13 → M0109 → B216-916CT0003 → B216-016CT0003 → B216-926CT0003 → B216-026CT0003 → B216-036CT0003 → B216-036CT0012 → B216-036CT0013 → B216-036CC0006 → B216-936CC0006 → END
B2-MCC-69601 | -P20 | 01 |  | PE-L1-5C25/16-03 | PE-L1-5C25/16-03 | ACC-B2-059 |  |  | 1 | 492 | B2-MCC-69601-P2001 | 0.6/1kV CU/XLPE/LSZH | 4C x 25sqmm + 1C X 16sqmm | PE-L1-5C25/16-03 | 15 | 400 | N | 240 | AIR COOLED CONDENSER | B2-MCC-69601 | 400V MCC FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, N, PE | B2-HTP-16601 | ACC HEAT TRACING PANEL | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, N, PE | B269-006BT0026 → B269-006BT0027 → B269-006BT0051 → D0107-L42 → M0108 → D0105-L22 → M0107 → D0108-L13 → M0109 → B216-916DT0004 → B216-016DT0004 → B216-926DT0004 → B216-026DT0004 → B216-036DT0004 → B216-036CT0012 → B216-036CT0014 → B216-936CT0021 → B216-026CT0021 → B216-926CT0021 → B216-016CT0021 → END
B2-MCC-69601 | -P20 | 02 |  | PE-L1-5C50/25-01 | PE-L1-5C50/25-01 | ACC-B2-059-001 |  |  | 1 | 493 | B2-MCC-69601-P2002 | 0.6/1kV CU/XLPE/LSZH | 4C x 50sqmm + 1C X 25sqmm | PE-L1-5C50/25-01 | 15 | 400 | N | 240 | AIR COOLED CONDENSER | B2-MCC-69601 | 400V MCC FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, N, PE | B2-LP-16601 | ACC LIGHTING PANEL | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, N, PE | B269-006CT0027 → B269-006CT0051 → D0107-L42 → M0108 → D0105-L22 → M0107 → D0108-L14 → M0109 → B216-916DT0004 → B216-016DT0004 → B216-926DT0004 → B216-026DT0004 → B216-036DT0004 → B216-036CT0012 → B216-036CT0014 → END
B2-MCC-69601 | -P20 | 03 |  | PE-L1-5C70/35-01 | PE-L1-5C70/35-01 | ACC-B2-059-002 |  |  | 1 | 494 | B2-MCC-69601-P2003 | 0.6/1kV CU/XLPE/LSZH | 4C x 70sqmm + 1C X 35sqmm | PE-L1-5C70/35-01 | 37 | 400 | N | 240 | AIR COOLED CONDENSER | B2-MCC-69601 | 400V MCC FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, N, PE | B2-RP-16601 | ACC POWER SOCKET PANEL | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, N, PE | B269-006BT0026 → B269-006BT0027 → B269-006BT0051 → D0107-L42 → M0108 → D0105-L22 → M0107 → D0108-L13 → M0109 → B216-916DT0004 → B216-016DT0004 → B216-926DT0004 → B216-026DT0004 → B216-036DT0004 → B216-036CT0012 → B216-036CT0014 → END
B2-MCC-69603 | -P20 | 02 |  | PE-L1-4C4-23 | PE-L1-4C4-23 | ACC-B2-061 |  |  | 1 | 495 | B2-MCC-69603-P2002 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-23 | 1 | 400 | N | 310 | AIR COOLED CONDENSER | B2-MCC-69603 | 400V MCC FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-MOV-16001 | ACC VACUUM BREAKER MOV A | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006CT0034 → B269-006CT0027 → B269-006CT0051 → D0107-L42 → M0108 → D0105-L22 → M0107 → D0108-L13 → M0109 → B216-916DT0004 → B216-016DT0004 → B216-926DT0004 → B216-026DT0004 → B216-036DT0004 → B216-036CT0012 → B216-036CT0014 → B216-936CT0022 → B216-036CT0022 → B216-026CT0022 → B216-926CT0022 → B216-026CT0023 → B216-926CT0024 → B216-026CT0024 → B216-926CC0003 → END
B2-MCC-69603 | -P20 | 03 |  | PE-L1-4C4-15 | PE-L1-4C4-15 | ACC-B2-061-001 |  |  | 1 | 496 | B2-MCC-69603-P2003 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-15 | 1 | 400 | N | 310 | AIR COOLED CONDENSER | B2-MCC-69603 | 400V MCC FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-MOV-16002 | ACC VACUUM BREAKER MOV B | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006CT0034 → B269-006CT0027 → B269-006CT0051 → D0107-L42 → M0108 → D0105-L22 → M0107 → D0108-L13 → M0109 → B216-916DT0004 → B216-016DT0004 → B216-926DT0004 → B216-026DT0004 → B216-036DT0004 → B216-036CT0012 → B216-036CT0014 → B216-936CT0022 → B216-036CT0022 → B216-026CT0022 → B216-926CT0022 → B216-026CT0023 → B216-926CT0024 → B216-026CT0024 → B216-926CC0004 → END
B2-MCC-69601 | -P20 | 04 |  | PE-L1-4C4-07 | PE-L1-4C4-07 | ACC-B2-064 |  |  | 1 | 497 | B2-MCC-69601-P2004 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-07 | 1 | 400 | N | 40 | AIR COOLED CONDENSER | B2-MCC-69601 | 400V MCC FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-MOV-16071 | ACC LRVP A AIR INLET MOV | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-006AT0020 → B169-006AT0019 → B016-017BC0011 → B016-006BC0018 → END
B2-MCC-69601 | -P20 | 05 |  | PE-L1-4C4-09 | PE-L1-4C4-09 | ACC-B2-065 |  |  | 1 | 498 | B2-MCC-69601-P2005 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-09 | 1 | 400 | N | 40 | AIR COOLED CONDENSER | B2-MCC-69601 | 400V MCC FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-MOV-16081 | ACC LRVP B AIR INLET MOV | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-006AT0020 → B016-017BC0008 → B016-006BC0017 → END
B2-MCC-69601 | -P20 | 06 |  | PE-L1-4C4-10 | PE-L1-4C4-10 | ACC-B2-066 |  |  | 1 | 499 | B2-MCC-69601-P2006 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-10 | 1 | 400 | N | 50 | AIR COOLED CONDENSER | B2-MCC-69601 | 400V MCC FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-MOV-16091 | ACC LRVP C AIR INLET MOV | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-006AT0020 → B169-006AT0021 → B016-017BC0005 → B016-006BC0016 → END
B2-MCC-69603 | -P20 | 04 |  | PE-L1-4C4-04 | PE-L1-4C4-04 | ACC-B2-066-001 |  |  | 1 | 500 | B2-MCC-69603-P2004 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-04 | 1 | 400 | N | 50 | AIR COOLED CONDENSER | B2-MCC-69603 | 400V MCC FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-MOV-16075 | ACC LRVP A COOLING WATER INLET MOV | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-006AT0013 → B169-006AT0033 → B169-006AT0019 → B016-017BC0012 → B016-006BC0018 → END
B2-MCC-69603 | -P20 | 05 |  | PE-L1-4C4-04 | PE-L1-4C4-04 | ACC-B2-066-002 |  |  | 1 | 501 | B2-MCC-69603-P2005 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-04 | 1 | 400 | N | 50 | AIR COOLED CONDENSER | B2-MCC-69603 | 400V MCC FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-MOV-16085 | ACC LRVP B COOLING WATER INLET MOV | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-006AT0013 → B169-006AT0033 → B169-006AT0020 → B016-017BC0009 → B016-006BC0017 → END
B2-MCC-69601 | -P20 | 07 |  | PE-L1-4C4-04 | PE-L1-4C4-04 | ACC-B2-066-003 |  |  | 1 | 502 | B2-MCC-69601-P2007 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-04 | 1 | 400 | N | 50 | AIR COOLED CONDENSER | B2-MCC-69601 | 400V MCC FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-MOV-16095 | ACC LRVP C COOLING WATER INLET MOV | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-006AT0020 → B169-006AT0021 → B016-017BC0006 → B016-006BC0016 → END
B2-MCC-69603 | -P20 | 06 |  | PE-L1-4C4-18 | PE-L1-4C4-18 | ACC-B2-066-004 |  |  | 1 | 503 | B2-MCC-69603-P2006 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-18 | 0.3 | 400 | N | 60 | AIR COOLED CONDENSER | B2-MCC-69603 | 400V MCC FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-MOV-16073 | ACC LRVP A MOTIVE LINE MOV | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-006AT0013 → B169-006AT0033 → B169-006AT0019 → B016-017BC0013 → B016-006BC0018 → END
B2-MCC-69603 | -P20 | 07 |  | PE-L1-4C4-18 | PE-L1-4C4-18 | ACC-B2-066-005 |  |  | 1 | 504 | B2-MCC-69603-P2007 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-18 | 0.3 | 400 | N | 60 | AIR COOLED CONDENSER | B2-MCC-69603 | 400V MCC FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-MOV-16083 | ACC LRVP B MOTIVE LINE MOV | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-006AT0013 → B169-006AT0033 → B169-006AT0020 → B016-017BC0010 → B016-006BC0017 → END
B2-MCC-69601 | -P20 | 08 |  | PE-L1-4C4-18 | PE-L1-4C4-18 | ACC-B2-066-006 |  |  | 1 | 505 | B2-MCC-69601-P2008 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-18 | 0.3 | 400 | N | 50 | AIR COOLED CONDENSER | B2-MCC-69601 | 400V MCC FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-MOV-16093 | ACC LRVP C MOTIVE LINE MOV | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-006AT0020 → B169-006AT0021 → B016-017BC0007 → B016-006BC0016 → END
B2-MCC-69601 | -P20 | 09 |  | PE-L1-4C4-14 | PE-L1-4C4-14 | ACC-B2-067 |  |  | 1 | 506 | B2-MCC-69601-P2009 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-14 | 1 | 400 | N | 260 | AIR COOLED CONDENSER | B2-MCC-69601 | 400V MCC FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-MOV-16005 | ACC QUICK AIR TAKEOFF MOV | 2.2_AIR COOLED CONDENSER (ACC) #2 | L1, L2, L3, PE | B269-006CT0034 → B269-006CT0027 → B269-006CT0051 → D0107-L42 → M0108 → D0105-L22 → M0107 → D0108-L13 → M0109 → B216-916DT0004 → B216-016DT0004 → B216-926DT0004 → B216-026DT0004 → B216-036DT0004 → B216-036CT0012 → B216-036CT0014 → B216-936CT0022 → B216-036CT0022 → B216-026CT0022 → B216-926CT0022 → B216-026CT0023 → B216-026CC0002 → END
B1-MCC-64601 | -P20 | 05 |  | PE-L1-4C50/25-03 | PE-L1-4C50/25-03 | FIN-B1-001 |  |  | 1 | 507 | B1-MCC-64601-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 50sqmm + 1C X 25sqmm | PE-L1-4C50/25-03 | 45 | 400 | N | 140 | CLOSED COOLING WATER | B1-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-C(M)-66001 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #1 | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, PE | B164-016CT0098 → B164-016CT0099 → B164-996CT0022 → M0504 → D0531-L35 → M0510 → D0517-L24 → M0501 → D0503-L46 → M0502 → D0504-L46 → M0503 → B132-006AC0003 → B182-017AT0001 → B182-037AT0001 → FIELD RUN
B1-MCC-64602 | -P20 | 08 |  | PE-L1-4C50/25-03 | PE-L1-4C50/25-03 | FIN-B1-002 |  |  | 1 | 508 | B1-MCC-64602-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 50sqmm + 1C X 25sqmm | PE-L1-4C50/25-03 | 45 | 400 | N | 150 | CLOSED COOLING WATER | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-C(M)-66002 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #2 | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, PE | B164-016ET0106 → B164-996ET0022 → M0504 → D0531-L35 → M0510 → D0517-L24 → M0501 → D0503-L46 → M0502 → D0504-L46 → M0503 → B132-006AC0003 → B182-017AT0001 → B182-037AT0001 → FIELD RUN
B1-MCC-64601 | -P20 | 06 |  | PE-L1-4C50/25-03 | PE-L1-4C50/25-03 | FIN-B1-003 | DONE(10/12) | DONE | 1 | 509 | B1-MCC-64601-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 50sqmm + 1C X 25sqmm | PE-L1-4C50/25-03 | 45 | 400 | N | 140 | CLOSED COOLING WATER | B1-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-C(M)-66003 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #3 | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, PE | B164-016CT0098 → B164-016CT0099 → B164-996CT0022 → M0504 → D0531-L35 → M0510 → D0517-L24 → M0501 → D0503-L46 → M0502 → D0504-L46 → M0503 → B132-006AC0004 → B182-017AT0001 → B182-037AT0002 → FIELD RUN
B1-MCC-64602 | -P20 | 09 |  | PE-L1-4C50/25-03 | PE-L1-4C50/25-03 | FIN-B1-004 | DONE(10/12) | DONE | 1 | 510 | B1-MCC-64602-P2009 | 0.6/1kV CU/XLPE/LSZH | 3C x 50sqmm + 1C X 25sqmm | PE-L1-4C50/25-03 | 45 | 400 | N | 140 | CLOSED COOLING WATER | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-C(M)-66004 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #4 | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, PE | B164-016ET0106 → B164-996ET0022 → M0504 → D0531-L35 → M0510 → D0517-L24 → M0501 → D0503-L46 → M0502 → D0504-L46 → M0503 → B132-006AC0004 → B182-017AT0001 → B182-037AT0002 → FIELD RUN
B1-MCC-64601 | -P20 | 07 |  | PE-L1-4C50/25-04 | PE-L1-4C50/25-04 | FIN-B1-005 | DONE(10/6) | DONE | 1 | 511 | B1-MCC-64601-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 50sqmm + 1C X 25sqmm | PE-L1-4C50/25-04 | 45 | 400 | N | 140 | CLOSED COOLING WATER | B1-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-C(M)-66005 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #5 | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, PE | B164-016CT0098 → B164-016CT0099 → B164-996CT0022 → M0504 → D0531-L36 → M0510 → D0517-L25 → M0501 → D0503-L47 → M0502 → D0504-L47 → M0503 → B132-006AC0005 → B182-017AT0001 → B182-037AT0002 → B182-037AT0003 → FIELD RUN
B1-MCC-64602 | -P20 | 10 |  | PE-L1-4C50/25-04 | PE-L1-4C50/25-04 | FIN-B1-006 | DONE(10/6) | DONE | 1 | 512 | B1-MCC-64602-P2010 | 0.6/1kV CU/XLPE/LSZH | 3C x 50sqmm + 1C X 25sqmm | PE-L1-4C50/25-04 | 45 | 400 | N | 150 | CLOSED COOLING WATER | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-C(M)-66006 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #6 | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, PE | B164-016ET0106 → B164-996ET0022 → M0504 → D0531-L36 → M0510 → D0517-L25 → M0501 → D0503-L47 → M0502 → D0504-L47 → M0503 → B132-006AC0005 → B182-017AT0001 → B182-037AT0002 → B182-037AT0003 → FIELD RUN
B1-MCC-64601 | -P20 | 08 |  | PE-L1-4C50/25-04 | PE-L1-4C50/25-04 | FIN-B1-007 | DONE(10/6) | DONE | 1 | 513 | B1-MCC-64601-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 50sqmm + 1C X 25sqmm | PE-L1-4C50/25-04 | 45 | 400 | N | 150 | CLOSED COOLING WATER | B1-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-C(M)-66007 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #7 | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, PE | B164-016CT0098 → B164-016CT0099 → B164-996CT0022 → M0504 → D0531-L36 → M0510 → D0517-L25 → M0501 → D0503-L47 → M0502 → D0504-L47 → M0503 → B132-006AC0006 → B182-017AT0001 → B182-037AT0002 → B182-037AT0003 → FIELD RUN
B1-MCC-64602 | -P20 | 11 |  | PE-L1-4C50/25-04 | PE-L1-4C50/25-04 | FIN-B1-008 | DONE(10/6) | DONE | 1 | 514 | B1-MCC-64602-P2011 | 0.6/1kV CU/XLPE/LSZH | 3C x 50sqmm + 1C X 25sqmm | PE-L1-4C50/25-04 | 45 | 400 | N | 160 | CLOSED COOLING WATER | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-C(M)-66008 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #8 | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, PE | B164-016ET0106 → B164-996ET0022 → M0504 → D0531-L36 → M0510 → D0517-L25 → M0501 → D0503-L47 → M0502 → D0504-L47 → M0503 → B132-006AC0006 → B182-017AT0001 → B182-037AT0002 → B182-037AT0003 → FIELD RUN
B1-MCC-64601 | -P20 | 09 |  | PE-L1-4C50/25-04 | PE-L1-4C50/25-04 | FIN-B1-009 | DONE(10/6) | DONE | 1 | 515 | B1-MCC-64601-P2009 | 0.6/1kV CU/XLPE/LSZH | 3C x 50sqmm + 1C X 25sqmm | PE-L1-4C50/25-04 | 45 | 400 | N | 160 | CLOSED COOLING WATER | B1-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-C(M)-66009 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #9 | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, PE | B164-016CT0098 → B164-016CT0099 → B164-996CT0022 → M0504 → D0531-L37 → M0510 → D0517-L26 → M0501 → D0503-L48 → M0502 → D0504-L48 → M0503 → B132-006AC0007 → B182-017AT0001 → B182-037AT0002 → B182-037AT0003 → FIELD RUN
B1-MCC-64602 | -P20 | 12 |  | PE-L1-4C50/25-04 | PE-L1-4C50/25-04 | FIN-B1-010 | DONE(10/6) | DONE | 1 | 516 | B1-MCC-64602-P2012 | 0.6/1kV CU/XLPE/LSZH | 3C x 50sqmm + 1C X 25sqmm | PE-L1-4C50/25-04 | 45 | 400 | N | 170 | CLOSED COOLING WATER | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-C(M)-66010 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #10 | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, PE | B164-016ET0106 → B164-996ET0022 → M0504 → D0531-L37 → M0510 → D0517-L26 → M0501 → D0503-L48 → M0502 → D0504-L48 → M0503 → B132-006AC0007 → B182-017AT0001 → B182-037AT0002 → B182-037AT0003 → FIELD RUN
B1-MCC-64601 | -P20 | 10 |  | PE-L1-4C50/25-04 | PE-L1-4C50/25-04 | FIN-B1-011 | DONE(10/6) | DONE | 1 | 517 | B1-MCC-64601-P2010 | 0.6/1kV CU/XLPE/LSZH | 3C x 50sqmm + 1C X 25sqmm | PE-L1-4C50/25-04 | 45 | 400 | N | 170 | CLOSED COOLING WATER | B1-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-C(M)-66011 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #11 | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, PE | B164-016CT0098 → B164-016CT0099 → B164-996CT0022 → M0504 → D0531-L37 → M0510 → D0517-L26 → M0501 → D0503-L48 → M0502 → D0504-L48 → M0503 → B132-006AC0008 → B182-017AT0001 → B182-037AT0002 → B182-037AT0003 → FIELD RUN
B1-MCC-64602 | -P20 | 13 |  | PE-L1-4C50/25-05 | PE-L1-4C50/25-05 | FIN-B1-012 | DONE(10/6) | DONE | 1 | 518 | B1-MCC-64602-P2013 | 0.6/1kV CU/XLPE/LSZH | 3C x 50sqmm + 1C X 25sqmm | PE-L1-4C50/25-05 | 45 | 400 | N | 180 | CLOSED COOLING WATER | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-C(M)-66012 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #12 | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, PE | B164-016ET0106 → B164-996ET0022 → M0504 → D0531-L37 → M0510 → D0517-L26 → M0501 → D0503-L48 → M0502 → D0504-L48 → M0503 → B132-006AC0008 → B182-017AT0001 → B182-037AT0002 → B182-037AT0003 → FIELD RUN
B1-MCC-64601 | -P20 | 11 |  | PE-L1-3C4-26 | PE-L1-3C4-26 | FIN-B1-019 |  |  | 1 | 519 | B1-MCC-64601-P2011 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-26 | 0.11 | 230 | N | 140 | CLOSED COOLING WATER | B1-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-C(MH)-66001 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #1_SPACE HEATER | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, N, PE | B164-016AT0091 → B164-996AT0022 → M0504 → D0531-L35 → M0510 → D0517-L24 → M0501 → D0503-L46 → M0502 → D0504-L46 → M0503 → B132-006AC0003 → B182-017AT0001 → B182-037AT0001 → FIELD RUN
B1-MCC-64602 | -P20 | 14 |  | PE-L1-3C4-26 | PE-L1-3C4-26 | FIN-B1-020 |  |  | 1 | 520 | B1-MCC-64602-P2014 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-26 | 0.11 | 230 | N | 140 | CLOSED COOLING WATER | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-C(MH)-66002 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #2_SPACE HEATER | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, N, PE | B164-016AT0115 → B164-996AT0023 → M0504 → D0531-L35 → M0510 → D0517-L24 → M0501 → D0503-L46 → M0502 → D0504-L46 → M0503 → B132-006AC0003 → B182-017AT0001 → B182-037AT0001 → FIELD RUN
B1-MCC-64601 | -P20 | 12 |  | PE-L1-3C4-25 | PE-L1-3C4-25 | FIN-B1-021 |  |  | 1 | 521 | B1-MCC-64601-P2012 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-25 | 0.11 | 230 | N | 130 | CLOSED COOLING WATER | B1-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-C(MH)-66003 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #3_SPACE HEATER | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, N, PE | B164-016AT0091 → B164-996AT0022 → M0504 → D0531-L35 → M0510 → D0517-L24 → M0501 → D0503-L46 → M0502 → D0504-L46 → M0503 → B132-006AC0004 → B182-017AT0001 → B182-037AT0002 → FIELD RUN
B1-MCC-64602 | -P20 | 15 |  | PE-L1-3C4-25 | PE-L1-3C4-25 | FIN-B1-022 |  |  | 1 | 522 | B1-MCC-64602-P2015 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-25 | 0.11 | 230 | N | 140 | CLOSED COOLING WATER | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-C(MH)-66004 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #4_SPACE HEATER | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, N, PE | B164-016AT0115 → B164-996AT0023 → M0504 → D0531-L35 → M0510 → D0517-L24 → M0501 → D0503-L46 → M0502 → D0504-L46 → M0503 → B132-006AC0004 → B182-017AT0001 → B182-037AT0002 → FIELD RUN
B1-MCC-64601 | -P20 | 13 |  | PE-L1-3C4-26 | PE-L1-3C4-26 | FIN-B1-023 |  |  | 1 | 523 | B1-MCC-64601-P2013 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-26 | 0.11 | 230 | N | 140 | CLOSED COOLING WATER | B1-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-C(MH)-66005 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #5_SPACE HEATER | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, N, PE | B164-016AT0091 → B164-996AT0022 → M0504 → D0531-L36 → M0510 → D0517-L25 → M0501 → D0503-L47 → M0502 → D0504-L47 → M0503 → B132-006AC0005 → B182-017AT0001 → B182-037AT0002 → B182-037AT0003 → FIELD RUN
B1-MCC-64602 | -P20 | 16 |  | PE-L1-3C4-26 | PE-L1-3C4-26 | FIN-B1-024 |  |  | 1 | 524 | B1-MCC-64602-P2016 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-26 | 0.11 | 230 | N | 150 | CLOSED COOLING WATER | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-C(MH)-66006 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #6_SPACE HEATER | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, N, PE | B164-016AT0115 → B164-996AT0023 → M0504 → D0531-L36 → M0510 → D0517-L25 → M0501 → D0503-L47 → M0502 → D0504-L47 → M0503 → B132-006AC0005 → B182-017AT0001 → B182-037AT0002 → B182-037AT0003 → FIELD RUN
B1-MCC-64601 | -P20 | 14 |  | PE-L1-3C4-26 | PE-L1-3C4-26 | FIN-B1-025 |  |  | 1 | 525 | B1-MCC-64601-P2014 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-26 | 0.11 | 230 | N | 150 | CLOSED COOLING WATER | B1-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-C(MH)-66007 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #7_SPACE HEATER | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, N, PE | B164-016AT0091 → B164-996AT0022 → M0504 → D0531-L36 → M0510 → D0517-L25 → M0501 → D0503-L47 → M0502 → D0504-L47 → M0503 → B132-006AC0006 → B182-017AT0001 → B182-037AT0002 → B182-037AT0003 → FIELD RUN
B1-MCC-64602 | -P20 | 17 |  | PE-L1-3C4-26 | PE-L1-3C4-26 | FIN-B1-026 |  |  | 1 | 526 | B1-MCC-64602-P2017 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-26 | 0.11 | 230 | N | 150 | CLOSED COOLING WATER | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-C(MH)-66008 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #8_SPACE HEATER | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, N, PE | B164-016AT0115 → B164-996AT0023 → M0504 → D0531-L36 → M0510 → D0517-L25 → M0501 → D0503-L47 → M0502 → D0504-L47 → M0503 → B132-006AC0006 → B182-017AT0001 → B182-037AT0002 → B182-037AT0003 → FIELD RUN
B1-MCC-64601 | -P20 | 15 |  | PE-L1-3C4-26 | PE-L1-3C4-26 | FIN-B1-027 |  |  | 1 | 527 | B1-MCC-64601-P2015 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-26 | 0.11 | 230 | N | 160 | CLOSED COOLING WATER | B1-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-C(MH)-66009 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #9_SPACE HEATER | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, N, PE | B164-016AT0091 → B164-996AT0022 → M0504 → D0531-L37 → M0510 → D0517-L26 → M0501 → D0503-L48 → M0502 → D0504-L48 → M0503 → B132-006AC0007 → B182-017AT0001 → B182-037AT0002 → B182-037AT0003 → FIELD RUN
B1-MCC-64602 | -P20 | 18 |  | PE-L1-3C4-26 | PE-L1-3C4-26 | FIN-B1-028 |  |  | 1 | 528 | B1-MCC-64602-P2018 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-26 | 0.11 | 230 | N | 160 | CLOSED COOLING WATER | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-C(MH)-66010 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #10_SPACE HEATER | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, N, PE | B164-016AT0115 → B164-996AT0023 → M0504 → D0531-L37 → M0510 → D0517-L26 → M0501 → D0503-L48 → M0502 → D0504-L48 → M0503 → B132-006AC0007 → B182-017AT0001 → B182-037AT0002 → B182-037AT0003 → FIELD RUN
B1-MCC-64601 | -P20 | 16 |  | PE-L1-3C4-26 | PE-L1-3C4-26 | FIN-B1-029 | DONE(10/12) | DONE | 1 | 529 | B1-MCC-64601-P2016 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-26 | 0.11 | 230 | N | 170 | CLOSED COOLING WATER | B1-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-C(MH)-66011 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #11_SPACE HEATER | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, N, PE | B164-016AT0091 → B164-996AT0022 → M0504 → D0531-L37 → M0510 → D0517-L26 → M0501 → D0503-L48 → M0502 → D0504-L48 → M0503 → B132-006AC0008 → B182-017AT0001 → B182-037AT0002 → B182-037AT0003 → FIELD RUN
B1-MCC-64602 | -P20 | 19 |  | PE-L1-3C4-26 | PE-L1-3C4-26 | FIN-B1-030 | DONE(10/12) | DONE | 1 | 530 | B1-MCC-64602-P2019 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-26 | 0.11 | 230 | N | 170 | CLOSED COOLING WATER | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-C(MH)-66012 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #12_SPACE HEATER | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, N, PE | B164-016AT0115 → B164-996AT0023 → M0504 → D0531-L37 → M0510 → D0517-L26 → M0501 → D0503-L48 → M0502 → D0504-L48 → M0503 → B132-006AC0008 → B182-017AT0001 → B182-037AT0002 → B182-037AT0003 → FIELD RUN
B1-MCC-64601 | -P20 | 17 |  | PE-L1-4C25/16-03 | PE-L1-4C25/16-03 | FIN-B1-037 | DONE(10/6) | DONE | 1 | 531 | B1-MCC-64601-P2017 | 0.6/1kV CU/XLPE/LSZH | 3C x 25sqmm + 1C X 16sqmm | PE-L1-4C25/16-03 | 18.5 | 400 | N | 190 | CLOSED COOLING WATER | B1-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-P-66001 | DELUGE SPRAY PUMP_MOTOR #1 | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, PE | B164-016CT0098 → B164-016CT0099 → B164-996CT0022 → M0504 → D0531-L25 → M0510 → D0517-L14 → M0501 → D0503-L46 → M0502 → D0504-L46 → M0503 → B132-006AC0003 → B182-017AT0001 → B182-037AT0002 → B182-037AT0003 → B182-037AT0004 → B182-037AT0005 → B182-017AT0003 → FIELD RUN
B1-MCC-64602 | -P20 | 20 |  | PE-L1-4C25/16-03 | PE-L1-4C25/16-03 | FIN-B1-038 | DONE(10/6) | DONE | 1 | 532 | B1-MCC-64602-P2020 | 0.6/1kV CU/XLPE/LSZH | 3C x 25sqmm + 1C X 16sqmm | PE-L1-4C25/16-03 | 18.5 | 400 | N | 190 | CLOSED COOLING WATER | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-P-66002 | DELUGE SPRAY PUMP_MOTOR #2 | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, PE | B164-016ET0106 → B164-996ET0022 → M0504 → D0531-L26 → M0510 → D0517-L15 → M0501 → D0503-L47 → M0502 → D0504-L47 → M0503 → B132-006AC0004 → B182-017AT0001 → B182-037AT0002 → B182-037AT0003 → B182-037AT0004 → B182-037AT0005 → B182-017AT0003 → FIELD RUN
B1-MCC-64602 | -P20 | 21 |  | PE-L1-5C50/25-01 | PE-L1-5C50/25-01 | FIN-B1-038-004 |  |  | 1 | 533 | B1-MCC-64602-P2021 | 0.6/1kV CU/XLPE/LSZH | 4C x 50sqmm + 1C X 25sqmm | PE-L1-5C50/25-01 | 40 | 400 | N | 120 | CLOSED COOLING WATER | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B1-PDP-66001 | PDP FOR HEAT TRACING & LIGHTING) | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, N, PE | B164-016ET0106 → B164-996ET0022 → M0504 → D0531-L36 → M0510 → D0517-L15 → M0501 → D0503-L47 → M0502 → D0504-L47 → M0503 → B132-006AC0002 → END
B1-MCC-64602 | -P20 | 22 |  | PE-L1-4C4-04 | PE-L1-4C4-04 | FIN-B1-039 | DONE(10/12) | DONE | 1 | 534 | B1-MCC-64602-P2022 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-04 | 0.2 | 400 | N | 190 | CLOSED COOLING WATER | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-66001 | M.O.V. FOR DELUGE TANK | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, PE | B164-016ET0106 → B164-996ET0022 → M0504 → D0531-L36 → M0510 → D0517-L15 → M0501 → D0503-L47 → M0502 → D0504-L47 → M0503 → B132-006AC0005 → B182-017AT0001 → B182-037AT0002 → B182-037AT0003 → B182-037AT0004 → B182-037AT0005 → B182-017AT0003 → FIELD RUN
B1-DB-64602 | -P20 | 17 |  | PE-L1-3C10-01 | PE-L1-3C10-01 | FIN-B1-040 | DONE(10/12) | DONE | 1 | 535 | B1-DB-64602-P2017 | 0.6/1kV CU/XLPE/LSZH | 3C x 10sqmm | PE-L1-3C10-01 | 1.11 | 230 | N | 180 | CLOSED COOLING WATER | B1-DB-64602 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-C(SH)-66013 | FIN FAN COOLER PACKAGE (CCW)_PIT INSTRUMENT BOX_SPACE HEATER | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, N, PE | B164-016AT0115 → B164-996AT0023 → M0504 → D0531-L41 → M0510 → D0517-L16 → M0501 → D0503-L48 → M0502 → D0504-L48 → M0503 → B132-006AC0008 → B182-017AT0001 → B182-037AT0002 → B182-037AT0003 → B182-037AT0004 → B182-037AT0005 → B182-017AT0003 → B132-016AC0002 → END
B2-MCC-64601 | -P20 | 06 |  | PE-L1-4C50/25-05 | PE-L1-4C50/25-05 | FIN-B2-001 |  |  | 1 | 536 | B2-MCC-64601-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 50sqmm + 1C X 25sqmm | PE-L1-4C50/25-05 | 45 | 400 | N | 150 | CLOSED COOLING WATER | B2-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-C(M)-66001 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #1 | 7.2_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, PE | B264-016AT0024 → B264-016AT0206 → B264-996AT0001 → M0401 → D0403-L13 → M0402 → D0402-L13 → M0424 → D0422-L13 → M0403 → B232-006AC0003 → B282-017AT0001 → B282-037AT0001 → FIELD RUN
B2-MCC-64602 | -P20 | 07 |  | PE-L1-4C50/25-05 | PE-L1-4C50/25-05 | FIN-B2-002 |  |  | 1 | 537 | B2-MCC-64602-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 50sqmm + 1C X 25sqmm | PE-L1-4C50/25-05 | 45 | 400 | N | 170 | CLOSED COOLING WATER | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-C(M)-66002 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #2 | 7.2_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, PE | B264-016BT0045 → B264-016BT0205 → B264-016BT0024 → B264-016BT0206 → B264-996BT0001 → M0401 → D0403-L13 → M0402 → D0402-L13 → M0424 → D0422-L13 → M0403 → B232-006AC0003 → B282-017AT0001 → B282-037AT0001 → FIELD RUN
B2-MCC-64601 | -P20 | 07 |  | PE-L1-4C50/25-05 | PE-L1-4C50/25-05 | FIN-B2-003 |  |  | 1 | 538 | B2-MCC-64601-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 50sqmm + 1C X 25sqmm | PE-L1-4C50/25-05 | 45 | 400 | N | 140 | CLOSED COOLING WATER | B2-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-C(M)-66003 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #3 | 7.2_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, PE | B264-016AT0024 → B264-016AT0206 → B264-996AT0001 → M0401 → D0403-L13 → M0402 → D0402-L13 → M0424 → D0422-L13 → M0403 → B232-006AC0004 → B282-017AT0001 → B282-037AT0002 → FIELD RUN
B2-MCC-64602 | -P20 | 08 |  | PE-L1-4C50/25-05 | PE-L1-4C50/25-05 | FIN-B2-004 |  |  | 1 | 539 | B2-MCC-64602-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 50sqmm + 1C X 25sqmm | PE-L1-4C50/25-05 | 45 | 400 | N | 160 | CLOSED COOLING WATER | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-C(M)-66004 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #4 | 7.2_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, PE | B264-016BT0045 → B264-016BT0205 → B264-016BT0024 → B264-016BT0206 → B264-996BT0001 → M0401 → D0403-L13 → M0402 → D0402-L13 → M0424 → D0422-L13 → M0403 → B232-006AC0004 → B282-017AT0001 → B282-037AT0002 → FIELD RUN
B2-MCC-64601 | -P20 | 08 |  | PE-L1-4C50/25-05 | PE-L1-4C50/25-05 | FIN-B2-005 |  |  | 1 | 540 | B2-MCC-64601-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 50sqmm + 1C X 25sqmm | PE-L1-4C50/25-05 | 45 | 400 | N | 150 | CLOSED COOLING WATER | B2-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-C(M)-66005 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #5 | 7.2_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, PE | B264-016AT0024 → B264-016AT0206 → B264-996AT0001 → M0401 → D0403-L14 → M0402 → D0402-L14 → M0424 → D0422-L12 → M0403 → B232-006AC0005 → B282-017AT0001 → B282-037AT0002 → B282-037AT0003 → FIELD RUN
B2-MCC-64602 | -P20 | 09 |  | PE-L1-4C50/25-05 | PE-L1-4C50/25-05 | FIN-B2-006 |  |  | 1 | 541 | B2-MCC-64602-P2009 | 0.6/1kV CU/XLPE/LSZH | 3C x 50sqmm + 1C X 25sqmm | PE-L1-4C50/25-05 | 45 | 400 | N | 170 | CLOSED COOLING WATER | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-C(M)-66006 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #6 | 7.2_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, PE | B264-016BT0045 → B264-016BT0205 → B264-016BT0024 → B264-016BT0206 → B264-996BT0001 → M0401 → D0403-L14 → M0402 → D0402-L14 → M0424 → D0422-L12 → M0403 → B232-006AC0005 → B282-017AT0001 → B282-037AT0002 → B282-037AT0003 → FIELD RUN
B2-MCC-64601 | -P20 | 09 |  | PE-L1-4C50/25-06 | PE-L1-4C50/25-06 | FIN-B2-007 |  |  | 1 | 542 | B2-MCC-64601-P2009 | 0.6/1kV CU/XLPE/LSZH | 3C x 50sqmm + 1C X 25sqmm | PE-L1-4C50/25-06 | 45 | 400 | N | 160 | CLOSED COOLING WATER | B2-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-C(M)-66007 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #7 | 7.2_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, PE | B264-016AT0024 → B264-016AT0206 → B264-996AT0001 → M0401 → D0403-L14 → M0402 → D0402-L14 → M0424 → D0422-L12 → M0403 → B232-006AC0006 → B282-017AT0001 → B282-037AT0002 → B282-037AT0003 → FIELD RUN
B2-MCC-64602 | -P20 | 10 |  | PE-L1-4C50/25-06 | PE-L1-4C50/25-06 | FIN-B2-008 |  |  | 1 | 543 | B2-MCC-64602-P2010 | 0.6/1kV CU/XLPE/LSZH | 3C x 50sqmm + 1C X 25sqmm | PE-L1-4C50/25-06 | 45 | 400 | N | 180 | CLOSED COOLING WATER | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-C(M)-66008 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #8 | 7.2_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, PE | B264-016BT0045 → B264-016BT0205 → B264-016BT0024 → B264-016BT0206 → B264-996BT0001 → M0401 → D0403-L14 → M0402 → D0402-L14 → M0424 → D0422-L12 → M0403 → B232-006AC0006 → B282-017AT0001 → B282-037AT0002 → B282-037AT0003 → FIELD RUN
B2-MCC-64601 | -P20 | 10 |  | PE-L1-4C50/25-06 | PE-L1-4C50/25-06 | FIN-B2-009 |  |  | 1 | 544 | B2-MCC-64601-P2010 | 0.6/1kV CU/XLPE/LSZH | 3C x 50sqmm + 1C X 25sqmm | PE-L1-4C50/25-06 | 45 | 400 | N | 170 | CLOSED COOLING WATER | B2-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-C(M)-66009 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #9 | 7.2_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, PE | B264-016AT0024 → B264-016AT0206 → B264-996AT0001 → M0401 → D0403-L15 → M0402 → D0402-L15 → M0424 → D0422-L11 → M0403 → B232-006AC0007 → B282-017AT0001 → B282-037AT0002 → B282-037AT0003 → FIELD RUN
B2-MCC-64602 | -P20 | 11 |  | PE-L1-4C50/25-06 | PE-L1-4C50/25-06 | FIN-B2-010 |  |  | 1 | 545 | B2-MCC-64602-P2011 | 0.6/1kV CU/XLPE/LSZH | 3C x 50sqmm + 1C X 25sqmm | PE-L1-4C50/25-06 | 45 | 400 | N | 190 | CLOSED COOLING WATER | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-C(M)-66010 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #10 | 7.2_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, PE | B264-016BT0045 → B264-016BT0205 → B264-016BT0024 → B264-016BT0206 → B264-996BT0001 → M0401 → D0403-L15 → M0402 → D0402-L15 → M0424 → D0422-L11 → M0403 → B232-006AC0007 → B282-017AT0001 → B282-037AT0002 → B282-037AT0003 → FIELD RUN
B2-MCC-64601 | -P20 | 11 |  | PE-L1-4C50/25-06 | PE-L1-4C50/25-06 | FIN-B2-011 |  |  | 1 | 546 | B2-MCC-64601-P2011 | 0.6/1kV CU/XLPE/LSZH | 3C x 50sqmm + 1C X 25sqmm | PE-L1-4C50/25-06 | 45 | 400 | N | 180 | CLOSED COOLING WATER | B2-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-C(M)-66011 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #11 | 7.2_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, PE | B264-016AT0024 → B264-016AT0206 → B264-996AT0001 → M0401 → D0403-L15 → M0402 → D0402-L15 → M0424 → D0422-L11 → M0403 → B232-006AC0008 → B282-017AT0001 → B282-037AT0002 → B282-037AT0003 → FIELD RUN
B2-MCC-64602 | -P20 | 12 |  | PE-L1-4C50/25-06 | PE-L1-4C50/25-06 | FIN-B2-012 |  |  | 1 | 547 | B2-MCC-64602-P2012 | 0.6/1kV CU/XLPE/LSZH | 3C x 50sqmm + 1C X 25sqmm | PE-L1-4C50/25-06 | 45 | 400 | N | 200 | CLOSED COOLING WATER | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-C(M)-66012 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #12 | 7.2_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, PE | B264-016BT0045 → B264-016BT0205 → B264-016BT0024 → B264-016BT0206 → B264-996BT0001 → M0401 → D0403-L15 → M0402 → D0402-L15 → M0424 → D0422-L13 → M0403 → B232-006AC0008 → B282-017AT0001 → B282-037AT0002 → B282-037AT0003 → FIELD RUN
B2-MCC-64601 | -P20 | 12 |  | PE-L1-3C4-26 | PE-L1-3C4-26 | FIN-B2-019 |  |  | 1 | 548 | B2-MCC-64601-P2012 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-26 | 0.11 | 230 | N | 150 | CLOSED COOLING WATER | B2-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-C(MH)-66001 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #1_SPACE HEATER | 7.2_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, N, PE | B264-016AT0024 → B264-016AT0206 → B264-996AT0001 → M0401 → D0403-L13 → M0402 → D0402-L13 → M0424 → D0422-L13 → M0403 → B232-006AC0003 → B282-017AT0001 → B282-037AT0001 → FIELD RUN
B2-MCC-64602 | -P20 | 13 | 재배정 | PE-L1-3C4-27 | PE-L1-3C4-29 | FIN-B2-020 |  |  | 1 | 549 | B2-MCC-64602-P2013 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-29 | 0.11 | 230 | N | 170 | CLOSED COOLING WATER | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-C(MH)-66002 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #2_SPACE HEATER | 7.2_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, N, PE | B264-016BT0045 → B264-016BT0205 → B264-016BT0024 → B264-016BT0206 → B264-996BT0001 → M0401 → D0403-L13 → M0402 → D0402-L13 → M0424 → D0422-L13 → M0403 → B232-006AC0003 → B282-017AT0001 → B282-037AT0001 → FIELD RUN
B2-MCC-64601 | -P20 | 13 |  | PE-L1-3C4-27 | PE-L1-3C4-29 | FIN-B2-021 |  |  | 1 | 550 | B2-MCC-64601-P2013 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-29 | 0.11 | 230 | N | 140 | CLOSED COOLING WATER | B2-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-C(MH)-66003 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #3_SPACE HEATER | 7.2_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, N, PE | B264-016AT0024 → B264-016AT0206 → B264-996AT0001 → M0401 → D0403-L13 → M0402 → D0402-L13 → M0424 → D0422-L13 → M0403 → B232-006AC0004 → B282-017AT0001 → B282-037AT0002 → FIELD RUN
B2-MCC-64602 | -P20 | 14 |  | PE-L1-3C4-27 | PE-L1-3C4-29 | FIN-B2-022 |  |  | 1 | 551 | B2-MCC-64602-P2014 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-29 | 0.11 | 230 | N | 160 | CLOSED COOLING WATER | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-C(MH)-66004 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #4_SPACE HEATER | 7.2_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, N, PE | B264-016BT0045 → B264-016BT0205 → B264-016BT0024 → B264-016BT0206 → B264-996BT0001 → M0401 → D0403-L13 → M0402 → D0402-L13 → M0424 → D0422-L13 → M0403 → B232-006AC0004 → B282-017AT0001 → B282-037AT0002 → FIELD RUN
B2-MCC-64601 | -P20 | 14 |  | PE-L1-3C4-27 | PE-L1-3C4-29 | FIN-B2-023 |  |  | 1 | 552 | B2-MCC-64601-P2014 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-29 | 0.11 | 230 | N | 150 | CLOSED COOLING WATER | B2-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-C(MH)-66005 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #5_SPACE HEATER | 7.2_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, N, PE | B264-016AT0024 → B264-016AT0206 → B264-996AT0001 → M0401 → D0403-L14 → M0402 → D0402-L14 → M0424 → D0422-L12 → M0403 → B232-006AC0005 → B282-017AT0001 → B282-037AT0002 → B282-037AT0003 → FIELD RUN
B2-MCC-64602 | -P20 | 15 |  | PE-L1-3C4-27 | PE-L1-3C4-29 | FIN-B2-024 |  |  | 1 | 553 | B2-MCC-64602-P2015 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-29 | 0.11 | 230 | N | 170 | CLOSED COOLING WATER | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-C(MH)-66006 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #6_SPACE HEATER | 7.2_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, N, PE | B264-016BT0045 → B264-016BT0205 → B264-016BT0024 → B264-016BT0206 → B264-996BT0001 → M0401 → D0403-L14 → M0402 → D0402-L14 → M0424 → D0422-L12 → M0403 → B232-006AC0005 → B282-017AT0001 → B282-037AT0002 → B282-037AT0003 → FIELD RUN
B2-MCC-64601 | -P20 | 15 |  | PE-L1-3C4-27 | PE-L1-3C4-29 | FIN-B2-025 |  |  | 1 | 554 | B2-MCC-64601-P2015 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-29 | 0.11 | 230 | N | 160 | CLOSED COOLING WATER | B2-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-C(MH)-66007 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #7_SPACE HEATER | 7.2_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, N, PE | B264-016AT0024 → B264-016AT0206 → B264-996AT0001 → M0401 → D0403-L14 → M0402 → D0402-L14 → M0424 → D0422-L12 → M0403 → B232-006AC0006 → B282-017AT0001 → B282-037AT0002 → B282-037AT0003 → FIELD RUN
B2-MCC-64602 | -P20 | 16 |  | PE-L1-3C4-27 | PE-L1-3C4-27 | FIN-B2-026 |  |  | 1 | 555 | B2-MCC-64602-P2016 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-27 | 0.11 | 230 | N | 180 | CLOSED COOLING WATER | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-C(MH)-66008 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #8_SPACE HEATER | 7.2_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, N, PE | B264-016BT0045 → B264-016BT0205 → B264-016BT0024 → B264-016BT0206 → B264-996BT0001 → M0401 → D0403-L14 → M0402 → D0402-L14 → M0424 → D0422-L12 → M0403 → B232-006AC0006 → B282-017AT0001 → B282-037AT0002 → B282-037AT0003 → FIELD RUN
B2-MCC-64601 | -P20 | 16 | 재배정 | PE-L1-3C4-27 | PE-L1-3C4-29 | FIN-B2-027 |  |  | 1 | 556 | B2-MCC-64601-P2016 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-29 | 0.11 | 230 | N | 170 | CLOSED COOLING WATER | B2-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-C(MH)-66009 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #9_SPACE HEATER | 7.2_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, N, PE | B264-016AT0024 → B264-016AT0206 → B264-996AT0001 → M0401 → D0403-L15 → M0402 → D0402-L15 → M0424 → D0422-L11 → M0403 → B232-006AC0007 → B282-017AT0001 → B282-037AT0002 → B282-037AT0003 → FIELD RUN
B2-MCC-64602 | -P20 | 17 |  | PE-L1-3C4-27 | PE-L1-3C4-27 | FIN-B2-028 |  |  | 1 | 557 | B2-MCC-64602-P2017 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-27 | 0.11 | 230 | N | 190 | CLOSED COOLING WATER | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-C(MH)-66010 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #10_SPACE HEATER | 7.2_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, N, PE | B264-016BT0045 → B264-016BT0205 → B264-016BT0024 → B264-016BT0206 → B264-996BT0001 → M0401 → D0403-L15 → M0402 → D0402-L15 → M0424 → D0422-L11 → M0403 → B232-006AC0007 → B282-017AT0001 → B282-037AT0002 → B282-037AT0003 → FIELD RUN
B2-MCC-64601 | -P20 | 17 |  | PE-L1-3C4-27 | PE-L1-3C4-27 | FIN-B2-029 |  |  | 1 | 558 | B2-MCC-64601-P2017 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-27 | 0.11 | 230 | N | 180 | CLOSED COOLING WATER | B2-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-C(MH)-66011 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #11_SPACE HEATER | 7.2_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, N, PE | B264-016AT0024 → B264-016AT0206 → B264-996AT0001 → M0401 → D0403-L15 → M0402 → D0402-L15 → M0424 → D0422-L11 → M0403 → B232-006AC0008 → B282-017AT0001 → B282-037AT0002 → B282-037AT0003 → FIELD RUN
B2-MCC-64602 | -P20 | 18 |  | PE-L1-3C4-27 | PE-L1-3C4-27 | FIN-B2-030 |  |  | 1 | 559 | B2-MCC-64602-P2018 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-27 | 0.11 | 230 | N | 200 | CLOSED COOLING WATER | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-C(MH)-66012 | FIN FAN COOLER PACKAGE (CCW)_FAN MOTOR #12_SPACE HEATER | 7.2_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, N, PE | B264-016BT0045 → B264-016BT0205 → B264-016BT0024 → B264-016BT0206 → B264-996BT0001 → M0401 → D0403-L15 → M0402 → D0402-L15 → M0424 → D0422-L11 → M0403 → B232-006AC0008 → B282-017AT0001 → B282-037AT0002 → B282-037AT0003 → FIELD RUN
B2-MCC-64602 | -P20 | 19 |  | PE-L1-4C25/16-02 | PE-L1-4C25/16-02 | FIN-B2-037 |  |  | 1 | 560 | B2-MCC-64602-P2019 | 0.6/1kV CU/XLPE/LSZH | 3C x 25sqmm + 1C X 16sqmm | PE-L1-4C25/16-02 | 18.5 | 400 | N | 210 | CLOSED COOLING WATER | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-P-66001 | DELUGE SPRAY PUMP_MOTOR #1 | 7.2_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, PE | B264-016BT0045 → B264-016BT0205 → B264-016BT0024 → B264-016BT0206 → B264-996BT0001 → M0401 → D0403-L14 → M0402 → D0402-L14 → M0424 → D0422-L11 → M0403 → B232-006AC0003 → B282-017AT0001 → B282-037AT0002 → B282-037AT0003 → B282-037AT0004 → B282-037AT0005 → B282-017AT0003 → FIELD RUN
B2-MCC-64601 | -P20 | 18 |  | PE-L1-4C25/16-02 | PE-L1-4C25/16-02 | FIN-B2-038 |  |  | 1 | 561 | B2-MCC-64601-P2018 | 0.6/1kV CU/XLPE/LSZH | 3C x 25sqmm + 1C X 16sqmm | PE-L1-4C25/16-02 | 18.5 | 400 | N | 190 | CLOSED COOLING WATER | B2-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-P-66002 | DELUGE SPRAY PUMP_MOTOR #2 | 7.2_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, PE | B264-016AT0024 → B264-016AT0206 → B264-996AT0001 → M0401 → D0403-L13 → M0402 → D0402-L13 → M0424 → D0422-L13 → M0403 → B232-006AC0004 → B282-017AT0001 → B282-037AT0002 → B282-037AT0003 → B282-037AT0004 → B282-037AT0005 → B282-017AT0003 → FIELD RUN
B2-MCC-64602 | -P20 | 20 |  | PE-L1-5C50/25-02 | PE-L1-5C50/25-02 | FIN-B2-038-004 |  |  | 1 | 562 | B2-MCC-64602-P2020 | 0.6/1kV CU/XLPE/LSZH | 4C x 50sqmm + 1C X 25sqmm | PE-L1-5C50/25-02 | 40 | 400 | N | 140 | CLOSED COOLING WATER | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, N, PE | B2-PDP-66001 | PDP FOR HEAT TRACING & LIGHTING) | 7.2_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, N, PE | B264-016BT0045 → B264-016BT0205 → B264-016BT0024 → B264-016BT0206 → B264-996BT0001 → M0401 → D0403-L11 → M0402 → D0402-L11 → M0424 → D0422-L11 → M0403 → B232-006AC0002 → END
B2-MCC-64602 | -P20 | 21 |  | PE-L1-4C4-26 | PE-L1-4C4-26 | FIN-B2-039 |  |  | 1 | 563 | B2-MCC-64602-P2021 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-26 | 0.2 | 400 | N | 210 | CLOSED COOLING WATER | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-66001 | M.O.V. FOR DELUGE TANK | 7.2_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, PE | B264-016BT0045 → B264-016BT0205 → B264-016BT0024 → B264-016BT0206 → B264-996BT0001 → M0401 → D0403-L11 → M0402 → D0402-L11 → M0424 → D0422-L11 → M0403 → B232-006AC0005 → B282-017AT0001 → B282-037AT0002 → B282-037AT0003 → B282-037AT0004 → B282-037AT0005 → B282-017AT0003 → FIELD RUN
B2-DB-64602 | -P20 | 08 |  | PE-L1-3C10-01 | PE-L1-3C10-01 | FIN-B2-040 |  |  | 1 | 564 | B2-DB-64602-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 10sqmm | PE-L1-3C10-01 | 1.11 | 230 | N | 210 | CLOSED COOLING WATER | B2-DB-64602 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-C(SH)-66013 | FIN FAN COOLER PACKAGE (CCW)_PIT INSTRUMENT BOX_SPACE HEATER | 7.2_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, N, PE | B264-016AT0027 → B264-016AT0026 → B264-016AT0025 → B264-016AT0206 → B264-996AT0001 → M0401 → D0403-L15 → M0402 → D0402-L15 → M0424 → D0422-L11 → M0403 → B232-006AC0008 → B282-017AT0001 → B282-037AT0002 → B282-037AT0003 → B282-037AT0004 → B282-037AT0005 → B282-017AT0003 → B232-016AC0002 → END | 부하추가
B0-MCC-49601 | -P20 | 01 |  | PE-L1-4C16-01 | PE-L1-4C16-01 | RWP-C-001 | DONE(10/27) | DONE | 1 | 565 | B0-MCC-49601-P2001 | 0.6/1kV CU/XLPE/LSZH | 4C x 16sqmm | PE-L1-4C16-01 | 15 | 400 | N | 220 | RAW WATER SYSTEM | B0-MCC-49601 | 400V MCC FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-P-38001A | RAW WATER DISTRIBUTION PUMP MOTOR - A | 12.1_RAW WATER&FIRE WATER PUMP HOUSE | L1, L2, L3, PE | B049-006AT0004 → B049-006AT0003 → B049-006AT0002 → D0204-L15 → M0207 → D0203-L21 → M0206 → D0205-L21 → M0205 → B025-996FT0005 → B025-016FT0029 → B025-016FT0028 → B038-017AC0501 → B038-006AC0011 → B038-006AC0006 → END
B0-MCC-49602 | -P20 | 01 |  | PE-L1-4C16-01 | PE-L1-4C16-01 | RWP-C-002 | DONE(10/27) | DONE | 1 | 566 | B0-MCC-49602-P2001 | 0.6/1kV CU/XLPE/LSZH | 4C x 16sqmm | PE-L1-4C16-01 | 15 | 400 | N | 230 | RAW WATER SYSTEM | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-P-38001B | RAW WATER DISTRIBUTION PUMP MOTOR - B | 12.1_RAW WATER&FIRE WATER PUMP HOUSE | L1, L2, L3, PE | B049-006AT0008 → B049-006AT0009 → B049-006AT0011 → B049-006AT0003 → B049-006AT0002 → D0204-L18 → M0207 → D0203-L24 → M0206 → D0205-L24 → M0205 → B025-996FT0005 → B025-016FT0029 → B025-016FT0028 → B038-017AC0501 → B038-006AC0011 → B038-006AC0005 → END
B0-MCC-49601 | -P20 | 02 |  | PE-L1-4C16-01 | PE-L1-4C16-01 | RWP-C-002-001 | DONE(10/27) | DONE | 1 | 567 | B0-MCC-49601-P2002 | 0.6/1kV CU/XLPE/LSZH | 4C x 16sqmm | PE-L1-4C16-01 | 15 | 400 | N | 220 | RAW WATER SYSTEM | B0-MCC-49601 | 400V MCC FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-P-38001C | RAW WATER DISTRIBUTION PUMP MOTOR - C | 12.1_RAW WATER&FIRE WATER PUMP HOUSE | L1, L2, L3, PE | B049-006BT0004 → B049-006BT0003 → B049-006BT0001 → D0204-L15 → M0207 → D0203-L21 → M0206 → D0205-L21 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B038-016AC0001 → B038-006AC0010 → B038-006AC0002 → END
B0-MCC-49602 | -P20 | 02 |  | PE-L1-4C16-01 | PE-L1-4C16-01 | RWP-C-002-002 | DONE(10/27) | DONE | 1 | 568 | B0-MCC-49602-P2002 | 0.6/1kV CU/XLPE/LSZH | 4C x 16sqmm | PE-L1-4C16-01 | 15 | 400 | N | 220 | RAW WATER SYSTEM | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-P-38001D | RAW WATER DISTRIBUTION PUMP MOTOR - D | 12.1_RAW WATER&FIRE WATER PUMP HOUSE | L1, L2, L3, PE | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L18 → M0207 → D0203-L24 → M0206 → D0205-L24 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B038-016AC0001 → B038-006AC0010 → B038-006AC0001 → END
B0-MCC-49601 | -P20 | 03 |  | PE-L1-4C25/16-02 | PE-L1-4C25/16-02 | RWP-C-005 | DONE(10/12) | DONE | 1 | 569 | B0-MCC-49601-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 25sqmm + 1C X 16sqmm | PE-L1-4C25/16-02 | 15 | 400 | N | 330 | SERVICE WATER SYSTEM | B0-MCC-49601 | 400V MCC FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-P-36001A | SERVICE WATER DISTRIBUTION PUMP MOTOR - A | 15.1_WATER DISTRIBUTION PUMP STATION | L1, L2, L3, PE | B049-006AT0004 → B049-006AT0003 → B049-006AT0002 → D0204-L17 → M0207 → D0203-L23 → M0206 → D0205-L23 → M0205 → B025-996FT0005 → B025-016FT0029 → B025-016FT0028 → B025-016FT0030 → B025-016FT0031 → B025-016FT0032 → B025-016FT0033 → B025-016FT0034 → B025-996FT0006 → M0202 → D0201-L11 → M0201 → B079-006AC0008 → END
B0-MCC-49602 | -P20 | 03 |  | PE-L1-4C25/16-02 | PE-L1-4C25/16-02 | RWP-C-006 | DONE(10/12) | DONE | 1 | 570 | B0-MCC-49602-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 25sqmm + 1C X 16sqmm | PE-L1-4C25/16-02 | 15 | 400 | N | 340 | SERVICE WATER SYSTEM | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-P-36001B | SERVICE WATER DISTRIBUTION PUMP MOTOR - B | 15.1_WATER DISTRIBUTION PUMP STATION | L1, L2, L3, PE | B049-006AT0008 → B049-006AT0009 → B049-006AT0011 → B049-006AT0003 → B049-006AT0002 → D0204-L18 → M0207 → D0203-L24 → M0206 → D0205-L24 → M0205 → B025-996FT0005 → B025-016FT0029 → B025-016FT0028 → B025-016FT0030 → B025-016FT0031 → B025-016FT0032 → B025-016FT0033 → B025-016FT0034 → B025-996FT0006 → M0202 → D0201-L12 → M0201 → B079-006AC0006 → END
B0-MCC-49601 | -P20 | 04 |  | PE-L1-4C25/16-04 | PE-L1-4C25/16-04 | RWP-C-006-001 | DONE(10/12) | DONE | 1 | 571 | B0-MCC-49601-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 25sqmm + 1C X 16sqmm | PE-L1-4C25/16-04 | 15 | 400 | N | 340 | SERVICE WATER SYSTEM | B0-MCC-49601 | 400V MCC FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-P-36001C | SERVICE WATER DISTRIBUTION PUMP MOTOR - C | 15.1_WATER DISTRIBUTION PUMP STATION | L1, L2, L3, PE | B049-006BT0004 → B049-006BT0003 → B049-006BT0001 → D0204-L17 → M0207 → D0203-L23 → M0206 → D0205-L23 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B025-016ET0030 → B025-016ET0031 → B025-016ET0032 → B025-016ET0033 → B025-016ET0034 → B025-996ET0006 → M0202 → D0201-L11 → M0201 → B079-006AC0004 → END
B0-MCC-49602 | -P20 | 04 |  | PE-L1-4C25/16-04 | PE-L1-4C25/16-04 | RWP-C-006-002 | DONE(10/12) | DONE | 1 | 572 | B0-MCC-49602-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 25sqmm + 1C X 16sqmm | PE-L1-4C25/16-04 | 15 | 400 | N | 350 | SERVICE WATER SYSTEM | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-P-36001D | SERVICE WATER DISTRIBUTION PUMP MOTOR - D | 15.1_WATER DISTRIBUTION PUMP STATION | L1, L2, L3, PE | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L18 → M0207 → D0203-L24 → M0206 → D0205-L24 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B025-016ET0030 → B025-016ET0031 → B025-016ET0032 → B025-016ET0033 → B025-016ET0034 → B025-996ET0006 → M0202 → D0201-L12 → M0201 → B079-006AC0002 → END
B0-MCC-49602 | -P20 | 05 |  | PE-L1-4C25/16-04 | PE-L1-4C25/16-04 | RWP-C-007 |  |  | 1 | 573 | B0-MCC-49602-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 25sqmm + 1C X 16sqmm | PE-L1-4C25/16-04 | 30 | 400 | N | 160 | POTABLE WATER SYSTEM | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-P-37001A | POTABLE WATER DISTRIBUTION PUMP MOTOR - A | 13.4_WATER SUPPLY PUMPING STATION | L1, L2, L3, PE | B049-006AT0008 → B049-006AT0009 → B049-006AT0011 → B049-006AT0003 → B049-006AT0002 → D0204-L16 → M0207 → D0206-L11 → M0208 → D0207-L11 → M0210 → D0209-L11 → M0209 → B038-006BC0009 → END
B0-MCC-49601 | -P20 | 05 |  | PE-L1-4C25/16-04 | PE-L1-4C25/16-04 | RWP-C-008 |  |  | 1 | 574 | B0-MCC-49601-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 25sqmm + 1C X 16sqmm | PE-L1-4C25/16-04 | 30 | 400 | N | 160 | POTABLE WATER SYSTEM | B0-MCC-49601 | 400V MCC FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-P-37001B | POTABLE WATER DISTRIBUTION PUMP MOTOR - B | 13.4_WATER SUPPLY PUMPING STATION | L1, L2, L3, PE | B049-006AT0004 → B049-006AT0003 → B049-006AT0002 → D0204-L16 → M0207 → D0206-L11 → M0208 → D0207-L11 → M0210 → D0209-L11 → M0209 → B038-006BC0007 → END
B0-MCC-49602 | -P20 | 06 |  | PE-L1-4C25/16-04 | PE-L1-4C25/16-04 | RWP-C-008-001 |  |  | 1 | 575 | B0-MCC-49602-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 25sqmm + 1C X 16sqmm | PE-L1-4C25/16-04 | 30 | 400 | N | 170 | POTABLE WATER SYSTEM | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-P-37001C | POTABLE WATER DISTRIBUTION PUMP MOTOR - C | 13.4_WATER SUPPLY PUMPING STATION | L1, L2, L3, PE | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L17 → M0207 → D0206-L12 → M0208 → D0207-L12 → M0210 → D0209-L12 → M0209 → B038-006BC0005 → END
B0-MCC-49601 | -P20 | 06 |  | PE-L1-4C25/16-04 | PE-L1-4C25/16-04 | RWP-C-008-002 |  |  | 1 | 576 | B0-MCC-49601-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 25sqmm + 1C X 16sqmm | PE-L1-4C25/16-04 | 30 | 400 | N | 170 | POTABLE WATER SYSTEM | B0-MCC-49601 | 400V MCC FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-P-37001D | POTABLE WATER DISTRIBUTION PUMP MOTOR - D | 13.4_WATER SUPPLY PUMPING STATION | L1, L2, L3, PE | B049-006BT0004 → B049-006BT0003 → B049-006BT0001 → D0204-L17 → M0207 → D0206-L12 → M0208 → D0207-L12 → M0210 → D0209-L12 → M0209 → B038-006BC0003 → END
B0-MCC-49602 | -P20 | 07 |  | PE-L1-3C4-07 | PE-L1-3C4-07 | RWP-C-009 |  |  | 1 | 577 | B0-MCC-49602-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-07 | 0.06 | 230 | N | 160 | POTABLE WATER SYSTEM | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, N, PE | B0-P-37001A | POTABLE WATER DISTRIBUTION PUMP MOTOR - A_SPACE HEATER | 13.4_WATER SUPPLY PUMPING STATION | L1, N, PE | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L16 → M0207 → D0206-L11 → M0208 → D0207-L11 → M0210 → D0209-L11 → M0209 → B038-007BC0004 → END
B0-MCC-49601 | -P20 | 07 |  | PE-L1-3C4-07 | PE-L1-3C4-07 | RWP-C-010 |  |  | 1 | 578 | B0-MCC-49601-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-07 | 0.06 | 230 | N | 160 | POTABLE WATER SYSTEM | B0-MCC-49601 | 400V MCC FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, N, PE | B0-P-37001B | POTABLE WATER DISTRIBUTION PUMP MOTOR - B_SPACE HEATER | 13.4_WATER SUPPLY PUMPING STATION | L1, N, PE | B049-006AT0004 → B049-006AT0003 → B049-006AT0002 → D0204-L16 → M0207 → D0206-L11 → M0208 → D0207-L11 → M0210 → D0209-L11 → M0209 → B038-007BC0003 → END
B0-MCC-49602 | -P20 | 08 |  | PE-L1-3C4-07 | PE-L1-3C4-07 | RWP-C-011 |  |  | 1 | 579 | B0-MCC-49602-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-07 | 0.06 | 230 | N | 170 | POTABLE WATER SYSTEM | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, N, PE | B0-P-37001C | POTABLE WATER DISTRIBUTION PUMP MOTOR - C_SPACE HEATER | 13.4_WATER SUPPLY PUMPING STATION | L1, N, PE | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L18 → M0207 → D0206-L12 → M0208 → D0207-L12 → M0210 → D0209-L12 → M0209 → B038-007BC0002 → END
B0-MCC-49601 | -P20 | 08 |  | PE-L1-3C4-07 | PE-L1-3C4-07 | RWP-C-012 |  |  | 1 | 580 | B0-MCC-49601-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-07 | 0.06 | 230 | N | 170 | POTABLE WATER SYSTEM | B0-MCC-49601 | 400V MCC FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, N, PE | B0-P-37001D | POTABLE WATER DISTRIBUTION PUMP MOTOR - D_SPACE HEATER | 13.4_WATER SUPPLY PUMPING STATION | L1, N, PE | B049-006AT0004 → B049-006AT0003 → B049-006AT0002 → D0204-L18 → M0207 → D0206-L12 → M0208 → D0207-L12 → M0210 → D0209-L12 → M0209 → B038-007BC0001 → END
B0-MCC-49601 | -P20 | 09 |  | PE-L1-4C4-04 | PE-L1-4C4-04 | RWP-C-013 | DONE(10/12) | DONE | 1 | 581 | B0-MCC-49601-P2009 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-04 | 0.75 | 400 | N | 230 | RAW WATER SYSTEM | B0-MCC-49601 | 400V MCC FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-MOV-38001 | EXTERNAL RAW WATER SUPPLY TO RAW WATER TANK INLET MOV A | 12.1_RAW WATER&FIRE WATER PUMP HOUSE | L1, L2, L3, PE | B049-006AT0004 → B049-006AT0003 → B049-006AT0002 → D0204-L14 → M0207 → D0203-L15 → M0206 → D0205-L15 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0023 → B025-016ET0024 → B025-016ET0025 → B025-016ET0026 → B038-016BC0006 → B038-006BC0016 → END
B0-MCC-49602 | -P20 | 09 |  | PE-L1-4C4-04 | PE-L1-4C4-04 | RWP-C-014 | DONE(10/12) | DONE | 1 | 582 | B0-MCC-49602-P2009 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-04 | 0.75 | 400 | N | 250 | RAW WATER SYSTEM | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-MOV-38002 | EXTERNAL RAW WATER SUPPLY TO RAW WATER TANK INLET MOV B | 12.1_RAW WATER&FIRE WATER PUMP HOUSE | L1, L2, L3, PE | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L15 → M0207 → D0203-L21 → M0206 → D0205-L21 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0023 → B025-016ET0024 → B025-016ET0025 → B025-016ET0026 → B038-016BC0005 → B038-006BC0015 → END
B0-MCC-49601 | -P20 | 10 |  | PE-L1-4C4-04 | PE-L1-4C4-04 | RWP-C-015 | DONE(10/12) | DONE | 1 | 583 | B0-MCC-49601-P2010 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-04 | 0.3 | 400 | N | 220 | RAW WATER SYSTEM | B0-MCC-49601 | 400V MCC FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-MOV-38003 | RAW WATER DISCHARGE TO RAW WATER DISTRIBUTION LINE COMMON MOV A | 12.1_RAW WATER&FIRE WATER PUMP HOUSE | L1, L2, L3, PE | B049-006AT0004 → B049-006AT0003 → B049-006AT0002 → D0204-L14 → M0207 → D0203-L15 → M0206 → D0205-L15 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B038-017AC0501 → B038-006AC0011 → B038-006AC0008 → END
B0-MCC-49602 | -P20 | 10 |  | PE-L1-4C4-04 | PE-L1-4C4-04 | RWP-C-016 | DONE(10/12) | DONE | 1 | 584 | B0-MCC-49602-P2010 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-04 | 0.3 | 400 | N | 230 | RAW WATER SYSTEM | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-MOV-38004 | RAW WATER DISCHARGE TO RAW WATER DISTRIBUTION LINE COMMON MOV B | 12.1_RAW WATER&FIRE WATER PUMP HOUSE | L1, L2, L3, PE | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L15 → M0207 → D0203-L21 → M0206 → D0205-L21 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B038-017AC0501 → B038-006AC0011 → B038-006AC0007 → END
B0-MCC-49601 | -P20 | 11 |  | PE-L1-4C4-04 | PE-L1-4C4-04 | RWP-C-017 | DONE(10/12) | DONE | 1 | 585 | B0-MCC-49601-P2011 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-04 | 0.3 | 400 | N | 220 | RAW WATER SYSTEM | B0-MCC-49601 | 400V MCC FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-MOV-38005 | RAW WATER DISCHARGE TO RAW WATER DISTRIBUTION LINE COMMON MOV C | 12.1_RAW WATER&FIRE WATER PUMP HOUSE | L1, L2, L3, PE | B049-006AT0004 → B049-006AT0003 → B049-006AT0002 → D0204-L14 → M0207 → D0203-L15 → M0206 → D0205-L15 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B038-016AC0001 → B038-006AC0010 → B038-006AC0004 → END
B0-MCC-49602 | -P20 | 11 |  | PE-L1-4C4-04 | PE-L1-4C4-04 | RWP-C-018 | DONE(10/12) | DONE | 1 | 586 | B0-MCC-49602-P2011 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-04 | 0.3 | 400 | N | 220 | RAW WATER SYSTEM | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-MOV-38006 | RAW WATER DISCHARGE TO RAW WATER DISTRIBUTION LINE COMMON MOV D | 12.1_RAW WATER&FIRE WATER PUMP HOUSE | L1, L2, L3, PE | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L15 → M0207 → D0203-L21 → M0206 → D0205-L21 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B038-016AC0001 → B038-006AC0010 → B038-006AC0003 → END
B0-MCC-49601 | -P20 | 12 |  | PE-L1-4C4-06 | PE-L1-4C4-06 | RWP-C-019 |  |  | 1 | 587 | B0-MCC-49601-P2012 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-06 | 0.4 | 400 | N | 140 | SERVICE WATER SYSTEM | B0-MCC-49601 | 400V MCC FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-MOV-36001 | EXTERNAL SERVICE WATER SUPPLY TO SERVICE WATER TANK INLET MOV A | 15.1_WATER DISTRIBUTION PUMP STATION | L1, L2, L3, PE | B049-006AT0004 → B049-006AT0003 → B049-006AT0002 → D0204-L15 → M0207 → D0203-L21 → M0206 → B038-006AC0013 → END
B0-MCC-49602 | -P20 | 12 |  | PE-L1-4C4-05 | PE-L1-4C4-05 | RWP-C-020 | DONE(10/12) | DONE | 1 | 588 | B0-MCC-49602-P2012 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-05 | 0.4 | 400 | N | 130 | SERVICE WATER SYSTEM | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-MOV-36002 | EXTERNAL SERVICE WATER SUPPLY TO SERVICE WATER TANK INLET MOV B | 15.1_WATER DISTRIBUTION PUMP STATION | L1, L2, L3, PE | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L15 → M0207 → D0203-L21 → M0206 → B038-006AC0012 → END
B0-MCC-49601 | -P20 | 13 |  | PE-L1-4C4-05 | PE-L1-4C4-05 | RWP-C-021 | DONE(10/12) | DONE | 1 | 589 | B0-MCC-49601-P2013 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-05 | 0.3 | 400 | N | 340 | SERVICE WATER SYSTEM | B0-MCC-49601 | 400V MCC FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-MOV-36003 | SERVICE WATER DISCHARGE TO SERVICE WATER DISTRIBUTION LINE COMMON MOV A | 15.1_WATER DISTRIBUTION PUMP STATION | L1, L2, L3, PE | B049-006AT0004 → B049-006AT0003 → B049-006AT0002 → D0204-L14 → M0207 → D0203-L15 → M0206 → D0205-L15 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B025-016ET0030 → B025-016ET0031 → B025-016ET0032 → B025-016ET0033 → B025-016ET0034 → B025-996ET0006 → M0202 → D0201-L11 → M0201 → B079-006AC0007 → END
B0-MCC-49602 | -P20 | 13 |  | PE-L1-4C4-05 | PE-L1-4C4-05 | RWP-C-022 | DONE(10/12) | DONE | 1 | 590 | B0-MCC-49602-P2013 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-05 | 0.3 | 400 | N | 350 | SERVICE WATER SYSTEM | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-MOV-36004 | SERVICE WATER DISCHARGE TO SERVICE WATER DISTRIBUTION LINE COMMON MOV B | 15.1_WATER DISTRIBUTION PUMP STATION | L1, L2, L3, PE | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L15 → M0207 → D0203-L21 → M0206 → D0205-L21 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B025-016ET0030 → B025-016ET0031 → B025-016ET0032 → B025-016ET0033 → B025-016ET0034 → B025-996ET0006 → M0202 → D0201-L12 → M0201 → B079-006AC0005 → END
B0-MCC-49601 | -P20 | 14 |  | PE-L1-4C4-05 | PE-L1-4C4-05 | RWP-C-023 | DONE(10/12) | DONE | 1 | 591 | B0-MCC-49601-P2014 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-05 | 0.3 | 400 | N | 340 | SERVICE WATER SYSTEM | B0-MCC-49601 | 400V MCC FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-MOV-36005 | SERVICE WATER DISCHARGE TO SERVICE WATER DISTRIBUTION LINE COMMON MOV C | 15.1_WATER DISTRIBUTION PUMP STATION | L1, L2, L3, PE | B049-006AT0004 → B049-006AT0003 → B049-006AT0002 → D0204-L14 → M0207 → D0203-L15 → M0206 → D0205-L15 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B025-016ET0030 → B025-016ET0031 → B025-016ET0032 → B025-016ET0033 → B025-016ET0034 → B025-996ET0006 → M0202 → D0201-L11 → M0201 → B079-006AC0003 → END
B0-MCC-49602 | -P20 | 14 |  | PE-L1-4C4-05 | PE-L1-4C4-05 | RWP-C-024 | DONE(10/12) | DONE | 1 | 592 | B0-MCC-49602-P2014 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-05 | 0.3 | 400 | N | 350 | SERVICE WATER SYSTEM | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-MOV-36006 | SERVICE WATER DISCHARGE TO SERVICE WATER DISTRIBUTION LINE COMMON MOV D | 15.1_WATER DISTRIBUTION PUMP STATION | L1, L2, L3, PE | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L15 → M0207 → D0203-L21 → M0206 → D0205-L21 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B025-016ET0030 → B025-016ET0031 → B025-016ET0032 → B025-016ET0033 → B025-016ET0034 → B025-996ET0006 → M0202 → D0201-L12 → M0201 → B079-006AC0001 → END
B0-MCC-49601 | -P20 | 15 |  | PE-L1-4C4-05 | PE-L1-4C4-05 | RWP-C-025 |  |  | 1 | 593 | B0-MCC-49601-P2015 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-05 | 0.3 | 400 | N | 170 | POTABLE WATER SYSTEM | B0-MCC-49601 | 400V MCC FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-MOV-37001 | EXTERNAL POTABLE WATER SUPPLY TO POTABLE WATER TANK INLET MOV B | 13.4_WATER SUPPLY PUMPING STATION | L1, L2, L3, PE | B049-006AT0004 → B049-006AT0003 → B049-006AT0002 → D0204-L14 → M0207 → D0206-L12 → M0208 → D0207-L12 → M0210 → D0209-L12 → M0209 → B038-006BC0013 → END
B0-MCC-49602 | -P20 | 15 |  | PE-L1-4C4-06 | PE-L1-4C4-06 | RWP-C-026 |  |  | 1 | 594 | B0-MCC-49602-P2015 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-06 | 0.3 | 400 | N | 160 | POTABLE WATER SYSTEM | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-MOV-37002 | EXTERNAL POTABLE WATER SUPPLY TO POTABLE WATER TANK INLET MOV A | 13.4_WATER SUPPLY PUMPING STATION | L1, L2, L3, PE | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L14 → M0207 → D0206-L11 → M0208 → D0207-L11 → M0210 → D0209-L11 → M0209 → B038-006BC0014 → END
B0-MCC-49602 | -P20 | 16 |  | PE-L1-4C4-06 | PE-L1-4C4-06 | RWP-C-027 |  |  | 1 | 595 | B0-MCC-49602-P2016 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-06 | 0.3 | 400 | N | 170 | POTABLE WATER SYSTEM | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-MOV-37003 | POTABLE WATER DISCHARGE TO POTABLE WATER DISTRIBUTION LINE COMMON MOV A | 13.4_WATER SUPPLY PUMPING STATION | L1, L2, L3, PE | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L14 → M0207 → D0206-L11 → M0208 → D0207-L11 → M0210 → D0209-L11 → M0209 → B038-006BC0008 → END
B0-MCC-49601 | -P20 | 16 |  | PE-L1-4C4-06 | PE-L1-4C4-06 | RWP-C-028 |  |  | 1 | 596 | B0-MCC-49601-P2016 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-06 | 0.3 | 400 | N | 160 | POTABLE WATER SYSTEM | B0-MCC-49601 | 400V MCC FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-MOV-37004 | POTABLE WATER DISCHARGE TO POTABLE WATER DISTRIBUTION LINE COMMON MOV B | 13.4_WATER SUPPLY PUMPING STATION | L1, L2, L3, PE | B049-006AT0004 → B049-006AT0003 → B049-006AT0002 → D0204-L14 → M0207 → D0206-L11 → M0208 → D0207-L11 → M0210 → D0209-L11 → M0209 → B038-006BC0006 → END
B0-MCC-49602 | -P20 | 17 |  | PE-L1-4C4-06 | PE-L1-4C4-06 | RWP-C-029 |  |  | 1 | 597 | B0-MCC-49602-P2017 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-06 | 0.3 | 400 | N | 170 | POTABLE WATER SYSTEM | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-MOV-37005 | POTABLE WATER DISCHARGE TO POTABLE WATER DISTRIBUTION LINE COMMON MOV C | 13.4_WATER SUPPLY PUMPING STATION | L1, L2, L3, PE | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L14 → M0207 → D0206-L11 → M0208 → D0207-L11 → M0210 → D0209-L11 → M0209 → B038-006BC0004 → END
B0-MCC-49601 | -P20 | 17 |  | PE-L1-4C4-06 | PE-L1-4C4-06 | RWP-C-030 |  |  | 1 | 598 | B0-MCC-49601-P2017 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-06 | 0.3 | 400 | N | 160 | POTABLE WATER SYSTEM | B0-MCC-49601 | 400V MCC FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-MOV-37006 | POTABLE WATER DISCHARGE TO POTABLE WATER DISTRIBUTION LINE COMMON MOV D | 13.4_WATER SUPPLY PUMPING STATION | L1, L2, L3, PE | B049-006AT0004 → B049-006AT0003 → B049-006AT0002 → D0204-L14 → M0207 → D0206-L11 → M0208 → D0207-L11 → M0210 → D0209-L11 → M0209 → B038-006BC0002 → END
B0-MCC-49601 | -P20 | 18 |  | PE-L1-4C70/35-03 | PE-L1-4C70/35-03 | DWP-C-001 | DONE(10/12) | DONE | 1 | 599 | B0-MCC-49601-P2018 | 0.6/1kV CU/XLPE/LSZH | 3C x 70sqmm + 1C X 35sqmm | PE-L1-4C70/35-03 | 55 | 400 | N | 330 | DEMINERALIZED WATER SYSTEM | B0-MCC-49601 | 400V MCC FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-P-35001A | DEMI PUMP MOTOR - A | 15.1_WATER DISTRIBUTION PUMP STATION | L1, L2, L3, PE | B049-006AT0004 → B049-006AT0003 → B049-006AT0002 → D0204-L16 → M0207 → D0203-L23 → M0206 → D0205-L22 → M0205 → B025-996FT0005 → B025-016FT0029 → B025-016FT0028 → B025-016FT0030 → B025-016FT0031 → B025-016FT0032 → B025-016FT0033 → B025-016FT0034 → B025-996FT0006 → M0202 → D0201-L11 → M0201 → B079-006AC0012 → END
B0-MCC-49602 | -P20 | 18 |  | PE-L1-4C70/35-04 | PE-L1-4C70/35-04 | DWP-C-002 | DONE(10/12) | DONE | 1 | 600 | B0-MCC-49602-P2018 | 0.6/1kV CU/XLPE/LSZH | 3C x 70sqmm + 1C X 35sqmm | PE-L1-4C70/35-04 | 55 | 400 | N | 340 | DEMINERALIZED WATER SYSTEM | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-P-35001B | DEMI PUMP MOTOR - B | 15.1_WATER DISTRIBUTION PUMP STATION | L1, L2, L3, PE | B049-006AT0008 → B049-006AT0009 → B049-006AT0011 → B049-006AT0003 → B049-006AT0002 → D0204-L17 → M0207 → D0203-L24 → M0206 → D0205-L23 → M0205 → B025-996FT0005 → B025-016FT0029 → B025-016FT0028 → B025-016FT0030 → B025-016FT0031 → B025-016FT0032 → B025-016FT0033 → B025-016FT0034 → B025-996FT0006 → M0202 → D0201-L11 → M0201 → B079-006AC0011 → END
B0-MCC-49601 | -P20 | 19 |  | PE-L1-4C70/35-04 | PE-L1-4C70/35-04 | DWP-C-003 | DONE(10/12) | DONE | 1 | 601 | B0-MCC-49601-P2019 | 0.6/1kV CU/XLPE/LSZH | 3C x 70sqmm + 1C X 35sqmm | PE-L1-4C70/35-04 | 55 | 400 | N | 330 | DEMINERALIZED WATER SYSTEM | B0-MCC-49601 | 400V MCC FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-P-35001C | DEMI PUMP MOTOR - C | 15.1_WATER DISTRIBUTION PUMP STATION | L1, L2, L3, PE | B049-006BT0004 → B049-006BT0003 → B049-006BT0001 → D0204-L16 → M0207 → D0203-L23 → M0206 → D0205-L22 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B025-016ET0030 → B025-016ET0031 → B025-016ET0032 → B025-016ET0033 → B025-016ET0034 → B025-996ET0006 → M0202 → D0201-L12 → M0201 → B079-006AC0010 → END
B0-MCC-49602 | -P20 | 19 |  | PE-L1-4C70/35-05 | PE-L1-4C70/35-05 | DWP-C-003-001 | DONE(10/12) | DONE | 1 | 602 | B0-MCC-49602-P2019 | 0.6/1kV CU/XLPE/LSZH | 3C x 70sqmm + 1C X 35sqmm | PE-L1-4C70/35-05 | 55 | 400 | N | 340 | DEMINERALIZED WATER SYSTEM | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-P-35001D | DEMI PUMP MOTOR - D | 15.1_WATER DISTRIBUTION PUMP STATION | L1, L2, L3, PE | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L17 → M0207 → D0203-L24 → M0206 → D0205-L23 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B025-016ET0030 → B025-016ET0031 → B025-016ET0032 → B025-016ET0033 → B025-016ET0034 → B025-996ET0006 → M0202 → D0201-L12 → M0201 → B079-006AC0009 → END
B0-MCC-49601 | -P20 | 20 |  | PE-L1-3C4-07 | PE-L1-3C4-07 | DWP-C-004 |  |  | 1 | 603 | B0-MCC-49601-P2020 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-07 | 0.12 | 230 | N | 330 | DEMINERALIZED WATER SYSTEM | B0-MCC-49601 | 400V MCC FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, N, PE | B0-P-35001A | DEMI PUMP - A_SPACE HEATER | 15.1_WATER DISTRIBUTION PUMP STATION | L1, N, PE | B049-006AT0004 → B049-006AT0003 → B049-006AT0002 → D0204-L16 → M0207 → D0203-L23 → M0206 → D0205-L22 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B025-016ET0030 → B025-016ET0031 → B025-016ET0032 → B025-016ET0033 → B025-016ET0034 → B025-996ET0006 → M0202 → D0201-L11 → M0201 → B079-007AC0004 → END
B0-MCC-49602 | -P20 | 20 |  | PE-L1-3C4-08 | PE-L1-3C4-08 | DWP-C-005 | DONE(10/12) | DONE | 1 | 604 | B0-MCC-49602-P2020 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-08 | 0.12 | 230 | N | 340 | DEMINERALIZED WATER SYSTEM | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, N, PE | B0-P-35001B | DEMI PUMP - B_SPACE HEATER | 15.1_WATER DISTRIBUTION PUMP STATION | L1, N, PE | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L17 → M0207 → D0203-L23 → M0206 → D0205-L23 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B025-016ET0030 → B025-016ET0031 → B025-016ET0032 → B025-016ET0033 → B025-016ET0034 → B025-996ET0006 → M0202 → D0201-L12 → M0201 → B079-007AC0003 → END
B0-MCC-49601 | -P20 | 21 |  | PE-L1-3C4-08 | PE-L1-3C4-08 | DWP-C-006 | DONE(10/12) | DONE | 1 | 605 | B0-MCC-49601-P2021 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-08 | 0.12 | 230 | N | 330 | DEMINERALIZED WATER SYSTEM | B0-MCC-49601 | 400V MCC FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, N, PE | B0-P-35001C | DEMI PUMP - C_SPACE HEATER | 15.1_WATER DISTRIBUTION PUMP STATION | L1, N, PE | B049-006AT0004 → B049-006AT0003 → B049-006AT0002 → D0204-L16 → M0207 → D0203-L23 → M0206 → D0205-L22 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B025-016ET0030 → B025-016ET0031 → B025-016ET0032 → B025-016ET0033 → B025-016ET0034 → B025-996ET0006 → M0202 → D0201-L11 → M0201 → B079-007AC0002 → END
B0-MCC-49602 | -P20 | 21 |  | PE-L1-3C4-06 | PE-L1-3C4-06 | DWP-C-006-001 | DONE(10/12) | DONE | 1 | 606 | B0-MCC-49602-P2021 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-06 | 0.12 | 230 | N | 340 | DEMINERALIZED WATER SYSTEM | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, N, PE | B0-P-35001D | DEMI PUMP - D_SPACE HEATER | 15.1_WATER DISTRIBUTION PUMP STATION | L1, N, PE | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L17 → M0207 → D0203-L23 → M0206 → D0205-L23 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B025-016ET0030 → B025-016ET0031 → B025-016ET0032 → B025-016ET0033 → B025-016ET0034 → B025-996ET0006 → M0202 → D0201-L12 → M0201 → B079-007AC0001 → END
B1-SWG-64303 | -P10 | 01 |  | PE-M1-3C120-04 | PE-M1-3C120-04 | CEP-B1-001 |  |  | 1 | 607 | B1-SWG-64303-P1001 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-04 | 350 | 10000 | N | 510 | CONDENSATE SYSTEM | B1-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B1-M-29001 | MOTOR FOR CONDENSATE EXTRACTION PUMP #A | 16_CEP BUILDING W/ACC LER | U1,V1,W1 | B164-013BT0290 → B164-013BT0054 → B164-013BT0053 → B164-013BT0052 → B164-013BT0228 → B164-013BT0227 → B164-013BT0226 → B164-993BT0019 → M0501 → D0503-M11 → M0502 → D0504-M11 → M0503 → D0501-M11 → M0328 → D0324-M11 → M0329 → B114-993CT0021 → B114-013CT0020 → B114-013CT0019 → B114-013CT0018 → B114-013CT0017 → B114-013CT0016 → B114-013CT0015 → B114-013CT0014 → B114-013CT0013 → B114-013CT0024 → B025-013CT0126 → B025-013CT0127 → B025-013CT0128 → B025-993CT0014 → M0105 → D0110-M13 → M0112 → D0111-M11 → M0113 → D0113-M11 → B169-003AT0045 → B169-003AT0003 → B169-003AT0002 → B016-003AC0003 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B1-SWG-64303 | -P20 | 01 |  | PE-L1-3C4-08 | PE-L1-3C4-08 | CEP-B1-002 |  |  | 1 | 608 | B1-SWG-64303-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-08 | 0.25 | 230 | N | 520 | CONDENSATE SYSTEM | B1-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-M-29001 | MOTOR SPACE HEATER FOR CONDENSATE EXTRACTION PUMP #A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B064-016AT0068 → B064-016AT0067 → B064-016AT0066 → B064-016AT0065 → B064-016AT0064 → B064-016AT0063 → B064-016AT0214 → B064-016AT0213 → B064-016AT0032 → B064-996AT0120 → M0501 → D0503-L41 → M0502 → D0504-L41 → M0503 → D0501-L41 → M0328 → D0324-L41 → M0329 → B114-996BT0046 → B114-016BT0045 → B114-016BT0044 → B114-016BT0043 → B114-016BT0042 → B114-016BT0041 → B114-016BT0040 → B114-016BT0039 → B114-016BT0038 → B215-016BT0023 → B025-016BT0123 → B025-016BT0124 → B025-016BT0125 → B025-996BT0013 → M0105 → D0110-L24 → M0112 → D0111-L24 → M0113 → D0113-L21 → B169-006AT0044 → B169-006AT0010 → B169-006AT0009 → B169-006AT0008 → B016-007AC0009 → END
B1-DB-69601 | -P20 | 13 |  | PE-L1-3C4-08 | PE-L1-3C4-08 | CEP-B1-003 |  |  | 1 | 609 | B1-DB-69601-P2013 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-08 | 0.03 | 230 | N | 40 | CONDENSATE SYSTEM | B1-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-M-29001 | REVERSE ROTATION SENSOR FOR CEP #A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0016 → B169-006AT0053 → B169-006AT0008 → B016-007AC0008 → END
B1-SWG-64304 | -P10 | 01 |  | PE-M1-3C120-05 | PE-M1-3C120-05 | CEP-B1-004 |  |  | 1 | 610 | B1-SWG-64304-P1001 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-05 | 350 | 10000 | N | 510 | CONDENSATE SYSTEM | B1-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B1-M-29002 | MOTOR FOR CONDENSATE EXTRACTION PUMP #B | 16_CEP BUILDING W/ACC LER | U1,V1,W1 | B164-013BT0291 → B164-013BT0290 → B164-013BT0054 → B164-013BT0053 → B164-013BT0052 → B164-013BT0228 → B164-013BT0227 → B164-013BT0226 → B164-993BT0019 → M0501 → D0503-M12 → M0502 → D0504-M12 → M0503 → D0501-M12 → M0328 → D0324-M12 → M0329 → B114-993CT0021 → B114-013CT0020 → B114-013CT0019 → B114-013CT0018 → B114-013CT0017 → B114-013CT0016 → B114-013CT0015 → B114-013CT0014 → B114-013CT0013 → B114-013CT0024 → B025-013CT0126 → B025-013CT0127 → B025-013CT0128 → B025-993CT0014 → M0105 → D0110-M14 → M0112 → D0111-M12 → M0113 → D0113-M12 → B169-003AT0045 → B169-003AT0003 → B169-003AT0002 → B016-003AC0002 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B1-SWG-64304 | -P20 | 01 |  | PE-L1-3C4-08 | PE-L1-3C4-08 | CEP-B1-005 |  |  | 1 | 611 | B1-SWG-64304-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-08 | 0.25 | 230 | N | 520 | CONDENSATE SYSTEM | B1-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-M-29002 | MOTOR SPACE HEATER FOR CONDENSATE EXTRACTION PUMP #B | 16_CEP BUILDING W/ACC LER | L1, N, PE | B064-016AT0079 → B064-016AT0078 → B064-016AT0077 → B064-016AT0076 → B064-016AT0075 → B064-016AT0074 → B064-016AT0073 → B064-016AT0215 → B064-016AT0214 → B064-016AT0213 → B064-016AT0032 → B064-996AT0120 → M0501 → D0503-L36 → M0502 → D0504-L36 → M0503 → D0501-L36 → M0328 → D0324-L36 → M0329 → B114-996BT0046 → B114-016BT0045 → B114-016BT0044 → B114-016BT0043 → B114-016BT0042 → B114-016BT0041 → B114-016BT0040 → B114-016BT0039 → B114-016BT0038 → B215-016BT0023 → B025-016BT0123 → B025-016BT0124 → B025-016BT0125 → B025-996BT0013 → M0105 → D0110-L25 → M0112 → D0111-L25 → M0113 → D0113-L22 → B169-006AT0044 → B169-006AT0010 → B169-006AT0009 → B169-006AT0008 → B016-007AC0007 → END
B1-DB-69603 | -P20 | 13 | 재배정 | PE-L1-3C4-06 | PE-L1-3C4-14 | CEP-B1-006 |  |  | 1 | 612 | B1-DB-69603-P2013 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-14 | 0.03 | 230 | N | 20 | CONDENSATE SYSTEM | B1-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-M-29002 | REVERSE ROTATION SENSOR FOR CEP #B | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0009 → B016-007AC0006 → END
B1-SWG-64303 | -P10 | 02 |  | PE-M1-3C120-06 | PE-M1-3C120-06 | CEP-B1-007 |  |  | 1 | 613 | B1-SWG-64303-P1002 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-06 | 350 | 10000 | N | 490 | CONDENSATE SYSTEM | B1-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B1-M-29003 | MOTOR FOR CONDENSATE EXTRACTION PUMP #C | 16_CEP BUILDING W/ACC LER | U1,V1,W1 | B164-013AT0058 → B164-013AT0275 → B164-013AT0052 → B164-013AT0228 → B164-013AT0227 → B164-013AT0226 → B164-993AT0019 → M0501 → D0503-M13 → M0502 → D0504-M13 → M0503 → D0501-M13 → M0328 → D0324-M13 → M0329 → B114-993DT0046 → B114-013DT0045 → B114-013DT0019 → B114-013DT0018 → B114-013DT0017 → B114-013DT0016 → B114-013DT0015 → B114-013DT0014 → B114-013DT0013 → B114-013DT0024 → B025-013DT0126 → B025-013DT0127 → B025-013DT0128 → B025-993DT0014 → M0105 → D0110-M15 → M0112 → D0111-M13 → M0113 → D0113-M13 → B016-003AC0001 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B1-SWG-64303 | -P20 | 02 |  | PE-L1-3C4-09 | PE-L1-3C4-09 | CEP-B1-008 |  |  | 1 | 614 | B1-SWG-64303-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-09 | 0.25 | 230 | N | 520 | CONDENSATE SYSTEM | B1-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-M-29003 | MOTOR SPACE HEATER FOR CONDENSATE EXTRACTION PUMP #C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B064-016AT0068 → B064-016AT0067 → B064-016AT0066 → B064-016AT0065 → B064-016AT0064 → B064-016AT0063 → B064-016AT0214 → B064-016AT0213 → B064-016AT0032 → B064-996AT0120 → M0501 → D0503-L42 → M0502 → D0504-L42 → M0503 → D0501-L42 → M0328 → D0324-L42 → M0329 → B114-996BT0046 → B114-016BT0045 → B114-016BT0044 → B114-016BT0043 → B114-016BT0042 → B114-016BT0041 → B114-016BT0040 → B114-016BT0039 → B114-016BT0038 → B215-016BT0023 → B025-016BT0123 → B025-016BT0124 → B025-016BT0125 → B025-996BT0013 → M0105 → D0110-L31 → M0112 → D0111-L31 → M0113 → D0113-L23 → B169-006AT0044 → B169-006AT0010 → B169-006AT0009 → B016-007AC0005 → END
B1-DB-69601 | -P20 | 14 | 재배정 | PE-L1-3C4-06 | PE-L1-3C4-14 | CEP-B1-009 |  |  | 1 | 615 | B1-DB-69601-P2014 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-14 | 0.03 | 230 | N | 40 | CONDENSATE SYSTEM | B1-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-M-29003 | REVERSE ROTATION SENSOR FOR CEP #C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0016 → B169-006AT0053 → B169-006AT0009 → B016-007AC0004 → END
B2-SWG-64303 | -P10 | 01 |  | PE-M1-3C120-20 | PE-M1-3C120-20 | CEP-B2-001 |  |  | 1 | 616 | B2-SWG-64303-P1001 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-20 | 350 | 10000 | N | 490 | CONDENSATE SYSTEM | B2-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1,V1,W1 | B2-M-29001 | MOTOR FOR CONDENSATE EXTRACTION PUMP #A | 16_CEP BUILDING W/ACC LER | U1,V1,W1 | B264-013LT0005 → B264-013LT0215 → B264-993LT0004 → M0405 → D0421-M11 → M0406 → D0301-M17 → M0301 → B215-993AT0001 → B215-013AT0002 → B215-013AT0003 → B215-013AT0004 → B215-013AT0005 → B215-013AT0006 → B215-013AT0007 → B215-013AT0008 → B215-013AT0009 → B215-013AT0010 → B215-013AT0011 → B215-013AT0012 → B215-013AT0023 → B025-013AT0123 → B025-013AT0124 → B025-013AT0125 → B025-993AT0013 → M0105 → D0103-M14 → M0106 → D0104-M14 → M0107 → D0106-M13 → B169-003AT0049 → B169-003AT0024 → B169-003AT0023 → B016-003BC0003 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B2-SWG-64303 | -P20 | 01 |  | PE-L1-3C4-05 | PE-L1-3C4-05 | CEP-B2-002 |  |  | 1 | 617 | B2-SWG-64303-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-05 | 0.25 | 230 | N | 510 | CONDENSATE SYSTEM | B2-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-M-29001 | MOTOR SPACE HEATER FOR CONDENSATE EXTRACTION PUMP #A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B264-016AT0011 → B264-016AT0233 → B264-016AT0015 → B264-996AT0011 → M0405 → D0421-L31 → M0406 → D0301-L37 → M0301 → B215-996BT0001 → B215-016BT0002 → B215-016BT0003 → B215-016BT0004 → B215-016BT0005 → B215-016BT0031 → B215-016BT0032 → B215-016BT0033 → B215-016BT0034 → B215-016BT0035 → B215-016BT0036 → B215-016BT0037 → B215-016BT0023 → B025-016BT0123 → B025-016BT0124 → B025-016BT0125 → B025-996BT0013 → M0105 → D0103-L24 → M0106 → D0104-L24 → M0107 → D0106-L23 → B169-006AT0049 → B169-006AT0017 → B169-006AT0016 → B169-006AT0015 → B016-007BC0009 → END
B2-DB-69601 | -P20 | 13 |  | PE-L1-3C4-05 | PE-L1-3C4-05 | CEP-B2-003 |  |  | 1 | 618 | B2-DB-69601-P2013 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-05 | 0.03 | 230 | N | 70 | CONDENSATE SYSTEM | B2-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-M-29001 | REVERSE ROTATION SENSOR FOR CEP #A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0020 → B169-006AT0019 → B169-006AT0018 → B169-006AT0017 → B169-006AT0016 → B169-006AT0015 → B016-007BC0008 → END
B2-SWG-64304 | -P10 | 01 |  | PE-M1-3C120-21 | PE-M1-3C120-21 | CEP-B2-004 |  |  | 1 | 619 | B2-SWG-64304-P1001 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-21 | 350 | 10000 | N | 490 | CONDENSATE SYSTEM | B2-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1,V1,W1 | B2-M-29002 | MOTOR FOR CONDENSATE EXTRACTION PUMP #B | 16_CEP BUILDING W/ACC LER | U1,V1,W1 | B264-013NT0020 → B264-013NT0216 → B264-993NT0005 → M0405 → D0421-M12 → M0406 → D0301-M16 → M0301 → B215-993AT0001 → B215-013AT0002 → B215-013AT0003 → B215-013AT0004 → B215-013AT0005 → B215-013AT0006 → B215-013AT0007 → B215-013AT0008 → B215-013AT0009 → B215-013AT0010 → B215-013AT0011 → B215-013AT0012 → B215-013AT0023 → B025-013AT0123 → B025-013AT0124 → B025-013AT0125 → B025-993AT0013 → M0105 → D0103-M15 → M0106 → D0104-M15 → M0107 → D0106-M12 → B169-003AT0049 → B169-003AT0024 → B169-003AT0023 → B016-003BC0002 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B2-SWG-64304 | -P20 | 01 |  | PE-L1-3C4-05 | PE-L1-3C4-05 | CEP-B2-005 |  |  | 1 | 620 | B2-SWG-64304-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-05 | 0.25 | 230 | N | 500 | CONDENSATE SYSTEM | B2-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-M-29002 | MOTOR SPACE HEATER FOR CONDENSATE EXTRACTION PUMP #B | 16_CEP BUILDING W/ACC LER | L1, N, PE | B264-016BT0015 → B264-996CT0009 → M0405 → D0421-L32 → M0406 → D0301-L36 → M0301 → B215-996BT0001 → B215-016BT0002 → B215-016BT0003 → B215-016BT0004 → B215-016BT0005 → B215-016BT0031 → B215-016BT0032 → B215-016BT0033 → B215-016BT0034 → B215-016BT0035 → B215-016BT0036 → B215-016BT0037 → B215-016BT0023 → B025-016BT0123 → B025-016BT0124 → B025-016BT0125 → B025-996BT0013 → M0105 → D0103-L25 → M0106 → D0104-L25 → M0107 → D0106-L24 → B169-006AT0049 → B169-006AT0017 → B169-006AT0016 → B169-006AT0015 → B016-007BC0007 → END
B2-DB-69603 | -P20 | 13 |  | PE-L1-3C4-05 | PE-L1-3C4-05 | CEP-B2-006 |  |  | 1 | 621 | B2-DB-69603-P2013 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-05 | 0.03 | 230 | N | 40 | CONDENSATE SYSTEM | B2-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-M-29002 | REVERSE ROTATION SENSOR FOR CEP #B | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0013 → B169-006AT0033 → B169-006AT0020 → B016-007BC0006 → END
B2-SWG-64303 | -P10 | 02 |  | PE-M1-3C120-22 | PE-M1-3C120-22 | CEP-B2-007 |  |  | 1 | 622 | B2-SWG-64303-P1002 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-22 | 350 | 10000 | N | 480 | CONDENSATE SYSTEM | B2-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1,V1,W1 | B2-M-29003 | MOTOR FOR CONDENSATE EXTRACTION PUMP #C | 16_CEP BUILDING W/ACC LER | U1,V1,W1 | B264-013MT0005 → B264-013MT0218 → B264-993MT0006 → M0405 → D0421-M13 → M0406 → D0301-M15 → M0301 → B215-993BT0001 → B215-013BT0002 → B215-013BT0003 → B215-013BT0004 → B215-013BT0005 → B215-013BT0006 → B215-013BT0007 → B215-013BT0008 → B215-013BT0009 → B215-013BT0010 → B215-013BT0011 → B215-013BT0012 → B215-013BT0023 → B025-013BT0123 → B025-013BT0124 → B025-013BT0125 → B025-993BT0013 → M0105 → D0103-M21 → M0106 → D0104-M21 → M0107 → D0106-M11 → B016-003BC0001 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B2-SWG-64303 | -P20 | 02 |  | PE-L1-3C4-05 | PE-L1-3C4-05 | CEP-B2-008 |  |  | 1 | 623 | B2-SWG-64303-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-05 | 0.25 | 230 | N | 500 | CONDENSATE SYSTEM | B2-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-M-29003 | MOTOR SPACE HEATER FOR CONDENSATE EXTRACTION PUMP #C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B264-016AT0011 → B264-016AT0233 → B264-016AT0015 → B264-996AT0011 → M0405 → D0421-L33 → M0406 → D0301-L35 → M0301 → B215-996BT0001 → B215-016BT0002 → B215-016BT0003 → B215-016BT0004 → B215-016BT0005 → B215-016BT0031 → B215-016BT0032 → B215-016BT0033 → B215-016BT0034 → B215-016BT0035 → B215-016BT0036 → B215-016BT0037 → B215-016BT0023 → B025-016BT0123 → B025-016BT0124 → B025-016BT0125 → B025-996BT0013 → M0105 → D0103-L31 → M0106 → D0104-L31 → M0107 → D0106-L31 → B169-006AT0049 → B169-006AT0017 → B016-007BC0005 → END
B2-DB-69601 | -P20 | 14 | 재배정 | PE-L1-3C4-05 | PE-L1-3C4-17 | CEP-B2-009 |  |  | 1 | 624 | B2-DB-69601-P2014 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-17 | 0.03 | 230 | N | 50 | CONDENSATE SYSTEM | B2-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-M-29003 | REVERSE ROTATION SENSOR FOR CEP #C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0020 → B169-006AT0019 → B169-006AT0018 → B169-006AT0017 → B016-007BC0004 → END
B1-MCC-59602 | -P20 | 16 |  | PE-L1-4C4-06 | PE-L1-4C4-06 | FTD-B1-001 |  |  | 1 | 625 | B1-MCC-59602-P2016 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-06 | 7.5 | 400 | N | 140 | ATMOSPHERIC FLASH TANK SYSTEM | B1-MCC-59602 | 400V MCC FOR ST #1 FOR BLOCK #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-P-33001A | ATMOSPHERIC FLASH TANK DRAIN PUMP MOTER - A FOR BLOCK #1 | 1.1_MAIN BUILDING COMPLEX / STG AREA PIT | L1, L2, L3, PE | B159-006AT0006 → B159-006AT0005 → B159-006AT0014 → B159-006AT0025 → D0326-L15 → M0316 → B113-997AT0010 → B113-017AT0009 → B113-017AT0003 → B113-017AT0004 → B113-017AT0005 → B113-017AT0006 → B113-017AT0007 → B113-016BC0037 → B113-006AC0006 → B113-016AC0012 → B113-016AC0010 → B113-016AC0008 → END
B1-MCC-59601 | -P20 | 15 |  | PE-L1-4C4-06 | PE-L1-4C4-06 | FTD-B1-002 |  |  | 1 | 626 | B1-MCC-59601-P2015 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-06 | 7.5 | 400 | N | 140 | ATMOSPHERIC FLASH TANK SYSTEM | B1-MCC-59601 | 400V MCC FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-P-33001B | ATMOSPHERIC FLASH TANK DRAIN PUMP MOTER - B FOR BLOCK #1 | 1.1_MAIN BUILDING COMPLEX / STG AREA PIT | L1, L2, L3, PE | B159-006BT0003 → B159-006BT0001 → D0326-L21 → M0316 → B113-996AT0012 → B113-016AT0011 → B113-016AT0003 → B113-016AT0004 → B113-016AT0005 → B113-016AT0006 → B113-016AT0007 → B113-016BC0036 → B113-006AC0005 → B113-016AC0011 → B113-016AC0009 → B113-016AC0007 → END
B2-MCC-59601 | -P20 | 15 | From변경 | PE-L1-4C4-18 | PE-L1-4C4-18 | FTD-B2-001 | B2-MCC-59601-P2015 |  | 1 | 627 | B2-MCC-59602-P2016 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-18 | 7.5 | 400 | N | 125 | ATMOSPHERIC FLASH TANK SYSTEM | B2-MCC-59602 | 400V MCC FOR ST #2 FOR BLOCK #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-P-33001A | ATMOSPHERIC FLASH TANK DRAIN PUMP MOTER - A FOR BLOCK #2 | 1.1_MAIN BUILDING COMPLEX / STG AREA PIT | L1, L2, L3, PE | B259-006BT0006 → B259-006BT0019 → B259-006BT0001 → D0325-L15 → M0313 → B213-997AT0010 → B213-017AT0009 → B213-017AT0003 → B213-017AT0004 → B213-017AT0005 → B213-017AT0006 → B213-017AT0007 → B213-016BC0037 → B213-016AC0012 → B213-016AC0010 → B213-016AC0008 → END
B2-MCC-59602 | -P20 | 16 | From변경 | PE-L1-4C4-18 | PE-L1-4C4-18 | FTD-B2-002 | B2-MCC-59602-P2016 |  | 1 | 628 | B2-MCC-59601-P2029 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-18 | 7.5 | 400 | N | 125 | ATMOSPHERIC FLASH TANK SYSTEM | B2-MCC-59601 | 400V MCC FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-P-33001B | ATMOSPHERIC FLASH TANK DRAIN PUMP MOTOR - B FOR BLOCK #2 | 1.1_MAIN BUILDING COMPLEX / STG AREA PIT | L1, L2, L3, PE | B259-006AT0003 → B259-006AT0025 → D0325-L21 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0003 → B213-016AT0004 → B213-016AT0005 → B213-016AT0006 → B213-016AT0007 → B213-016BC0036 → B213-016AC0011 → B213-016AC0009 → B213-016AC0007 → END
B1-MCC-59602 | -P20 | 17 |  | PE-L1-4C4-06 | PE-L1-4C4-06 | FTD-B1-003 |  |  | 1 | 629 | B1-MCC-59602-P2017 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-06 | 0.2 | 400 | N | 140 | ATMOSPHERIC FLASH TANK SYSTEM | B1-MCC-59602 | 400V MCC FOR ST #1 FOR BLOCK #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-MOV-33001 | DRAIN QUENCHING MOV - FOR BLOCK #1 | 1.1_MAIN BUILDING COMPLEX / STG AREA PIT | L1, L2, L3, PE | B159-006AT0006 → B159-006AT0005 → B159-006AT0014 → B159-006AT0025 → D0326-L12 → M0316 → B113-996AT0012 → B113-016AT0011 → B113-016AT0003 → B113-016AT0004 → B113-016AT0005 → B113-016AT0006 → B113-016AT0007 → B113-016BC0036 → B113-006AC0006 → B113-016AC0017 → END
B2-MCC-59601 | -P20 | 16 |  | PE-L1-4C4-26 | PE-L1-4C4-26 | FTD-B2-003 |  |  | 1 | 630 | B2-MCC-59601-P2016 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-26 | 0.2 | 400 | N | 130 | ATMOSPHERIC FLASH TANK SYSTEM | B2-MCC-59601 | 400V MCC FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-MOV-33001 | DRAIN QUENCHING MOV - FOR BLOCK #2 | 1.1_MAIN BUILDING COMPLEX / STG AREA PIT | L1, L2, L3, PE | B259-006AT0003 → B259-006AT0025 → D0325-L12 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0003 → B213-016AT0004 → B213-016AT0005 → B213-016AT0006 → B213-016AT0007 → B213-016BC0036 → B213-006AC0006 → B213-016AC0017 → END
B0-MCC-49601 | -P20 | 22 |  | PE-L1-4C50/25-01 | PE-L1-4C50/25-01 | FOP-C-001 |  |  | 1 | 631 | B0-MCC-49601-P2022 | 0.6/1kV CU/XLPE/LSZH | 3C x 50sqmm + 1C X 25sqmm | PE-L1-4C50/25-01 | 30 | 400 | N | 380 | FUEL OIL SYSTEM | B0-MCC-49601 | 400V MCC FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-P-46001A | FUEL OIL UNLOADING PUMP MOTOR - A | 21_DIESEL OIL PUMP STATION | L1, L2, L3, PE | B049-006AT0004 → B049-006AT0003 → B049-006AT0002 → D0204-L14 → M0207 → D0203-L15 → M0206 → D0205-L15 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B025-016ET0020 → B025-016ET0019 → B025-016ET0018 → B025-016ET0017 → B025-016ET0016 → B025-996ET0003 → M0103 → B070-006AC0007 → END
B0-MCC-49602 | -P20 | 22 |  | PE-L1-4C50/25-01 | PE-L1-4C50/25-01 | FOP-C-002 |  |  | 1 | 632 | B0-MCC-49602-P2022 | 0.6/1kV CU/XLPE/LSZH | 3C x 50sqmm + 1C X 25sqmm | PE-L1-4C50/25-01 | 30 | 400 | N | 390 | FUEL OIL SYSTEM | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-P-46001B | FUEL OIL UNLOADING PUMP MOTOR - B | 21_DIESEL OIL PUMP STATION | L1, L2, L3, PE | B049-006AT0008 → B049-006AT0009 → B049-006AT0011 → B049-006AT0003 → B049-006AT0002 → D0204-L15 → M0207 → D0203-L21 → M0206 → D0205-L21 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B025-016ET0020 → B025-016ET0019 → B025-016ET0018 → B025-016ET0017 → B025-016ET0016 → B025-996ET0003 → M0103 → B070-006AC0008 → END
B0-MCC-49601 | -P20 | 23 |  | PE-L1-4C50/25-02 | PE-L1-4C50/25-02 | FOP-C-003 |  |  | 1 | 633 | B0-MCC-49601-P2023 | 0.6/1kV CU/XLPE/LSZH | 3C x 50sqmm + 1C X 25sqmm | PE-L1-4C50/25-02 | 30 | 400 | N | 390 | FUEL OIL SYSTEM | B0-MCC-49601 | 400V MCC FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-P-46001C | FUEL OIL UNLOADING PUMP MOTOR - C | 21_DIESEL OIL PUMP STATION | L1, L2, L3, PE | B049-006BT0004 → B049-006BT0003 → B049-006BT0001 → D0204-L18 → M0207 → D0203-L15 → M0206 → D0205-L15 → M0205 → B025-996FT0005 → B025-016FT0029 → B025-016FT0028 → B025-016FT0020 → B025-016FT0019 → B025-016FT0018 → B025-016FT0017 → B025-016FT0016 → B025-996FT0003 → M0103 → B070-006AC0009 → END
B0-MCC-49601 | -P20 | 24 |  | PE-L1-3C4-09 | PE-L1-3C4-09 | FOP-C-004 |  |  | 1 | 634 | B0-MCC-49601-P2024 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-09 | 0.06 | 230 | N | 380 | FUEL OIL SYSTEM | B0-MCC-49601 | 400V MCC FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, N, PE | B0-P-46001A | FUEL OIL UNLOADING PUMP MOTOR - A_SPACE HEATER | 21_DIESEL OIL PUMP STATION | L1, N, PE | B049-006AT0004 → B049-006AT0003 → B049-006AT0002 → D0204-L18 → M0207 → D0203-L21 → M0206 → D0205-L15 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B025-016ET0020 → B025-016ET0019 → B025-016ET0018 → B025-016ET0017 → B025-016ET0016 → B025-996ET0003 → M0103 → B070-007AC0003 → END
B0-MCC-49602 | -P20 | 23 |  | PE-L1-3C4-09 | PE-L1-3C4-09 | FOP-C-005 |  |  | 1 | 635 | B0-MCC-49602-P2023 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-09 | 0.06 | 230 | N | 390 | FUEL OIL SYSTEM | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, N, PE | B0-P-46001B | FUEL OIL UNLOADING PUMP MOTOR - B_SPACE HEATER | 21_DIESEL OIL PUMP STATION | L1, N, PE | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L15 → M0207 → D0203-L22 → M0206 → D0205-L21 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B025-016ET0020 → B025-016ET0019 → B025-016ET0018 → B025-016ET0017 → B025-016ET0016 → B025-996ET0003 → M0103 → B070-007AC0004 → END
B0-MCC-49601 | -P20 | 25 |  | PE-L1-3C4-09 | PE-L1-3C4-09 | FOP-C-006 |  |  | 1 | 636 | B0-MCC-49601-P2025 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-09 | 0.06 | 230 | N | 390 | FUEL OIL SYSTEM | B0-MCC-49601 | 400V MCC FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, N, PE | B0-P-46001C | FUEL OIL UNLOADING PUMP MOTOR - C_SPACE HEATER | 21_DIESEL OIL PUMP STATION | L1, N, PE | B049-006AT0004 → B049-006AT0003 → B049-006AT0002 → D0204-L18 → M0207 → D0203-L22 → M0206 → D0205-L15 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B025-016ET0020 → B025-016ET0019 → B025-016ET0018 → B025-016ET0017 → B025-016ET0016 → B025-996ET0003 → M0103 → B070-007AC0005 → END
B0-SWG-49602 | -P20 | 01 | From변경 | PE-L1-4C95/50-15 | PE-L1-4C95/50-15 | FOP-C-007 | B0-SWG-49602-P2001 |  | 1 | 637 | B0-SWG-49601-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-15 | 132 | 400 | N | 370 | FUEL OIL SYSTEM | B0-SWG-49601 | 400V SWITCHGEAR FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-P-46002A | FUEL OIL TRANSFER PUMP MOTOR - A | 21_DIESEL OIL PUMP STATION | L1, L2, L3, PE | B049-006AT0003 → B049-006AT0002 → D0204-L15 → M0207 → D0203-L22 → M0206 → D0205-L22 → M0205 → B025-996FT0005 → B025-016FT0029 → B025-016FT0028 → B025-016FT0020 → B025-016FT0019 → B025-016FT0018 → B025-016FT0017 → B025-016FT0016 → B025-996FT0003 → M0103 → B070-006AC0002 → END
B0-SWG-49602 | -P20 | 02 | From변경 | PE-L1-4C95/50-08 | PE-L1-4C95/50-08 |  | B0-SWG-49602-P2002 |  | 1 | 638 | B0-SWG-49601-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-08 | 132 | 400 | N | 370 | FUEL OIL SYSTEM | B0-SWG-49601 | 400V SWITCHGEAR FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-P-46002A | FUEL OIL TRANSFER PUMP MOTOR - A | 21_DIESEL OIL PUMP STATION | L1, L2, L3, PE | B049-006AT0003 → B049-006AT0002 → D0204-L15 → M0207 → D0203-L22 → M0206 → D0205-L22 → M0205 → B025-996FT0005 → B025-016FT0029 → B025-016FT0028 → B025-016FT0020 → B025-016FT0019 → B025-016FT0018 → B025-016FT0017 → B025-016FT0016 → B025-996FT0003 → M0103 → B070-006AC0002 → END
B0-SWG-49601 | -P20 | 01 | From변경 | PE-L1-4C95/50-16 | PE-L1-4C95/50-16 | FOP-C-008 | B0-SWG-49601-P2001 |  | 1 | 639 | B0-SWG-49602-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-16 | 132 | 400 | N | 375 | FUEL OIL SYSTEM | B0-SWG-49602 | 400V SWITCHGEAR FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-P-46002B | FUEL OIL TRANSFER PUMP MOTOR - B | 21_DIESEL OIL PUMP STATION | L1, L2, L3, PE | B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L18 → M0207 → D0203-L24 → M0206 → D0205-L24 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B025-016ET0020 → B025-016ET0019 → B025-016ET0018 → B025-016ET0017 → B025-016ET0016 → B025-996ET0003 → M0103 → B070-006AC0005 → END
B0-SWG-49601 | -P20 | 02 | From변경 | PE-L1-4C95/50-16 | PE-L1-4C95/50-16 |  | B0-SWG-49601-P2002 |  | 1 | 640 | B0-SWG-49602-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-16 | 132 | 400 | N | 375 | FUEL OIL SYSTEM | B0-SWG-49602 | 400V SWITCHGEAR FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-P-46002B | FUEL OIL TRANSFER PUMP MOTOR - B | 21_DIESEL OIL PUMP STATION | L1, L2, L3, PE | B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L18 → M0207 → D0203-L24 → M0206 → D0205-L24 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B025-016ET0020 → B025-016ET0019 → B025-016ET0018 → B025-016ET0017 → B025-016ET0016 → B025-996ET0003 → M0103 → B070-006AC0006 → END
B0-SWG-49602 | -P20 | 03 | From변경 | PE-L1-3C4-10 | PE-L1-3C4-10 | FOP-C-009 | B0-SWG-49602-P2003 |  | 1 | 641 | B0-SWG-49601-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-10 | 0.2 | 230 | N | 380 | FUEL OIL SYSTEM | B0-SWG-49601 | 400V SWITCHGEAR FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, N, PE | B0-P-46002A | FUEL OIL TRANSFER PUMP MOTOR - A_SPACE HEATER | 21_DIESEL OIL PUMP STATION | L1, N, PE | B049-006AT0003 → B049-006AT0002 → D0204-L15 → M0207 → D0203-L22 → M0206 → D0205-L22 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B025-016ET0020 → B025-016ET0019 → B025-016ET0018 → B025-016ET0017 → B025-016ET0016 → B025-996ET0003 → M0103 → B070-007AC0001 → END
B0-SWG-49601 | -P20 | 03 | From변경 | PE-L1-3C4-10 | PE-L1-3C4-10 | FOP-C-010 | B0-SWG-49601-P2003 |  | 1 | 642 | B0-SWG-49602-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-10 | 0.2 | 230 | N | 380 | FUEL OIL SYSTEM | B0-SWG-49602 | 400V SWITCHGEAR FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, N, PE | B0-P-46002B | FUEL OIL TRANSFER PUMP MOTOR - B_SPACE HEATER | 21_DIESEL OIL PUMP STATION | L1, N, PE | B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L18 → M0207 → D0203-L24 → M0206 → D0205-L24 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B025-016ET0020 → B025-016ET0019 → B025-016ET0018 → B025-016ET0017 → B025-016ET0016 → B025-996ET0003 → M0103 → B070-007AC0002 → END
B0-MCC-49602 | -P20 | 24 |  | PE-L1-4C10-01 | PE-L1-4C10-01 | FOP-C-011 |  |  | 1 | 643 | B0-MCC-49602-P2024 | 0.6/1kV CU/XLPE/LSZH | 4C x 10sqmm | PE-L1-4C10-01 | 5.5 | 400 | N | 390 | FUEL OIL SYSTEM | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-P-46003A | DRAIN OIL PUMP MOTOR - A | 23.7_DIESEL FUEL DRAINAGE RESERVOIR | L1, L2, L3, PE | B049-006AT0008 → B049-006AT0009 → B049-006AT0011 → B049-006AT0003 → B049-006AT0002 → D0204-L16 → M0207 → D0203-L22 → M0206 → D0205-L22 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B025-016ET0020 → B025-016ET0019 → B025-016ET0018 → B025-016ET0017 → B025-016ET0016 → B070-016AC0004 → B070-006AC0014 → B070-016AC0005 → B070-016AC0002 → END
B0-MCC-49601 | -P20 | 26 |  | PE-L1-4C10-01 | PE-L1-4C10-01 | FOP-C-012 |  |  | 1 | 644 | B0-MCC-49601-P2026 | 0.6/1kV CU/XLPE/LSZH | 4C x 10sqmm | PE-L1-4C10-01 | 5.5 | 400 | N | 335 | FUEL OIL SYSTEM | B0-MCC-49601 | 400V MCC FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-P-46003B | DRAIN OIL PUMP MOTOR - B | 23.7_DIESEL FUEL DRAINAGE RESERVOIR | L1, L2, L3, PE | B049-006BT0004 → B049-006BT0003 → B049-006BT0001 → D0204-L17 → M0207 → D0203-L23 → M0206 → D0205-L23 → M0205 → B025-996FT0005 → B025-016FT0028 → B025-016FT0020 → B025-016FT0019 → B025-016FT0018 → B070-016AC0006 → B070-006AC0017 → B070-016AC0003 → B070-016AC0001 → END
B0-MCC-49602 | -P20 | 25 |  | PE-L1-4C4-07 | PE-L1-4C4-07 | FOP-C-013 |  |  | 1 | 645 | B0-MCC-49602-P2025 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-07 | 1.5 | 400 | N | 400 | FUEL OIL SYSTEM | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-MOV-46001 | FUEL OIL TRANSFER PUMP A DISCHARGE MOV | 21_DIESEL OIL PUMP STATION | L1, L2, L3, PE | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L16 → M0207 → D0203-L22 → M0206 → D0205-L22 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B025-016ET0020 → B025-016ET0019 → B025-016ET0018 → B025-016ET0017 → B025-016ET0016 → B025-996ET0003 → M0103 → B070-006AC0001 → END
B0-MCC-49601 | -P20 | 27 |  | PE-L1-4C4-07 | PE-L1-4C4-07 | FOP-C-014 |  |  | 1 | 646 | B0-MCC-49601-P2027 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-07 | 1.5 | 400 | N | 380 | FUEL OIL SYSTEM | B0-MCC-49601 | 400V MCC FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-MOV-46002 | FUEL OIL TRANSFER PUMP B DISCHARGE MOV | 21_DIESEL OIL PUMP STATION | L1, L2, L3, PE | B049-006AT0004 → B049-006AT0003 → B049-006AT0002 → D0204-L16 → M0207 → D0203-L22 → M0206 → D0205-L22 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B025-016ET0020 → B025-016ET0019 → B025-016ET0018 → B025-016ET0017 → B025-016ET0016 → B025-996ET0003 → M0103 → B070-006AC0004 → END
B0-MCC-72601 | -P20 | 01 |  | PE-L1-4C4-06 | PE-L1-4C4-06 | OFS-C-001 |  |  | 1 | 647 | B0-MCC-72601-P2001 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-06 | 3.7 | 400 | N | 150 | OIL FACILITY SYSTEM | B0-MCC-72601 | 400V MCC FOR WORKSHOP - A | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, L2, L3, PE | B0-P-52001A | FRESH LUBE OIL UNLOADING PUMP MOTOR - A | 35_TURBINE LUBRICANT OIL(LO) PUMP STATION | L1, L2, L3, PE | B071-007AT0001 → D0101-L11 → M0102 → B025-996AT0001 → B025-016AT0004 → B025-016AT0005 → B025-016AT0006 → B025-996AT0015 → B025-016AT0007 → B025-996AT0002 → M0101 → B052-006AC0006 → END
B0-MCC-72602 | -P20 | 01 |  | PE-L1-4C4-06 | PE-L1-4C4-06 | OFS-C-002 |  |  | 1 | 648 | B0-MCC-72602-P2001 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-06 | 3.7 | 400 | N | 150 | OIL FACILITY SYSTEM | B0-MCC-72602 | 400V MCC FOR WORKSHOP - B | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, L2, L3, PE | B0-P-52001B | FRESH LUBE OIL UNLOADING PUMP MOTOR - B | 35_TURBINE LUBRICANT OIL(LO) PUMP STATION | L1, L2, L3, PE | B071-006AT0001 → D0101-L11 → M0102 → B025-997AT0001 → B025-017AT0004 → B025-017AT0005 → B025-017AT0006 → B025-997AT0015 → B025-017AT0007 → B025-997AT0002 → M0101 → B052-006AC0005 → END
B0-MCC-72601 | -P20 | 02 |  | PE-L1-4C16-01 | PE-L1-4C16-01 | OFS-C-003 |  |  | 1 | 649 | B0-MCC-72601-P2002 | 0.6/1kV CU/XLPE/LSZH | 4C x 16sqmm | PE-L1-4C16-01 | 18.5 | 400 | N | 160 | OIL FACILITY SYSTEM | B0-MCC-72601 | 400V MCC FOR WORKSHOP - A | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, L2, L3, PE | B0-P-52003A | LUBE OIL FORWARDING PUMP MOTOR - A | 35_TURBINE LUBRICANT OIL(LO) PUMP STATION | L1, L2, L3, PE | B071-007AT0001 → D0101-L12 → M0102 → B025-996AT0001 → B025-016AT0004 → B025-016AT0005 → B025-016AT0006 → B025-996AT0015 → B025-016AT0007 → B025-996AT0002 → M0101 → B052-006AC0004 → END
B0-MCC-72602 | -P20 | 02 |  | PE-L1-4C16-01 | PE-L1-4C16-01 | OFS-C-004 |  |  | 1 | 650 | B0-MCC-72602-P2002 | 0.6/1kV CU/XLPE/LSZH | 4C x 16sqmm | PE-L1-4C16-01 | 18.5 | 400 | N | 160 | OIL FACILITY SYSTEM | B0-MCC-72602 | 400V MCC FOR WORKSHOP - B | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, L2, L3, PE | B0-P-52003B | LUBE OIL FORWARDING PUMP MOTOR - B | 35_TURBINE LUBRICANT OIL(LO) PUMP STATION | L1, L2, L3, PE | B071-006AT0001 → D0101-L12 → M0102 → B025-997AT0001 → B025-017AT0004 → B025-017AT0005 → B025-017AT0006 → B025-997AT0015 → B025-017AT0007 → B025-997AT0002 → M0101 → B052-006AC0003 → END
B0-MCC-72602 | -P20 | 03 |  | PE-L1-4C4-07 | PE-L1-4C4-07 | OFS-C-004-004 |  |  | 1 | 651 | B0-MCC-72602-P2003 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-07 | 3.7 | 400 | N | 170 | OIL FACILITY SYSTEM | B0-MCC-72602 | 400V MCC FOR WORKSHOP - B | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, L2, L3, PE | B0-P-52004A | DRAIN LUBE OIL PUMP - A | 35.1_TURBINE OIL DRAINAGE RESERVOIR | L1, L2, L3, PE | B071-007AT0001 → D0101-L13 → M0102 → B025-996AT0001 → B025-016AT0004 → B025-016AT0005 → B025-016AT0006 → B025-996AT0015 → B025-016AT0007 → B025-016AT0008 → B052-016AC0005 → B052-006AC0001 → B052-016AC0006 → B052-016AC0003 → END
B0-MCC-72601 | -P20 | 03 |  | PE-L1-4C4-07 | PE-L1-4C4-07 | OFS-C-004-005 |  |  | 1 | 652 | B0-MCC-72601-P2003 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-07 | 3.7 | 400 | N | 170 | OIL FACILITY SYSTEM | B0-MCC-72601 | 400V MCC FOR WORKSHOP - A | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, L2, L3, PE | B0-P-52004B | DRAIN LUBE OIL PUMP - B | 35.1_TURBINE OIL DRAINAGE RESERVOIR | L1, L2, L3, PE | B071-006AT0001 → D0101-L13 → M0102 → B025-997AT0001 → B025-017AT0004 → B025-017AT0005 → B025-017AT0006 → B025-997AT0015 → B025-017AT0007 → B025-017AT0008 → B052-016AC0007 → B052-006AC0010 → B052-016AC0001 → B052-016AC0002
B0-MCC-64602 | -P20 | 03 |  | PE-L1-5C150/95-01 | PE-L1-5C150/95-01 | FGS-C-024 | DONE(10/27) | DONE | 1 | 653 | B0-MCC-64602-P2003 | 0.6/1kV CU/XLPE/LSZH | 4C x 150sqmm + 1C X 95sqmm | PE-L1-5C150/95-01 | 69.9 | 400 | N | 510 | FUEL GAS SUPPLY SYSTEM | B0-MCC-64602 | 400V MCC FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B0-PP-44601 | LV PDP FOR FGSS | 18_AUXILIARY BOILER / LER | L1, L2, L3, N, PE | B064-016AT0033 → B064-016AT0034 → B064-016AT0233 → B064-016AT0234 → B064-016AT0048 → B064-016AT0049 → B064-016AT0050 → B064-016AT0051 → B064-016AT0312 → B064-016AT0071 → B064-016AT0070 → B064-016AT0069 → B064-016AT0068 → B064-016AT0067 → B064-016AT0277 → B064-016AT0278 → B064-016AT0094 → B064-016AT0296 → B064-016AT0110 → B064-016AT0109 → B064-016AT0285 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0054 → B025-016DT0053 → B025-016DT0051 → B025-996DT0018 → B025-016DT0052 → B025-016DT0050 → B025-016DT0049 → B025-016DT0048 → B025-016DT0047 → B025-996DT0008 → M0521 → D0528-L11 → B078-006AT0001 → END
B0-UPSP-64701 | -P20 | 01 | 길이오류 정정 (550->470m_10/12) | PE-L1-3C25/16-02 | PE-L1-3C25/16-02 | FGS-C-025 | DONE(10/27) | DONE | 1 | 654 | B0-UPSP-64701-P2001 | 0.6/1kV CU/XLPE/LSZH | 2C x 25sqmm + 1C X 16sqmm | PE-L1-3C25/16-02 | 1 | 230 | U | 470 | FUEL GAS SUPPLY SYSTEM | B0-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-P-4401 | PLC PANEL CONTROL POWER (MAIN) | 18_AUXILIARY BOILER / LER | L1, N, PE | B164-006HT0206 → B164-006HT0205 → B164-006HT0004 → B164-006HT0005 → B064-006AC0007 → M0501 → B064-996AT0120 → B064-016AT0032 → B064-016AT0213 → B064-016AT0214 → B064-016AT0215 → B064-016AT0216 → B064-016AT0217 → B064-016AT0106 → B064-016AT0107 → B064-016AT0108 → B064-016AT0285 → B025-016CT0090 → B025-016CT0089 → B025-016CT0067 → B025-016CT0066 → B025-016CT0065 → B025-016CT0064 → B025-016CT0063 → B025-016CT0062 → B025-016CT0061 → B025-016CT0060 → B025-996CT0020 → B025-016CT0059 → B025-016CT0054 → B025-016CT0053 → B025-016CT0050 → B025-016CT0049 → B025-016CT0048 → B025-016CT0047 → B025-996CT0008 → M0521 → D0528-L11 → B078-006AT0001 → END
B0-UPSP-64702 | -P20 | 01 | 길이오류 정정 ('520->470m_10/12) | PE-L1-3C25/16-02 | PE-L1-3C25/16-02 | FGS-C-025-001 | DONE(10/27) | DONE | 1 | 655 | B0-UPSP-64702-P2001 | 0.6/1kV CU/XLPE/LSZH | 2C x 25sqmm + 1C X 16sqmm | PE-L1-3C25/16-02 | 1 | 230 | U | 470 | FUEL GAS SUPPLY SYSTEM | B0-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-P-4401 | PLC PANEL CONTROL POWER (REDUNDANT) | 18_AUXILIARY BOILER / LER | L1, N, PE | B064-006FT0206 → B064-006FT0205 → B064-006FT0003 → B064-006AC0006 → M0501 → B064-996BT0020 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0054 → B025-016DT0053 → B025-016DT0050 → B025-016DT0049 → B025-016DT0048 → B025-016DT0047 → B025-996DT0008 → M0521 → D0528-L12 → B078-006BT0001 → END
B1-MCC-64602 | -P20 | 23 |  | PE-L1-5C4-01 | PE-L1-5C4-01 | FGS-C-026-003 |  |  | 1 | 656 | B1-MCC-64602-P2023 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-01 | 1.6 | 400 | N | 330 | FUEL GAS SUPPLY SYSTEM | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B1-LCP-4403 | FUEL GAS CONDENSATE PUMP FOR FINAL FILTER #11 | 1.1_MAIN BUILDING COMPLEX (NEAR HRSG #11) | L1, L2, L3, N, PE | B164-016ET0106 → B164-996ET0022 → M0504 → D0531-L31 → M0510 → D0517-L22 → M0501 → D0503-L41 → M0502 → D0504-L41 → M0503 → D0501-L41 → M0328 → D0324-L41 → M0329 → B114-996DT0081 → B114-016DT0082 → B114-016DT0083 → B114-016DT0084 → B114-016DT0096 → B114-016DT0097 → B114-016DT0098 → B114-016DT0099 → B161-016AC0004 → B161-006AC0005 → END
B1-MCC-64603 | -P20 | 06 |  | PE-L1-5C4-01 | PE-L1-5C4-01 | FGS-C-026-004 |  | DONE | 1 | 657 | B1-MCC-64603-P2006 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-01 | 1.6 | 400 | N | 400 | FUEL GAS SUPPLY SYSTEM | B1-MCC-64603 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B1-LCP-4404 | FUEL GAS CONDENSATE PUMP FOR FINAL FILTER #12 | 1.1_MAIN BUILDING COMPLEX (NEAR HRSG #12) | L1, L2, L3, N, PE | B164-016AT0094 → B164-016AT0093 → B164-016AT0092 → B164-996AT0022 → M0504 → D0531-L32 → M0510 → D0517-L23 → M0501 → D0503-L42 → M0502 → D0504-L42 → M0503 → D0501-L42 → M0328 → D0324-L42 → M0329 → B114-996CT0071 → B114-016CT0072 → B114-016CT0073 → B114-016CT0074 → B114-016CT0075 → B114-016CT0076 → B114-016CT0087 → B114-016CT0088 → B114-016CT0089 → B114-016CT0090 → B161-016CC0004 → B161-006CC0005 → END
B2-MCC-64601 | -P20 | 19 |  | PE-L1-5C4-04 | PE-L1-5C4-04 | FGS-C-026-005 |  |  | 1 | 658 | B2-MCC-64601-P2019 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-04 | 1.6 | 400 | N | 360 | FUEL GAS SUPPLY SYSTEM | B2-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, N, PE | B2-LCP-4405 | FUEL GAS CONDENSATE PUMP FOR FINAL FILTER #21 | 1.1_MAIN BUILDING COMPLEX (NEAR HRSG #21) | L1, L2, L3, N, PE | B264-016CT0024 → B264-016CT0025 → B264-016CT0026 → B264-016CT0027 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L33 → M0406 → D0301-L35 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B215-016AT0050 → B215-016AT0051 → B215-016AT0064 → B215-016AT0065 → B215-016AT0066 → B215-016AT0055 → B215-016AT0056 → B215-016AT0057 → B215-016AT0058 → B261-016CC0004 → B261-006CC0005 → END
B2-MCC-64603 | -P20 | 06 |  | PE-L1-5C4-04 | PE-L1-5C4-04 | FGS-C-026-006 |  |  | 1 | 659 | B2-MCC-64603-P2006 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-04 | 1.6 | 400 | N | 120 | FUEL GAS SUPPLY SYSTEM | B2-MCC-64603 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, N, PE | B2-LCP-4406 | FUEL GAS CONDENSATE PUMP FOR FINAL FILTER #22 | 1.1_MAIN BUILDING COMPLEX (NEAR HRSG #22) | L1, L2, L3, N, PE | B264-016CT0027 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L33 → M0406 → D0301-L35 → M0301 → B261-006AC0005 → END
B0-UPSP-64702 | -P20 | 02 |  | PE-L1-3C70/35-01 | PE-L1-3C70/35-01 | FGS-C-030 | DONE(10/27) | DONE | 1 | 660 | B0-UPSP-64702-P2002 | 0.6/1kV CU/XLPE/LSZH | 2C x 70sqmm + 1C X 35sqmm | PE-L1-3C70/35-01 | 4.3 | 230 | U | 490 | FUEL GAS SUPPLY SYSTEM | B0-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-UPSP-44701 | UPS PDP FOR FGSS | 18_AUXILIARY BOILER / LER | L1, N, PE | B064-006FT0206 → B064-006FT0009 → B064-006FT0208 → B064-006FT0207 → B064-006FT0005 → B064-006AC0011 → M0501 → B064-996BT0020 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B025-016CT0090 → B025-016CT0089 → B025-016CT0067 → B025-016CT0066 → B025-016CT0065 → B025-016CT0064 → B025-016CT0063 → B025-016CT0062 → B025-016CT0061 → B025-016CT0060 → B025-996CT0020 → B025-016CT0059 → B025-016CT0054 → B025-016CT0053 → B025-016CT0051 → B025-996CT0018 → B025-016CT0052 → B025-016CT0050 → B025-016CT0049 → B025-016CT0048 → B025-016CT0047 → B025-996CT0008 → M0521 → D0528-L12 → B078-007BC0001 → END
B1-SWG-64303 | -P10 | 03 |  | PE-M1-3C120-07 | PE-M1-3C120-07 | FWP-U1-001 | DONE(9/28) | DONE | 1 | 661 | B1-SWG-64303-P1003 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-07 | 1300 | 10000 | N | 290 | FEEDWATER SYSTEM | B1-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B1-M-30001A | MOTOR FOR BOILER FEEDWATER PUMP #A | 1.1_MAIN BUILDING COMPLEX | U1,V1,W1 | B164-013AT0058 → B164-013AT0275 → B164-013AT0052 → B164-013AT0228 → B164-013AT0227 → B164-013AT0226 → B164-993AT0019 → M0501 → D0503-M14 → M0502 → D0504-M14 → M0503 → D0501-M14 → M0328 → D0324-M14 → M0329 → B114-993ET0081 → B114-013ET0082 → B114-013ET0083 → B114-013ET0084 → B114-013ET0096 → B114-013ET0097 → B114-013ET0098 → B161-013AC0002 → B161-003AC0002 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B1-SWG-64303 | -P20 | 03 |  | PE-L1-3C4-10 | PE-L1-3C4-10 | FWP-U1-002 | DONE(9/28) | DONE | 1 | 662 | B1-SWG-64303-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-10 | 0.5 | 230 | N | 300 | FEEDWATER SYSTEM | B1-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-M-30001A | MOTOR SPACE HEATER FOR BOILER FEEDWATER PUMP #A | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B064-016AT0068 → B064-016AT0067 → B064-016AT0066 → B064-016AT0065 → B064-016AT0064 → B064-016AT0063 → B064-016AT0214 → B064-016AT0213 → B064-016AT0032 → B064-996AT0120 → M0501 → D0503-L41 → M0502 → D0504-L41 → M0503 → D0501-L41 → M0328 → D0324-L41 → M0329 → B114-996DT0081 → B114-016DT0082 → B114-016DT0083 → B114-016DT0084 → B114-016DT0096 → B114-016DT0097 → B114-016DT0098 → B161-017AC0004 → B161-007AC0004 → END
B1-DB-64601 | -P20 | 02 |  | PE-L1-3C4-10 | PE-L1-3C4-10 | FWP-U1-003 | DONE(9/28) | DONE | 1 | 663 | B1-DB-64601-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-10 | 0.05 | 230 | N | 310 | FEEDWATER SYSTEM | B1-DB-64601 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-M-30001A | REVERSE ROTATION SENSOR FOR BFP #A | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B164-016AT0090 → B164-016AT0091 → B164-996AT0022 → M0504 → D0531-L31 → M0510 → D0517-L22 → M0501 → D0503-L41 → M0502 → D0504-L41 → M0503 → D0501-L41 → M0328 → D0324-L41 → M0329 → B114-996DT0081 → B114-016DT0082 → B114-016DT0083 → B114-016DT0084 → B114-016DT0096 → B114-016DT0097 → B114-016DT0098 → B161-017AC0003 → B161-007AC0003 → END
B1-SWG-64304 | -P10 | 02 |  | PE-M1-3C120-08 | PE-M1-3C120-08 | FWP-U1-006 | DONE(9/28) | DONE | 1 | 664 | B1-SWG-64304-P1002 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-08 | 1300 | 10000 | N | 300 | FEEDWATER SYSTEM | B1-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B1-M-30001B | MOTOR FOR BOILER FEEDWATER PUMP #B | 1.1_MAIN BUILDING COMPLEX | U1,V1,W1 | B164-013BT0085 → B164-013BT0291 → B164-013BT0290 → B164-013BT0054 → B164-013BT0053 → B164-013BT0052 → B164-013BT0228 → B164-013BT0227 → B164-013BT0226 → B164-993BT0019 → M0501 → D0503-M15 → M0502 → D0504-M15 → M0503 → D0501-M15 → M0328 → D0324-M15 → M0329 → B114-993FT0071 → B114-013FT0072 → B114-013FT0073 → B114-013FT0074 → B114-013FT0092 → B114-013FT0093 → B114-013FT0094 → B161-013AC0001 → B161-003AC0001 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B1-SWG-64304 | -P20 | 04 |  | PE-L1-3C4-10 | PE-L1-3C4-10 | FWP-U1-007 | DONE(9/28) | DONE | 1 | 665 | B1-SWG-64304-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-10 | 0.5 | 230 | N | 310 | FEEDWATER SYSTEM | B1-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-M-30001B | MOTOR SPACE HEATER FOR BOILER FEEDWATER PUMP #B | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B064-016AT0079 → B064-016AT0078 → B064-016AT0077 → B064-016AT0076 → B064-016AT0075 → B064-016AT0074 → B064-016AT0073 → B064-016AT0215 → B064-016AT0214 → B064-016AT0213 → B064-016AT0032 → B064-996AT0120 → M0501 → D0503-L42 → M0502 → D0504-L42 → M0503 → D0501-L42 → M0328 → D0324-L42 → M0329 → B114-996DT0081 → B114-016DT0082 → B114-016DT0083 → B114-016DT0084 → B114-016DT0096 → B114-016DT0097 → B114-016DT0098 → B161-017AC0002 → B161-007AC0002 → END
B1-DB-64602 | -P20 | 01 |  | PE-L1-3C4-11 | PE-L1-3C4-11 | FWP-U1-008 | DONE(9/28) | DONE | 1 | 666 | B1-DB-64602-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-11 | 0.05 | 230 | N | 300 | FEEDWATER SYSTEM | B1-DB-64602 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-M-30001B | REVERSE ROTATION SENSOR FOR BFP #B | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B164-016AT0115 → B164-996AT0023 → M0504 → D0531-L32 → M0510 → D0517-L23 → M0501 → D0503-L42 → M0502 → D0504-L42 → M0503 → D0501-L42 → M0328 → D0324-L42 → M0329 → B114-996DT0081 → B114-016DT0082 → B114-016DT0083 → B114-016DT0084 → B114-016DT0096 → B114-016DT0097 → B114-016DT0098 → B161-017AC0001 → B161-007AC0001 → END
B1-SWG-64304 | -P10 | 03 |  | PE-M1-3C120-09 | PE-M1-3C120-09 | FWP-U2-001 | DONE(9/28) | DONE | 1 | 667 | B1-SWG-64304-P1003 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-09 | 1300 | 10000 | N | 340 | FEEDWATER SYSTEM | B1-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B1-M-31001A | MOTOR FOR BOILER FEEDWATER PUMP #A | 1.1_MAIN BUILDING COMPLEX | U1,V1,W1 | B164-013BT0085 → B164-013BT0291 → B164-013BT0290 → B164-013BT0054 → B164-013BT0053 → B164-013BT0052 → B164-013BT0228 → B164-013BT0227 → B164-013BT0226 → B164-993BT0019 → M0501 → D0503-M16 → M0502 → D0504-M16 → M0503 → D0501-M16 → M0328 → D0324-M16 → M0329 → B114-993FT0071 → B114-013FT0072 → B114-013FT0073 → B114-013FT0074 → B114-013FT0075 → B114-013FT0076 → B114-013FT0077 → B114-013FT0078 → B114-013FT0079 → B161-013CC0002 → B161-003CC0002 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B1-SWG-64304 | -P20 | 02 |  | PE-L1-3C4-11 | PE-L1-3C4-11 | FWP-U2-002 | DONE(9/28) | DONE | 1 | 668 | B1-SWG-64304-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-11 | 0.5 | 230 | N | 350 | FEEDWATER SYSTEM | B1-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-M-31001A | MOTOR SPACE HEATER FOR BOILER FEEDWATER PUMP #A | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B064-016AT0079 → B064-016AT0078 → B064-016AT0077 → B064-016AT0076 → B064-016AT0075 → B064-016AT0074 → B064-016AT0073 → B064-016AT0215 → B064-016AT0214 → B064-016AT0213 → B064-016AT0032 → B064-996AT0120 → M0501 → D0503-L41 → M0502 → D0504-L41 → M0503 → D0501-L41 → M0328 → D0324-L41 → M0329 → B114-996CT0071 → B114-016CT0072 → B114-016CT0073 → B114-016CT0074 → B114-016CT0075 → B114-016CT0076 → B114-016CT0087 → B114-016CT0088 → B114-016CT0089 → B161-017CC0004 → B161-007CC0004 → END
B1-DB-64604 | -P20 | 01 |  | PE-L1-3C4-11 | PE-L1-3C4-11 | FWP-U2-003 | DONE(9/28) | DONE | 1 | 669 | B1-DB-64604-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-11 | 0.05 | 230 | N | 360 | FEEDWATER SYSTEM | B1-DB-64604 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-M-31001A | REVERSE ROTATION SENSOR FOR BFP #A | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B164-016AT0118 → B164-016AT0117 → B164-016AT0116 → B164-996AT0023 → M0504 → D0531-L31 → M0510 → D0517-L22 → M0501 → D0503-L41 → M0502 → D0504-L41 → M0503 → D0501-L41 → M0328 → D0324-L41 → M0329 → B114-996CT0071 → B114-016CT0072 → B114-016CT0073 → B114-016CT0074 → B114-016CT0075 → B114-016CT0076 → B114-016CT0087 → B114-016CT0088 → B114-016CT0089 → B161-017CC0003 → B161-007CC0003 → END
B1-SWG-64303 | -P10 | 04 |  | PE-M1-3C120-10 | PE-M1-3C120-10 | FWP-U2-006 | DONE(9/28) | DONE | 1 | 670 | B1-SWG-64303-P1004 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-10 | 1300 | 10000 | N | 330 | FEEDWATER SYSTEM | B1-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B1-M-31001B | MOTOR FOR BOILER FEEDWATER PUMP #B | 1.1_MAIN BUILDING COMPLEX | U1,V1,W1 | B164-013AT0059 → B164-013AT0058 → B164-013AT0275 → B164-013AT0052 → B164-013AT0228 → B164-013AT0227 → B164-013AT0226 → B164-993AT0019 → M0501 → D0503-M17 → M0502 → D0504-M17 → M0503 → D0501-M17 → M0328 → D0324-M17 → M0329 → B114-993ET0081 → B114-013ET0082 → B114-013ET0083 → B114-013ET0084 → B114-013ET0085 → B114-013ET0086 → B114-013ET0087 → B114-013ET0088 → B114-013ET0089 → B161-013CC0001 → B161-003CC0001 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B1-SWG-64303 | -P20 | 04 |  | PE-L1-3C4-11 | PE-L1-3C4-11 | FWP-U2-007 | DONE(9/28) | DONE | 1 | 671 | B1-SWG-64303-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-11 | 0.5 | 230 | N | 350 | FEEDWATER SYSTEM | B1-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-M-31001B | MOTOR SPACE HEATER FOR BOILER FEEDWATER PUMP #B | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B064-016AT0068 → B064-016AT0067 → B064-016AT0066 → B064-016AT0065 → B064-016AT0064 → B064-016AT0063 → B064-016AT0214 → B064-016AT0213 → B064-016AT0032 → B064-996AT0120 → M0501 → D0503-L42 → M0502 → D0504-L42 → M0503 → D0501-L42 → M0328 → D0324-L42 → M0329 → B114-996CT0071 → B114-016CT0072 → B114-016CT0073 → B114-016CT0074 → B114-016CT0075 → B114-016CT0076 → B114-016CT0087 → B114-016CT0088 → B114-016CT0089 → B161-017CC0002 → B161-007CC0002 → END
B1-DB-64603 | -P20 | 02 |  | PE-L1-3C4-11 | PE-L1-3C4-11 | FWP-U2-008 | DONE(9/28) | DONE | 1 | 672 | B1-DB-64603-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-11 | 0.05 | 230 | N | 370 | FEEDWATER SYSTEM | B1-DB-64603 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-M-31001B | REVERSE ROTATION SENSOR FOR BFP #B | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B164-016AT0094 → B164-016AT0093 → B164-016AT0092 → B164-996AT0022 → M0504 → D0531-L32 → M0510 → D0517-L23 → M0501 → D0503-L42 → M0502 → D0504-L42 → M0503 → D0501-L42 → M0328 → D0324-L42 → M0329 → B114-996CT0071 → B114-016CT0072 → B114-016CT0073 → B114-016CT0074 → B114-016CT0075 → B114-016CT0076 → B114-016CT0087 → B114-016CT0088 → B114-016CT0089 → B161-017CC0001 → B161-007CC0001 → END
B2-SWG-64303 | -P10 | 03 |  | PE-M1-3C120-23 | PE-M1-3C120-23 | FWP-U3-001 |  |  | 1 | 673 | B2-SWG-64303-P1003 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-23 | 1300 | 10000 | N | 290 | FEEDWATER SYSTEM | B2-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1,V1,W1 | B2-M-30001A | MOTOR FOR BOILER FEEDWATER PUMP #A | 1.1_MAIN BUILDING COMPLEX | U1,V1,W1 | B264-013LT0005 → B264-013LT0215 → B264-993LT0004 → M0405 → D0421-M14 → M0406 → D0301-M14 → M0301 → B215-993CT0026 → B215-013CT0048 → B215-013CT0061 → B215-013CT0062 → B215-013CT0063 → B215-013CT0064 → B215-013CT0065 → B215-013CT0066 → B215-013CT0067 → B215-013CT0068 → B215-013CT0069 → B261-013CC0002 → B261-003CC0002 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B2-SWG-64303 | -P20 | 03 |  | PE-L1-3C4-20 | PE-L1-3C4-20 | FWP-U3-002 |  |  | 1 | 674 | B2-SWG-64303-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-20 | 0.5 | 230 | N | 300 | FEEDWATER SYSTEM | B2-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-M-30001A | MOTOR SPACE HEATER FOR BOILER FEEDWATER PUMP #A | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B264-016AT0011 → B264-016AT0233 → B264-016AT0015 → B264-996AT0011 → M0405 → D0421-L32 → M0406 → D0301-L36 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B215-016AT0050 → B215-016AT0051 → B215-016AT0064 → B215-016AT0065 → B215-016AT0066 → B215-016AT0055 → B215-016AT0056 → B215-016AT0057 → B261-017CC0004 → B261-007CC0004 → END
B2-DB-64601 | -P20 | 02 |  | PE-L1-3C4-20 | PE-L1-3C4-20 | FWP-U3-003 |  |  | 1 | 675 | B2-DB-64601-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-20 | 0.05 | 230 | N | 320 | FEEDWATER SYSTEM | B2-DB-64601 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-M-30001A | REVERSE ROTATION SENSOR FOR BFP #A | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B264-016CT0024 → B264-016CT0025 → B264-016CT0026 → B264-016CT0027 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L32 → M0406 → D0301-L36 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B215-016AT0050 → B215-016AT0051 → B215-016AT0064 → B215-016AT0065 → B215-016AT0066 → B215-016AT0055 → B215-016AT0056 → B215-016AT0057 → B261-017CC0003 → B261-007CC0003 → END
B2-SWG-64304 | -P10 | 02 | From변경(9/30) | PE-M1-3C120-24 | PE-M1-3C120-24 | FWP-U3-006 | B2-SWG-64304-P1002 |  | 1 | 676 | B2-SWG-64303-P1004 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-24 | 1300 | 10000 | N | 300 | FEEDWATER SYSTEM | B2-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1,V1,W1 | B2-M-30001B | MOTOR FOR BOILER FEEDWATER PUMP #B | 1.1_MAIN BUILDING COMPLEX | U1,V1,W1 | B264-013MT0005 → B264-013MT0218 → B264-993MT0006 → M0405 → D0421-M15 → M0406 → D0301-M13 → M0301 → B215-993DT0001 → B215-013DT0002 → B215-013DT0003 → B215-013DT0004 → B215-013DT0005 → B215-013DT0052 → B215-013DT0053 → B215-013DT0054 → B215-013DT0055 → B215-013DT0056 → B215-013DT0057 → B261-013CC0001 → B261-003CC0001 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B2-SWG-64304 | -P20 | 03 | From변경(9/30) | PE-L1-3C4-21 | PE-L1-3C4-21 | FWP-U3-007 | B2-SWG-64304-P2003 |  | 1 | 677 | B2-SWG-64303-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-21 | 0.5 | 230 | N | 300 | FEEDWATER SYSTEM | B2-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-M-30001B | MOTOR SPACE HEATER FOR BOILER FEEDWATER PUMP #B | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B264-016AT0011 → B264-016AT0233 → B264-016AT0015 → B264-996AT0011 → M0405 → D0421-L32 → M0406 → D0301-L36 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B215-016AT0050 → B215-016AT0051 → B215-016AT0064 → B215-016AT0065 → B215-016AT0066 → B215-016AT0055 → B215-016AT0056 → B215-016AT0057 → B261-017CC0002 → B261-007CC0002 → END
B2-DB-64602 | -P20 | 01 |  | PE-L1-3C4-21 | PE-L1-3C4-21 | FWP-U3-008 |  |  | 1 | 678 | B2-DB-64602-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-21 | 0.05 | 230 | N | 330 | FEEDWATER SYSTEM | B2-DB-64602 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-M-30001B | REVERSE ROTATION SENSOR FOR BFP #B | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B264-016AT0045 → B264-016AT0046 → B264-016AT0209 → B264-016AT0026 → B264-016AT0027 → B264-016AT0225 → B264-996AT0011 → M0405 → D0421-L32 → M0406 → D0301-L36 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B215-016AT0050 → B215-016AT0051 → B215-016AT0064 → B215-016AT0065 → B215-016AT0066 → B215-016AT0055 → B215-016AT0056 → B215-016AT0057 → B261-017CC0001 → B261-007CC0001 → END
B2-SWG-64304 | -P10 | 03 |  | PE-M1-3C120-23 | PE-M1-3C120-23 | FWP-U4-001 |  |  | 1 | 679 | B2-SWG-64304-P1003 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-23 | 1300 | 10000 | N | 210 | FEEDWATER SYSTEM | B2-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1,V1,W1 | B2-M-31001A | MOTOR FOR BOILER FEEDWATER PUMP #A | 1.1_MAIN BUILDING COMPLEX | U1,V1,W1 | B264-013PT0020 → B264-013PT0219 → B264-993PT0007 → M0405 → D0421-M16 → M0406 → D0301-M12 → M0301 → B215-993DT0001 → B215-013DT0002 → B215-013DT0003 → B215-013DT0004 → B261-013AC0002 → B261-003AC0002 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B2-SWG-64304 | -P20 | 02 |  | PE-L1-3C4-21 | PE-L1-3C4-21 | FWP-U4-002 |  |  | 1 | 680 | B2-SWG-64304-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-21 | 0.5 | 230 | N | 190 | FEEDWATER SYSTEM | B2-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-M-31001A | MOTOR SPACE HEATER FOR BOILER FEEDWATER PUMP #A | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B264-016BT0015 → B264-996CT0009 → M0405 → D0421-L32 → M0406 → D0301-L36 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B261-017AC0004 → B261-007AC0004 → END
B2-DB-64604 | -P20 | 01 |  | PE-L1-3C4-20 | PE-L1-3C4-20 | FWP-U4-003 |  |  | 1 | 681 | B2-DB-64604-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-20 | 0.05 | 230 | N | 220 | FEEDWATER SYSTEM | B2-DB-64604 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-M-31001A | REVERSE ROTATION SENSOR FOR BFP #A | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B264-016CT0047 → B264-016CT0209 → B264-016CT0026 → B264-016CT0027 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L32 → M0406 → D0301-L36 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B261-017AC0003 → B261-007AC0003 → END
B2-SWG-64303 | -P10 | 04 | From변경(9/30) | PE-M1-3C120-24 | PE-M1-3C120-24 | FWP-U4-006 | B2-SWG-64303-P1004 |  | 1 | 682 | B2-SWG-64304-P1007 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-24 | 1300 | 10000 | N | 210 | FEEDWATER SYSTEM | B2-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1,V1,W1 | B2-M-31001B | MOTOR FOR BOILER FEEDWATER PUMP #B | 1.1_MAIN BUILDING COMPLEX | U1,V1,W1 | B264-013NT0020 → B264-013NT0216 → B264-993NT0005 → M0405 → D0421-M17 → M0406 → D0301-M11 → M0301 → B215-993CT0026 → B215-013CT0048 → B215-013CT0061 → B215-013CT0062 → B261-013AC0001 → B261-003AC0001 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B2-SWG-64303 | -P20 | 04 | From변경(9/30) | PE-L1-3C4-21 | PE-L1-3C4-21 | FWP-U4-007 | B2-SWG-64303-P2004 |  | 1 | 683 | B2-SWG-64304-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-21 | 0.5 | 230 | N | 190 | FEEDWATER SYSTEM | B2-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-M-31001B | MOTOR SPACE HEATER FOR BOILER FEEDWATER PUMP #B | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B264-016BT0015 → B264-996CT0009 → M0405 → D0421-L32 → M0406 → D0301-L36 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B261-017AC0002 → B261-007AC0002 → END
B2-DB-64604 | -P20 | 02 |  | PE-L1-3C4-12 | PE-L1-3C4-12 | FWP-U4-008 |  |  | 1 | 684 | B2-DB-64604-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-12 | 0.05 | 230 | N | 220 | FEEDWATER SYSTEM | B2-DB-64604 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-M-31001B | REVERSE ROTATION SENSOR FOR BFP #B | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B264-016CT0047 → B264-016CT0209 → B264-016CT0026 → B264-016CT0027 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L32 → M0406 → D0301-L36 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B261-017AC0001 → B261-007AC0001 → END
B0-SWG-64301 | -P10 | 01 |  | PE-M1-3C120-03 | PE-M1-3C120-03 | EDG-C-001 |  | DONE | 1 | 685 | B0-SWG-64301-P1001 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-03 | 2000 | 10000 | N | 160 | BSEDG | B0-SWG-64301 | 10KV SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B0-CB-43301A | BSEDG GENERATOR VCB PANEL - A | 9_BLACK START DIESEL GENERATOR (CONTAINER TYPE) | U1,V1,W1 | B064-013CT0040 → B064-013CT0041 → B064-013CT0042 → B064-013CT0043 → B064-013CT0044 → B064-013CT0246 → B064-013CT0297 → B064-013CT0298 → B064-013CT0299 → B064-013CT0112 → B064-993CT0026 → M0509 → D0507-M17 → M0524 → D0509-M14 → M0511 → D0518-M13 → B043-021MVT0001 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B0-SWG-64301 | -P10 | 02 |  | PE-M1-3C120-07 | PE-M1-3C120-07 | EDG-C-002 |  | DONE | 1 | 686 | B0-SWG-64301-P1002 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-07 | 2000 | 10000 | N | 180 | BSEDG | B0-SWG-64301 | 10KV SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B0-CB-43301B | BSEDG GENERATOR VCB PANEL - B | 9_BLACK START DIESEL GENERATOR (CONTAINER TYPE) | U1,V1,W1 | B064-013CT0040 → B064-013CT0041 → B064-013CT0042 → B064-013CT0043 → B064-013CT0044 → B064-013CT0246 → B064-013CT0297 → B064-013CT0298 → B064-013CT0299 → B064-013CT0112 → B064-993CT0026 → M0509 → D0507-M16 → M0524 → D0509-M13 → M0511 → D0510-M13 → M0512 → D0519-M13 → B043-021MVT0002 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B0-SWG-64302 | -P10 | 01 |  | PE-M1-3C120-08 | PE-M1-3C120-08 | EDG-C-003 |  | DONE | 1 | 687 | B0-SWG-64302-P1001 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-08 | 2000 | 10000 | N | 180 | BSEDG | B0-SWG-64302 | 10KV SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B0-CB-43301C | BSEDG GENERATOR VCB PANEL - C | 9_BLACK START DIESEL GENERATOR (CONTAINER TYPE) | U1,V1,W1 | B064-013CT0042 → B064-013CT0043 → B064-013CT0044 → B064-013CT0246 → B064-013CT0297 → B064-013CT0298 → B064-013CT0299 → B064-013CT0112 → B064-993CT0026 → M0509 → D0507-M15 → M0524 → D0509-M12 → M0511 → D0510-M12 → M0512 → D0511-M12 → M0513 → D0520-M13 → B043-021MVT0003 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B0-SWG-64302 | -P10 | 02 |  | PE-M1-3C120-13 | PE-M1-3C120-13 | EDG-C-004 |  | DONE | 1 | 688 | B0-SWG-64302-P1002 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-13 | 2000 | 10000 | N | 200 | BSEDG | B0-SWG-64302 | 10KV SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B0-CB-43301D | BSEDG GENERATOR VCB PANEL - D | 9_BLACK START DIESEL GENERATOR (CONTAINER TYPE) | U1,V1,W1 | B064-013CT0042 → B064-013CT0043 → B064-013CT0044 → B064-013CT0246 → B064-013CT0297 → B064-013CT0298 → B064-013CT0299 → B064-013CT0112 → B064-993CT0026 → M0509 → D0507-M14 → M0524 → D0509-M11 → M0511 → D0510-M11 → M0512 → D0511-M11 → M0513 → D0512-M11 → M0514 → D0521-M13 → B043-021MVT0004 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B0-EMCC-64601 | -P20 | 01 | 재배정 | PE-L1-5C150/95-03 | PE-L1-5C150/95-02 | EDG-C-005 |  | DONE | 1 | 689 | B0-EMCC-64601-P2001 | 0.6/1kV CU/XLPE/LSZH | 4C x 150sqmm + 1C X 95sqmm | PE-L1-5C150/95-02 | 106.8 | 400 | E | 160 | BSEDG | B0-EMCC-64601 | 400V EMERGENCY MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B0-PP-43301A | DISTRIBUTION PANEL FOR BSEDG - A | 9_BLACK START DIESEL GENERATOR (CONTAINER TYPE) | L1, L2, L3, N, PE | B064-016BT0015 → B064-016BT0016 → B064-016BT0309 → B064-016BT0038 → B064-016BT0249 → B064-016BT0250 → B064-016BT0061 → B064-016BT0062 → B064-016BT0305 → B064-016BT0306 → B064-016BT0307 → B064-016BT0105 → B064-996BT0027 → M0509 → D0507-L27 → M0524 → D0509-L23 → M0511 → D0518-L11 → B043-016LVT0001 → END
B0-EMCC-64601 | -P20 | 02 | 재배정 | PE-L1-5C150/95-03 | PE-L1-5C150/95-02 | EDG-C-007 |  | DONE | 1 | 690 | B0-EMCC-64601-P2002 | 0.6/1kV CU/XLPE/LSZH | 4C x 150sqmm + 1C X 95sqmm | PE-L1-5C150/95-02 | 106.8 | 400 | E | 180 | BSEDG | B0-EMCC-64601 | 400V EMERGENCY MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B0-PP-43301B | DISTRIBUTION PANEL FOR BSEDG - B | 9_BLACK START DIESEL GENERATOR (CONTAINER TYPE) | L1, L2, L3, N, PE | B064-016BT0015 → B064-016BT0016 → B064-016BT0309 → B064-016BT0038 → B064-016BT0249 → B064-016BT0250 → B064-016BT0061 → B064-016BT0062 → B064-016BT0305 → B064-016BT0306 → B064-016BT0307 → B064-016BT0105 → B064-996BT0027 → M0509 → D0507-L35 → M0524 → D0509-L21 → M0511 → D0510-L21 → M0512 → D0519-L11 → B043-016LVT0002 → END
B0-EMCC-64602 | -P20 | 01 | 재배정 | PE-L1-5C150/95-02 | PE-L1-5C150/95-03 | EDG-C-009 |  | DONE | 1 | 691 | B0-EMCC-64602-P2001 | 0.6/1kV CU/XLPE/LSZH | 4C x 150sqmm + 1C X 95sqmm | PE-L1-5C150/95-03 | 106.8 | 400 | E | 190 | BSEDG | B0-EMCC-64602 | 400V EMERGENCY MCC FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B0-PP-43301C | DISTRIBUTION PANEL FOR BSEDG - C | 9_BLACK START DIESEL GENERATOR (CONTAINER TYPE) | L1, L2, L3, N, PE | B064-016BT0037 → B064-016BT0038 → B064-016BT0249 → B064-016BT0250 → B064-016BT0061 → B064-016BT0062 → B064-016BT0305 → B064-016BT0306 → B064-016BT0307 → B064-016BT0105 → B064-996BT0027 → M0509 → D0507-L36 → M0524 → D0509-L22 → M0511 → D0510-L22 → M0512 → D0511-L22 → M0513 → D0520-L11 → B043-016LVT0003 → END
B0-EMCC-64602 | -P20 | 02 | 재배정 | PE-L1-5C150/95-02 | PE-L1-5C150/95-03 | EDG-C-011 |  | DONE | 1 | 692 | B0-EMCC-64602-P2002 | 0.6/1kV CU/XLPE/LSZH | 4C x 150sqmm + 1C X 95sqmm | PE-L1-5C150/95-03 | 106.8 | 400 | E | 200 | BSEDG | B0-EMCC-64602 | 400V EMERGENCY MCC FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B0-PP-43301D | DISTRIBUTION PANEL FOR BSEDG - D | 9_BLACK START DIESEL GENERATOR (CONTAINER TYPE) | L1, L2, L3, N, PE | B064-016BT0037 → B064-016BT0038 → B064-016BT0249 → B064-016BT0250 → B064-016BT0061 → B064-016BT0062 → B064-016BT0305 → B064-016BT0306 → B064-016BT0307 → B064-016BT0105 → B064-996BT0027 → M0509 → D0507-L37 → M0524 → D0509-L23 → M0511 → D0510-L23 → M0512 → D0511-L23 → M0513 → D0512-L13 → M0514 → D0521-L11 → B043-016LVT0004 → END
B0-UPSP-64701 | -P20 | 02 |  | PE-L1-3C25/16-01 | PE-L1-3C25/16-01 | EDG-C-015 |  | DONE | 1 | 693 | B0-UPSP-64701-P2002 | 0.6/1kV CU/XLPE/LSZH | 2C x 25sqmm + 1C X 16sqmm | PE-L1-3C25/16-01 | 3 | 230 | U | 270 | BSEDG | B0-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-PMS-43301 | UPS-A FOR BSEDG MASTER PLC PANEL | 9_BLACK START DIESEL GENERATOR (CONTAINER TYPE) | L1, N, PE | B064-006FT0205 → B064-006FT0003 → B064-006AC0006 → M0501 → B064-996BT0020 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → B064-016BT0037 → B064-016BT0038 → B064-016BT0249 → B064-016BT0250 → B064-016BT0061 → B064-016BT0062 → B064-016BT0305 → B064-016BT0306 → B064-016BT0307 → B064-016BT0105 → B064-996BT0027 → M0509 → D0507-L27 → M0524 → D0509-L23 → M0511 → D0510-L23 → M0512 → D0511-L23 → M0513 → D0512-L13 → M0514 → D0513-L11 → M0515 → D0522-L13 → B043-011LVT0005 → END
B0-UPSP-64702 | -P20 | 03 |  | PE-L1-3C25/16-01 | PE-L1-3C25/16-01 | EDG-C-015-001 |  | DONE | 1 | 694 | B0-UPSP-64702-P2003 | 0.6/1kV CU/XLPE/LSZH | 2C x 25sqmm + 1C X 16sqmm | PE-L1-3C25/16-01 | 3 | 230 | U | 290 | BSEDG | B0-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-PMS-43301 | UPS-B FOR BSEDG MASTER PLC PANEL | 9_BLACK START DIESEL GENERATOR (CONTAINER TYPE) | L1, N, PE | B164-006HT0206 → B164-006HT0205 → B164-006HT0004 → B164-006HT0005 → B064-006AC0006 → M0501 → B064-996AT0120 → B064-016AT0032 → B064-016AT0213 → B064-016AT0214 → B064-016AT0215 → B064-016AT0073 → B064-016AT0074 → B064-016AT0075 → B064-016AT0076 → B064-016AT0077 → B064-016AT0078 → B064-016AT0079 → B064-016AT0080 → B064-016AT0081 → B064-016AT0082 → B064-016AT0307 → B064-016AT0308 → B064-016AT0113 → B064-996AT0025 → M0509 → D0507-L35 → M0524 → D0509-L21 → M0511 → D0510-L21 → M0512 → D0511-L21 → M0513 → D0512-L21 → M0514 → D0513-L11 → M0515 → D0522-L13 → B043-011LVT0005 → END
B0-DCP-64701 | -P20 | 01 |  | PE-L1-2C50-01 | PE-L1-2C50-01 | EDG-C-016 |  | DONE | 1 | 695 | B0-DCP-64701-P2001 | 0.6/1kV CU/XLPE/LSZH | 2C x 50sqmm | PE-L1-2C50-01 | 7 | 220 | D | 270 | BSEDG | B0-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B0-PMS-43301 | DC-A FOR BSEDG MASTER PLC PANEL | 9_BLACK START DIESEL GENERATOR (CONTAINER TYPE) | L+, L- | B164-006GT0207 → B164-006GT0005 → B064-006AC0005 → M0501 → B064-996BT0020 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → B064-016BT0037 → B064-016BT0038 → B064-016BT0249 → B064-016BT0250 → B064-016BT0061 → B064-016BT0062 → B064-016BT0305 → B064-016BT0306 → B064-016BT0307 → B064-016BT0105 → B064-996BT0027 → M0509 → D0507-L36 → M0524 → D0509-L22 → M0511 → D0510-L22 → M0512 → D0511-L22 → M0513 → D0512-L21 → M0514 → D0513-L11 → M0515 → D0522-L13 → B043-011LVT0005 → END
B0-DCP-64702 | -P20 | 01 |  | PE-L1-2C50-01 | PE-L1-2C50-01 | EDG-C-017 |  | DONE | 1 | 696 | B0-DCP-64702-P2001 | 0.6/1kV CU/XLPE/LSZH | 2C x 50sqmm | PE-L1-2C50-01 | 7 | 220 | D | 280 | BSEDG | B0-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B0-PMS-43301 | DC-B FOR BSEDG MASTER PLC PANEL | 9_BLACK START DIESEL GENERATOR (CONTAINER TYPE) | L+, L- | B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0005 → M0501 → B064-996AT0120 → B064-016AT0032 → B064-016AT0213 → B064-016AT0214 → B064-016AT0215 → B064-016AT0073 → B064-016AT0074 → B064-016AT0075 → B064-016AT0076 → B064-016AT0077 → B064-016AT0078 → B064-016AT0079 → B064-016AT0080 → B064-016AT0081 → B064-016AT0082 → B064-016AT0307 → B064-016AT0308 → B064-016AT0113 → B064-996AT0025 → M0509 → D0507-L37 → M0524 → D0509-L23 → M0511 → D0510-L23 → M0512 → D0511-L23 → M0513 → D0512-L13 → M0514 → D0513-L11 → M0515 → D0522-L13 → B043-011LVT0005 → END
B0-EMCC-64601 | -P20 | 03 |  | PE-L1-5C50/25-02 | PE-L1-5C50/25-02 | EDG-C-018 |  | DONE | 1 | 697 | B0-EMCC-64601-P2003 | 0.6/1kV CU/XLPE/LSZH | 4C x 50sqmm + 1C X 25sqmm | PE-L1-5C50/25-02 | 28.2 | 400 | E | 240 | BSEDG | B0-EMCC-64601 | 400V EMERGENCY MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B0-PP-43302 | DISTRIBUTION PANEL FOR MASTER PLC | 9_BLACK START DIESEL GENERATOR (CONTAINER TYPE) | L1, L2, L3, N, PE | B064-016BT0015 → B064-016BT0016 → B064-016BT0309 → B064-016BT0038 → B064-016BT0249 → B064-016BT0250 → B064-016BT0061 → B064-016BT0062 → B064-016BT0305 → B064-016BT0306 → B064-016BT0307 → B064-016BT0105 → B064-996BT0027 → M0509 → D0507-L37 → M0524 → D0509-L23 → M0511 → D0510-L23 → M0512 → D0511-L23 → M0513 → D0512-L13 → M0514 → D0513-L11 → M0515 → D0522-L13 → B043-016LVT0005 → END
B1-SWG-64602 | -P20 | 01 |  | PE-L1-4C70/35-05 | PE-L1-4C70/35-05 | CCW-C-0001 | DONE(10/6) | DONE | 1 | 698 | B1-SWG-64602-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 70sqmm + 1C X 35sqmm | PE-L1-4C70/35-05 | 160 | 400 | N | 200 | CLOSED COOLING WATER | B1-SWG-64602 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-M-32001A | CLOSED COOLING WATER PUMP #1-1 | 8.1_CCW PUMP/HEAT EXCHANGER BUILDING | L1, L2, L3, PE | B164-016AT0115 → B164-016AT0114 → B164-016AT0217 → B164-016AT0090 → B164-016AT0216 → B164-016AT0215 → B164-016AT0055 → B164-016AT0056 → B164-016AT0057 → B164-016AT0058 → B164-016AT0059 → B164-016AT0060 → B164-016AT0254 → B164-016AT0253 → B164-996AT0021 → M0505 → D0524-L11 → M0506 → D0505-L11 → M0507 → D0506-L11 → M0508 → B132-006AC0059 → END
B1-SWG-64602 | -P20 | 02 |  | PE-L1-4C70/35-05 | PE-L1-4C70/35-05 |  | DONE(10/6) | DONE | 1 | 699 | B1-SWG-64602-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 70sqmm + 1C X 35sqmm | PE-L1-4C70/35-05 | 160 | 400 | N | 200 | CLOSED COOLING WATER | B1-SWG-64602 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-M-32001A | CLOSED COOLING WATER PUMP #1-1 | 8.1_CCW PUMP/HEAT EXCHANGER BUILDING | L1, L2, L3, PE | B164-016AT0115 → B164-016AT0114 → B164-016AT0217 → B164-016AT0090 → B164-016AT0216 → B164-016AT0215 → B164-016AT0055 → B164-016AT0056 → B164-016AT0057 → B164-016AT0058 → B164-016AT0059 → B164-016AT0060 → B164-016AT0254 → B164-016AT0253 → B164-996AT0021 → M0505 → D0524-L11 → M0506 → D0505-L11 → M0507 → D0506-L11 → M0508 → B132-006AC0059 → END
B1-SWG-64602 | -P20 | 03 |  | PE-L1-3C4-12 | PE-L1-3C4-12 | CCW-C-0004 | DONE(10/6) | DONE | 1 | 700 | B1-SWG-64602-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-12 | 0.2 | 230 | N | 200 | CLOSED COOLING WATER | B1-SWG-64602 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-M-32001A | CLOSED COOLING WATER PUMP #1-1_SPACE HEATER | 8.1_CCW PUMP/HEAT EXCHANGER BUILDING | L1, N, PE | B164-016AT0115 → B164-016AT0114 → B164-016AT0217 → B164-016AT0090 → B164-016AT0216 → B164-016AT0215 → B164-016AT0055 → B164-016AT0056 → B164-016AT0057 → B164-016AT0058 → B164-016AT0059 → B164-016AT0060 → B164-016AT0254 → B164-016AT0253 → B164-996AT0021 → M0505 → D0524-L11 → M0506 → D0505-L11 → M0507 → D0506-L11 → M0508 → B132-007AC0053 → END
B1-SWG-64601 | -P20 | 08 |  | PE-L1-4C70/35-05 | PE-L1-4C70/35-05 | CCW-C-0002 | DONE(10/6) | DONE | 1 | 701 | B1-SWG-64601-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 70sqmm + 1C X 35sqmm | PE-L1-4C70/35-05 | 160 | 400 | N | 200 | CLOSED COOLING WATER | B1-SWG-64601 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-M-32001B | CLOSED COOLING WATER PUMP #1-2 | 8.1_CCW PUMP/HEAT EXCHANGER BUILDING | L1, L2, L3, PE | B164-016AT0090 → B164-016AT0216 → B164-016AT0215 → B164-016AT0055 → B164-016AT0056 → B164-016AT0057 → B164-016AT0058 → B164-016AT0059 → B164-016AT0060 → B164-016AT0254 → B164-016AT0253 → B164-016AT0252 → B164-996AT0021 → M0505 → D0524-L12 → M0506 → D0505-L12 → M0507 → D0506-L12 → M0508 → B132-006AC0056 → END
B1-SWG-64601 | -P20 | 09 |  | PE-L1-4C70/35-04 | PE-L1-4C70/35-04 |  | DONE(10/6) | DONE | 1 | 702 | B1-SWG-64601-P2009 | 0.6/1kV CU/XLPE/LSZH | 3C x 70sqmm + 1C X 35sqmm | PE-L1-4C70/35-04 | 160 | 400 | N | 190 | CLOSED COOLING WATER | B1-SWG-64601 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-M-32001B | CLOSED COOLING WATER PUMP #1-2 | 8.1_CCW PUMP/HEAT EXCHANGER BUILDING | L1, L2, L3, PE | B164-016AT0090 → B164-016AT0216 → B164-016AT0215 → B164-016AT0055 → B164-016AT0056 → B164-016AT0057 → B164-016AT0058 → B164-016AT0059 → B164-016AT0060 → B164-016AT0254 → B164-016AT0253 → M0505 → D0524-L12 → M0506 → D0505-L12 → M0507 → D0506-L12 → M0508 → B132-006AC0057 → END
B1-SWG-64601 | -P20 | 10 |  | PE-L1-3C4-12 | PE-L1-3C4-12 | CCW-C-0005 | DONE(10/6) | DONE | 1 | 703 | B1-SWG-64601-P2010 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-12 | 0.2 | 230 | N | 200 | CLOSED COOLING WATER | B1-SWG-64601 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-M-32001B | CLOSED COOLING WATER PUMP #1-2_SPACE HEATER | 8.1_CCW PUMP/HEAT EXCHANGER BUILDING | L1, N, PE | B164-016AT0090 → B164-016AT0216 → B164-016AT0215 → B164-016AT0055 → B164-016AT0056 → B164-016AT0057 → B164-016AT0058 → B164-016AT0059 → B164-016AT0060 → B164-016AT0254 → B164-016AT0253 → B164-016AT0252 → B164-996AT0021 → M0505 → D0524-L12 → M0506 → D0505-L12 → M0507 → D0506-L12 → M0508 → B132-007AC0052 → END
B1-SWG-64602 | -P20 | 04 |  | PE-L1-4C70/35-06 | PE-L1-4C70/35-06 | CCW-C-0003 | DONE(10/6) | DONE | 1 | 704 | B1-SWG-64602-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 70sqmm + 1C X 35sqmm | PE-L1-4C70/35-06 | 160 | 400 | N | 230 | CLOSED COOLING WATER | B1-SWG-64602 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-M-32001C | CLOSED COOLING WATER PUMP #1-3 | 8.1_CCW PUMP/HEAT EXCHANGER BUILDING | L1, L2, L3, PE | B064-016AT0106 → B064-016AT0217 → B064-016AT0090 → B064-016AT0091 → B064-016AT0092 → B064-016AT0093 → B064-016AT0278 → B064-016AT0077 → B064-016AT0078 → B064-016AT0079 → B064-016AT0080 → B064-016AT0081 → B064-016AT0082 → B064-016AT0306 → B064-016AT0072 → B064-016AT0312 → B064-016AT0051 → B064-016AT0245 → B064-016AT0309 → B064-016AT0017 → B064-016AT0251 → B064-996AT0021 → M0505 → D0524-L13 → M0506 → D0505-L13 → M0507 → D0506-L13 → M0508 → B132-006AC0053 → END
B1-SWG-64602 | -P20 | 05 |  | PE-L1-4C70/35-06 | PE-L1-4C70/35-06 |  | DONE(10/6) | DONE | 1 | 705 | B1-SWG-64602-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 70sqmm + 1C X 35sqmm | PE-L1-4C70/35-06 | 160 | 400 | N | 230 | CLOSED COOLING WATER | B1-SWG-64602 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-M-32001C | CLOSED COOLING WATER PUMP #1-3 | 8.1_CCW PUMP/HEAT EXCHANGER BUILDING | L1, L2, L3, PE | B064-016AT0106 → B064-016AT0217 → B064-016AT0090 → B064-016AT0091 → B064-016AT0092 → B064-016AT0093 → B064-016AT0278 → B064-016AT0077 → B064-016AT0078 → B064-016AT0079 → B064-016AT0080 → B064-016AT0081 → B064-016AT0082 → B064-016AT0306 → B064-016AT0072 → B064-016AT0312 → B064-016AT0051 → B064-016AT0245 → B064-016AT0309 → B064-016AT0017 → B064-016AT0251 → B064-996AT0021 → M0505 → D0524-L13 → M0506 → D0505-L13 → M0507 → D0506-L13 → M0508 → B132-006AC0054 → END
B1-SWG-64602 | -P20 | 06 |  | PE-L1-3C4-25 | PE-L1-3C4-25 | CCW-C-0006 | DONE(10/6) | DONE | 1 | 706 | B1-SWG-64602-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-25 | 0.2 | 230 | N | 210 | CLOSED COOLING WATER | B1-SWG-64602 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-M-32001C | CLOSED COOLING WATER PUMP #1-3_SPACE HEATER | 8.1_CCW PUMP/HEAT EXCHANGER BUILDING | L1, N, PE | B164-016AT0115 → B164-016AT0114 → B164-016AT0217 → B164-016AT0090 → B164-016AT0216 → B164-016AT0215 → B164-016AT0055 → B164-016AT0056 → B164-016AT0057 → B164-016AT0058 → B164-016AT0059 → B164-016AT0060 → B164-016AT0254 → B164-016AT0253 → B164-996AT0021 → M0505 → D0524-L13 → M0506 → D0505-L13 → M0507 → D0506-L13 → M0508 → B132-007AC0051 → END
B1-MCC-64602 | -P20 | 24 |  | PE-L1-4C4-07 | PE-L1-4C4-07 | CCW-C-0007 | DONE(10/6) | DONE | 1 | 707 | B1-MCC-64602-P2024 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-07 | 0.75 | 400 | N | 200 | CLOSED COOLING WATER | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-32001 | MOV CCWP DISCHARGE #1-1 | 8.1_CCW PUMP/HEAT EXCHANGER BUILDING | L1, L2, L3, PE | B164-016AT0115 → B164-016AT0114 → B164-016AT0217 → B164-016AT0090 → B164-016AT0216 → B164-016AT0215 → B164-016AT0055 → B164-016AT0056 → B164-016AT0057 → B164-016AT0058 → B164-016AT0059 → B164-016AT0060 → B164-016AT0254 → B164-016AT0253 → B164-016AT0252 → B164-996AT0021 → M0505 → D0524-L11 → M0506 → D0505-L11 → M0507 → D0506-L11 → M0508 → B132-006AC0058 → END
B1-MCC-64601 | -P20 | 18 |  | PE-L1-4C4-07 | PE-L1-4C4-07 | CCW-C-0008 | DONE(10/6) | DONE | 1 | 708 | B1-MCC-64601-P2018 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-07 | 0.75 | 400 | N | 190 | CLOSED COOLING WATER | B1-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-32002 | MOV CCWP DISCHARGE #1-2 | 8.1_CCW PUMP/HEAT EXCHANGER BUILDING | L1, L2, L3, PE | B164-016AT0090 → B164-016AT0216 → B164-016AT0215 → B164-016AT0055 → B164-016AT0056 → B164-016AT0057 → B164-016AT0058 → B164-016AT0059 → B164-016AT0060 → B164-016AT0254 → B164-016AT0253 → B164-016AT0252 → B164-996AT0021 → M0505 → D0524-L12 → M0506 → D0505-L12 → M0507 → D0506-L12 → M0508 → B132-006AC0055 → END
B1-MCC-64602 | -P20 | 25 |  | PE-L1-4C4-07 | PE-L1-4C4-07 | CCW-C-0009 | DONE(10/6) | DONE | 1 | 709 | B1-MCC-64602-P2025 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-07 | 0.75 | 400 | N | 210 | CLOSED COOLING WATER | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-32003 | MOV CCWP DISCHARGE #1-3 | 8.1_CCW PUMP/HEAT EXCHANGER BUILDING | L1, L2, L3, PE | B164-016AT0115 → B164-016AT0114 → B164-016AT0217 → B164-016AT0090 → B164-016AT0216 → B164-016AT0215 → B164-016AT0055 → B164-016AT0056 → B164-016AT0057 → B164-016AT0058 → B164-016AT0059 → B164-016AT0060 → B164-016AT0254 → B164-016AT0253 → B164-016AT0252 → B164-996AT0021 → M0505 → D0524-L13 → M0506 → D0505-L13 → M0507 → D0506-L13 → M0508 → B132-006AC0052 → END
B1-MCC-64602 | -P20 | 26 |  | PE-L1-4C4-08 | PE-L1-4C4-08 | CCW-C-0014 | DONE(9/28) | DONE | 1 | 710 | B1-MCC-64602-P2026 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-08 | 0.2 | 400 | N | 230 | CLOSED COOLING WATER | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-32005 | MOV CCW HEAD TANK MAKE UP #1 | 1.1_MAIN BUILDING COMPLEX | L1, L2, L3, PE | B164-016ET0106 → B164-996ET0022 → M0504 → D0531-L32 → M0510 → D0517-L23 → M0501 → D0503-L42 → M0502 → D0504-L42 → M0503 → D0501-L42 → M0328 → D0324-L42 → M0329 → B114-996BT0046 → B114-016BT0045 → B114-016BT0044 → B161-016AC0017 → END
B1-MCC-64601 | -P20 | 19 |  | PE-L1-4C4-08 | PE-L1-4C4-08 | CCW-C-0015 | DONE(10/12) | DONE | 1 | 711 | B1-MCC-64601-P2019 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-08 | 0.75 | 400 | N | 190 | CLOSED COOLING WATER | B1-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-32004 | CCW H/E BYPASS #1 | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, PE | B164-016AT0091 → B164-996AT0022 → M0504 → D0531-L37 → M0510 → D0517-L25 → M0501 → D0503-L47 → M0502 → D0504-L47 → M0503 → B132-006AC0005 → B182-017AT0001 → B182-037AT0002 → B182-037AT0003 → B182-037AT0004 → B182-037AT0005 → B132-006AC0001 → END
B2-SWG-64602 | -P20 | 01 |  | PE-L1-4C70/35-06 | PE-L1-4C70/35-06 | CCW-C-0016 |  |  | 1 | 712 | B2-SWG-64602-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 70sqmm + 1C X 35sqmm | PE-L1-4C70/35-06 | 160 | 400 | N | 150 | CLOSED COOLING WATER | B2-SWG-64602 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-M-32001A | CLOSED COOLING WATER PUMP #2-1 | 8.2_CCW PUMP/HEAT EXCHANGER BUILDING | L1, L2, L3, PE | B264-016BT0046 → B264-016BT0209 → B264-016BT0025 → B264-016BT0206 → B264-996BT0001 → M0401 → D0403-L11 → M0402 → D0402-L11 → M0424 → D0401-L11 → M0404 → B232-006AC0059 → END
B2-SWG-64602 | -P20 | 02 |  | PE-L1-4C70/35-06 | PE-L1-4C70/35-06 |  |  |  | 1 | 713 | B2-SWG-64602-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 70sqmm + 1C X 35sqmm | PE-L1-4C70/35-06 | 160 | 400 | N | 150 | CLOSED COOLING WATER | B2-SWG-64602 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-M-32001A | CLOSED COOLING WATER PUMP #2-1 | 8.2_CCW PUMP/HEAT EXCHANGER BUILDING | L1, L2, L3, PE | B264-016BT0046 → B264-016BT0209 → B264-016BT0025 → B264-016BT0206 → B264-996BT0001 → M0401 → D0403-L11 → M0402 → D0402-L11 → M0424 → D0401-L11 → M0404 → B232-006AC0060 → END
B2-SWG-64602 | -P20 | 03 |  | PE-L1-3C4-13 | PE-L1-3C4-13 | CCW-C-0019 |  |  | 1 | 714 | B2-SWG-64602-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-13 | 0.2 | 230 | N | 150 | CLOSED COOLING WATER | B2-SWG-64602 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-M-32001A | CLOSED COOLING WATER PUMP #2-1_SPACE HEATER | 8.2_CCW PUMP/HEAT EXCHANGER BUILDING | L1, N, PE | B264-016BT0046 → B264-016BT0209 → B264-016BT0025 → B264-016BT0206 → B264-996BT0001 → M0401 → D0403-L11 → M0402 → D0402-L11 → M0424 → D0401-L11 → M0404 → B232-007AC0053 → END
B2-SWG-64601 | -P20 | 08 |  | PE-L1-4C70/35-06 | PE-L1-4C70/35-06 | CCW-C-0017 |  |  | 1 | 715 | B2-SWG-64601-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 70sqmm + 1C X 35sqmm | PE-L1-4C70/35-06 | 160 | 400 | N | 140 | CLOSED COOLING WATER | B2-SWG-64601 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-M-32001B | CLOSED COOLING WATER PUMP #2-2 | 8.2_CCW PUMP/HEAT EXCHANGER BUILDING | L1, L2, L3, PE | B264-016BT0025 → B264-016BT0206 → B264-996BT0001 → M0401 → D0403-L12 → M0402 → D0402-L12 → M0424 → D0401-L12 → M0404 → B232-006AC0056 → END
B2-SWG-64601 | -P20 | 09 |  | PE-L1-4C70/35-04 | PE-L1-4C70/35-04 |  |  |  | 1 | 716 | B2-SWG-64601-P2009 | 0.6/1kV CU/XLPE/LSZH | 3C x 70sqmm + 1C X 35sqmm | PE-L1-4C70/35-04 | 160 | 400 | N | 140 | CLOSED COOLING WATER | B2-SWG-64601 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-M-32001B | CLOSED COOLING WATER PUMP #2-2 | 8.2_CCW PUMP/HEAT EXCHANGER BUILDING | L1, L2, L3, PE | B264-016AT0025 → B264-016AT0206 → B264-996AT0001 → M0401 → D0403-L12 → M0402 → D0402-L12 → M0424 → D0401-L12 → M0404 → B232-006AC0057 → END
B2-SWG-64601 | -P20 | 10 |  | PE-L1-3C4-13 | PE-L1-3C4-13 | CCW-C-0020 |  |  | 1 | 717 | B2-SWG-64601-P2010 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-13 | 0.2 | 230 | N | 140 | CLOSED COOLING WATER | B2-SWG-64601 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-M-32001B | CLOSED COOLING WATER PUMP #2-2_SPACE HEATER | 8.2_CCW PUMP/HEAT EXCHANGER BUILDING | L1, N, PE | B264-016AT0025 → B264-016AT0206 → B264-996AT0001 → M0401 → D0403-L12 → M0402 → D0402-L12 → M0424 → D0401-L12 → M0404 → B232-007AC0052 → END
B2-SWG-64602 | -P20 | 04 |  | PE-L1-4C70/35-01 | PE-L1-4C70/35-01 | CCW-C-0018 |  |  | 1 | 718 | B2-SWG-64602-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 70sqmm + 1C X 35sqmm | PE-L1-4C70/35-01 | 160 | 400 | N | 160 | CLOSED COOLING WATER | B2-SWG-64602 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-M-32001C | CLOSED COOLING WATER PUMP #2-3 | 8.2_CCW PUMP/HEAT EXCHANGER BUILDING | L1, L2, L3, PE | B264-016AT0046 → B264-016AT0209 → B264-016AT0025 → B264-016AT0206 → B264-996AT0001 → M0401 → D0403-L13 → M0402 → D0402-L13 → M0424 → D0401-L13 → M0404 → B232-006AC0053 → END
B2-SWG-64602 | -P20 | 05 |  | PE-L1-4C70/35-02 | PE-L1-4C70/35-02 |  |  |  | 1 | 719 | B2-SWG-64602-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 70sqmm + 1C X 35sqmm | PE-L1-4C70/35-02 | 160 | 400 | N | 160 | CLOSED COOLING WATER | B2-SWG-64602 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-M-32001C | CLOSED COOLING WATER PUMP #2-3 | 8.2_CCW PUMP/HEAT EXCHANGER BUILDING | L1, L2, L3, PE | B264-016BT0046 → B264-016BT0209 → B264-016BT0025 → B264-016BT0206 → B264-996BT0001 → M0401 → D0403-L13 → M0402 → D0402-L13 → M0424 → D0401-L13 → M0404 → B232-006AC0054 → END
B2-SWG-64602 | -P20 | 06 |  | PE-L1-3C4-13 | PE-L1-3C4-13 | CCW-C-0021 |  |  | 1 | 720 | B2-SWG-64602-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-13 | 0.2 | 230 | N | 160 | CLOSED COOLING WATER | B2-SWG-64602 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-M-32001C | CLOSED COOLING WATER PUMP #2-3_SPACE HEATER | 8.2_CCW PUMP/HEAT EXCHANGER BUILDING | L1, N, PE | B264-016BT0046 → B264-016BT0209 → B264-016BT0025 → B264-016BT0206 → B264-996BT0001 → M0401 → D0403-L13 → M0402 → D0402-L13 → M0424 → D0401-L13 → M0404 → B232-007AC0051 → END
B2-MCC-64602 | -P20 | 22 |  | PE-L1-4C4-08 | PE-L1-4C4-08 | CCW-C-0022 |  |  | 1 | 721 | B2-MCC-64602-P2022 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-08 | 0.75 | 400 | N | 150 | CLOSED COOLING WATER | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-32001 | MOV CCWP DISCHARGE #2-1 | 8.2_CCW PUMP/HEAT EXCHANGER BUILDING | L1, L2, L3, PE | B264-016BT0045 → B264-016BT0205 → B264-016BT0024 → B264-016BT0206 → B264-996BT0001 → M0401 → D0403-L11 → M0402 → D0402-L11 → M0424 → D0401-L11 → M0404 → B232-006AC0058 → END
B2-MCC-64601 | -P20 | 20 |  | PE-L1-4C4-15 | PE-L1-4C4-15 | CCW-C-0023 |  |  | 1 | 722 | B2-MCC-64601-P2020 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-15 | 0.75 | 400 | N | 150 | CLOSED COOLING WATER | B2-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-32002 | MOV CCWP DISCHARGE #2-2 | 8.2_CCW PUMP/HEAT EXCHANGER BUILDING | L1, L2, L3, PE | B264-016AT0025 → B264-016AT0206 → B264-996AT0001 → M0401 → D0403-L12 → M0402 → D0402-L12 → M0424 → D0401-L12 → M0404 → B232-006AC0055 → END
B2-MCC-64602 | -P20 | 23 |  | PE-L1-4C4-21 | PE-L1-4C4-21 | CCW-C-0024 |  |  | 1 | 723 | B2-MCC-64602-P2023 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-21 | 0.75 | 400 | N | 160 | CLOSED COOLING WATER | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-32003 | MOV CCWP DISCHARGE #2-3 | 8.2_CCW PUMP/HEAT EXCHANGER BUILDING | L1, L2, L3, PE | B264-016BT0045 → B264-016BT0205 → B264-016BT0024 → B264-016BT0206 → B264-996BT0001 → M0401 → D0403-L13 → M0402 → D0402-L13 → M0424 → D0401-L13 → M0404 → B232-006AC0052 → END
B2-MCC-64602 | -P20 | 24 |  | PE-L1-4C4-21 | PE-L1-4C4-21 | CCW-C-0029 |  |  | 1 | 724 | B2-MCC-64602-P2024 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-21 | 0.2 | 400 | N | 300 | CLOSED COOLING WATER | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-32005 | MOV CCW HEAD TANK MAKE UP #2 | 1.1_MAIN BUILDING COMPLEX | L1, L2, L3, PE | B264-016AT0045 → B264-016AT0046 → B264-016AT0209 → B264-016AT0026 → B264-016AT0027 → B264-016AT0225 → B264-996AT0011 → M0405 → D0421-L33 → M0406 → D0301-L35 → M0301 → B215-996BT0001 → B215-016BT0002 → B215-016BT0003 → B215-016BT0004 → B215-016BT0005 → B215-016BT0031 → B215-016BT0032 → B261-016AC0009 → END
B2-MCC-64601 | -P20 | 21 |  | PE-L1-4C4-26 | PE-L1-4C4-26 | CCW-C-0030 |  |  | 1 | 725 | B2-MCC-64601-P2021 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-26 | 0.75 | 400 | N | 200 | CLOSED COOLING WATER | B2-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-32004 | CCW H/E BYPASS #2 | 7.2_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, L2, L3, PE | B264-016AT0025 → B264-016AT0206 → B264-996AT0001 → M0401 → D0403-L14 → M0402 → D0402-L14 → M0424 → D0422-L12 → M0403 → B232-006AC0005 → B282-017AT0001 → B282-037AT0002 → B282-037AT0003 → B282-037AT0004 → B282-037AT0005 → B232-006AC0001 → END
B0-MCC-49601 | -P20 | 28 |  | PE-L1-4C4-08 | PE-L1-4C4-08 | DWST-C-001 |  |  | 1 | 726 | B0-MCC-49601-P2028 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-08 | 0.4 | 400 | N | 320 | DEMINERALIZED WATER STORAGE AND TRANSFER SYSTEM | B0-MCC-49601 | 400V MCC FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-MOV-35001 | DEMI PLANT TO DEMI WATER TANK A INLET MOV | 15.4_DEMI WATER STORAGE TANK | L1, L2, L3, PE | B049-006AT0004 → B049-006AT0003 → B049-006AT0002 → D0204-L18 → M0207 → D0203-L23 → M0206 → D0205-L24 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B025-016ET0030 → B025-016ET0031 → B079-016AC0001 → B079-006AC0014 → B079-006AC0015 → B079-006AC0017 → END
B0-MCC-49602 | -P20 | 26 |  | PE-L1-4C4-08 | PE-L1-4C4-08 | DWST-C-002 |  |  | 1 | 727 | B0-MCC-49602-P2026 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-08 | 0.4 | 400 | N | 320 | DEMINERALIZED WATER STORAGE AND TRANSFER SYSTEM | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, PE | B0-MOV-35002 | DEMI PLANT TO DEMI WATER TANK B INLET MOV | 15.5_DEMI WATER STORAGE TANK | L1, L2, L3, PE | B049-006BT0008 → B169-006AT0016 → B169-006AT0053 → B169-006AT0008 → B049-006BT0001 → D0204-L18 → M0207 → D0203-L23 → M0206 → D0205-L24 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B025-016ET0030 → B025-016ET0031 → B079-016AC0001 → B079-006AC0014 → B079-006AC0015 → B079-006AC0016 → END
B1-MCC-69601 | -P20 | 08 |  | PE-L1-4C4-08 | PE-L1-4C4-08 | COD-B1-001 |  |  | 1 | 728 | B1-MCC-69601-P2008 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-08 | 0.75 | 400 | N | 40 | CONDENSATE SYSTEM | B1-MCC-69601 | 400V MCC FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-MOV-29001 | #1 CONDENSATE EXTRACTION PUMP A DISCHARGE MOV | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-006AT0016 → B169-006AT0053 → B169-006AT0008 → B016-006AC0010 → END
B1-MCC-69603 | -P20 | 10 |  | PE-L1-4C4-07 | PE-L1-4C4-07 | COD-B1-002 |  |  | 1 | 729 | B1-MCC-69603-P2010 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-07 | 0.75 | 400 | N | 30 | CONDENSATE SYSTEM | B1-MCC-69603 | 400V MCC FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-MOV-29002 | #1 CONDENSATE EXTRACTION PUMP B DISCHARGE MOV | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-006AT0009 → B016-006AC0009 → END
B1-MCC-69601 | -P20 | 09 |  | PE-L1-4C4-08 | PE-L1-4C4-08 | COD-B1-003 |  |  | 1 | 730 | B1-MCC-69601-P2009 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-08 | 0.75 | 400 | N | 50 | CONDENSATE SYSTEM | B1-MCC-69601 | 400V MCC FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B1-MOV-29003 | #1 CONDENSATE EXTRACTION PUMP C DISCHARGE MOV | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-006AT0016 → B169-006AT0053 → B169-006AT0009 → B016-006AC0008 → END
B2-MCC-69601 | -P20 | 10 |  | PE-L1-4C4-11 | PE-L1-4C4-11 | COD-B2-001 |  |  | 1 | 731 | B2-MCC-69601-P2010 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-11 | 0.75 | 400 | N | 80 | CONDENSATE SYSTEM | B2-MCC-69601 | 400V MCC FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-MOV-29001 | #2 CONDENSATE EXTRACTION PUMP A DISCHARGE MOV | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-006AT0020 → B169-006AT0019 → B169-006AT0018 → B169-006AT0017 → B169-006AT0016 → B169-006AT0015 → B016-006BC0010 → END
B2-MCC-69603 | -P20 | 08 |  | PE-L1-4C4-11 | PE-L1-4C4-11 | COD-B2-002 |  |  | 1 | 732 | B2-MCC-69603-P2008 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-11 | 0.75 | 400 | N | 50 | CONDENSATE SYSTEM | B2-MCC-69603 | 400V MCC FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-MOV-29002 | #2 CONDENSATE EXTRACTION PUMP B DISCHARGE MOV | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-006AT0013 → B169-006AT0033 → B169-006AT0020 → B016-006BC0009 → END
B2-MCC-69601 | -P20 | 11 |  | PE-L1-4C4-18 | PE-L1-4C4-18 | COD-B2-003 |  |  | 1 | 733 | B2-MCC-69601-P2011 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-18 | 0.75 | 400 | N | 60 | CONDENSATE SYSTEM | B2-MCC-69601 | 400V MCC FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B2-MOV-29003 | #2 CONDENSATE EXTRACTION PUMP C DISCHARGE MOV | 16_CEP BUILDING W/ACC LER | L1, L2, L3, PE | B169-006AT0020 → B169-006AT0019 → B169-006AT0018 → B169-006AT0017 → B016-006BC0008 → END
B1-MCC-64601 | -P20 | 20 |  | PE-L1-4C4-08 | PE-L1-4C4-08 | BPSS-U1-003 |  |  | 1 | 734 | B1-MCC-64601-P2020 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-08 | 0.4 | 400 | N | 280 | STEAM | B1-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-26001 | HRSG #11 HP STEAM WARM-UP LINE DRAIN MOV (BEFORE CHECK V/V) | 1.1_MAIN BUILDING COMPLEX(HRSG#11) | L1, L2, L3, PE | B164-016AT0091 → B164-996AT0022 → M0504 → D0531-L35 → M0510 → D0517-L26 → M0501 → D0503-L45 → M0502 → D0504-L45 → M0503 → D0501-L45 → M0328 → D0324-L45 → M0329 → B114-996BT0046 → B114-016BT0045 → B114-016BT0044 → B114-016BT0043 → B114-016BT0042 → B161-016CC0035 → END
B1-MCC-64601 | -P20 | 21 |  | PE-L1-4C4-08 | PE-L1-4C4-08 | BPSS-U1-004 |  |  | 1 | 735 | B1-MCC-64601-P2021 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-08 | 0.4 | 400 | N | 290 | STEAM | B1-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-26003 | HRSG #11 HP STEAM WARM-UP LINE DRAIN MOV (AFTER CHECK V/V) | 1.1_MAIN BUILDING COMPLEX(HRSG#11) | L1, L2, L3, PE | B164-016AT0091 → B164-996AT0022 → M0504 → D0531-L34 → M0510 → D0517-L25 → M0501 → D0503-L44 → M0502 → D0504-L44 → M0503 → D0501-L44 → M0328 → D0324-L44 → M0329 → B114-996DT0081 → B114-016DT0082 → B114-016DT0083 → B114-016DT0084 → B114-016DT0096 → B114-016DT0097 → B161-016AC0007 → END
B1-MCC-64601 | -P20 | 22 |  | PE-L1-4C4-15 | PE-L1-4C4-15 | BPSS-U1-006 |  |  | 1 | 736 | B1-MCC-64601-P2022 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-15 | 0.4 | 400 | N | 290 | STEAM | B1-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-27001 | HRSG #11 LP STEAM WARM-UP LINE DRAIN MOV (BEFORE CHECK V/V) | 1.1_MAIN BUILDING COMPLEX(HRSG#11) | L1, L2, L3, PE | B164-016AT0091 → B164-996AT0022 → M0504 → D0531-L35 → M0510 → D0517-L26 → M0501 → D0503-L45 → M0502 → D0504-L45 → M0503 → D0501-L45 → M0328 → D0324-L45 → M0329 → B114-996DT0081 → B114-016DT0082 → B114-016DT0083 → B114-016DT0084 → B114-016DT0096 → B114-016DT0097 → B161-016AC0008 → END
B1-MCC-64601 | -P20 | 23 |  | PE-L1-4C4-15 | PE-L1-4C4-15 | BPSS-U1-007 |  |  | 1 | 737 | B1-MCC-64601-P2023 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-15 | 0.4 | 400 | N | 280 | STEAM | B1-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-27003 | HRSG #11 LP STEAM WARM-UP LINE DRAIN MOV (AFTER CHECK V/V) | 1.1_MAIN BUILDING COMPLEX(HRSG#11) | L1, L2, L3, PE | B164-016AT0091 → B164-996AT0022 → M0504 → D0531-L34 → M0510 → D0517-L25 → M0501 → D0503-L44 → M0502 → D0504-L44 → M0503 → D0501-L44 → M0328 → D0324-L44 → M0329 → B114-996DT0081 → B114-016DT0082 → B114-016DT0083 → B114-016DT0084 → B114-016DT0096 → B114-016DT0097 → B161-016AC0009 → END
B1-MCC-64603 | -P20 | 08 |  | PE-L1-4C4-15 | PE-L1-4C4-15 | BPSS-U2-004 |  |  | 1 | 738 | B1-MCC-64603-P2008 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-15 | 0.4 | 400 | N | 340 | STEAM | B1-MCC-64603 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-26004 | HRSG #12 HP STEAM WARM-UP LINE DRAIN MOV (AFTER CHECK V/V) | 1.1_MAIN BUILDING COMPLEX(HRSG#12) | L1, L2, L3, PE | B164-016AT0094 → B164-016AT0093 → B164-016AT0092 → B164-996AT0022 → M0504 → D0531-L34 → M0510 → D0517-L25 → M0501 → D0503-L44 → M0502 → D0504-L44 → M0503 → D0501-L44 → M0328 → D0324-L44 → M0329 → B114-996CT0071 → B114-016CT0072 → B114-016CT0073 → B114-016CT0074 → B114-016CT0075 → B114-016CT0076 → B114-016CT0087 → B161-016CC0028 → END
B1-MCC-64603 | -P20 | 09 |  | PE-L1-4C4-15 | PE-L1-4C4-15 | BPSS-U2-006 |  |  | 1 | 739 | B1-MCC-64603-P2009 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-15 | 0.4 | 400 | N | 340 | STEAM | B1-MCC-64603 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-27002 | HRSG #12 LP STEAM WARM-UP LINE DRAIN MOV (BEFORE CHECK V/V) | 1.1_MAIN BUILDING COMPLEX(HRSG#12) | L1, L2, L3, PE | B164-016AT0094 → B164-016AT0093 → B164-016AT0092 → B164-996AT0022 → M0504 → D0531-L35 → M0510 → D0517-L26 → M0501 → D0503-L45 → M0502 → D0504-L45 → M0503 → D0501-L45 → M0328 → D0324-L44 → M0329 → B114-996CT0071 → B114-016CT0072 → B114-016CT0073 → B114-016CT0074 → B114-016CT0075 → B114-016CT0076 → B114-016CT0087 → B161-016CC0029 → END
B1-MCC-64603 | -P20 | 10 |  | PE-L1-4C4-14 | PE-L1-4C4-14 | BPSS-U2-007 |  |  | 1 | 740 | B1-MCC-64603-P2010 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-14 | 0.4 | 400 | N | 340 | STEAM | B1-MCC-64603 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-27004 | HRSG #12 LP STEAM WARM-UP LINE DRAIN MOV (AFTER CHECK V/V) | 1.1_MAIN BUILDING COMPLEX(HRSG#12) | L1, L2, L3, PE | B164-016AT0094 → B164-016AT0093 → B164-016AT0092 → B164-996AT0022 → M0504 → D0531-L34 → M0510 → D0517-L25 → M0501 → D0503-L44 → M0502 → D0504-L44 → M0503 → D0501-L44 → M0328 → D0324-L44 → M0329 → B114-996CT0071 → B114-016CT0072 → B114-016CT0073 → B114-016CT0074 → B114-016CT0075 → B114-016CT0076 → B114-016CT0087 → B161-016CC0027 → END
B2-MCC-64601 | -P20 | 23 |  | PE-L1-4C4-18 | PE-L1-4C4-18 | BPSS-U3-004 |  |  | 1 | 741 | B2-MCC-64601-P2023 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-18 | 0.4 | 400 | N | 290 | STEAM | B2-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-26003 | HRSG #21 HP STEAM WARM-UP LINE DRAIN MOV (AFTER CHECK V/V) | 1.1_MAIN BUILDING COMPLEX(HRSG#21) | L1, L2, L3, PE | B264-016CT0024 → B264-016CT0025 → B264-016CT0026 → B264-016CT0027 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L26 → M0406 → D0301-L22 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B215-016AT0050 → B215-016AT0051 → B215-016AT0064 → B215-016AT0065 → B215-016AT0066 → B215-016AT0055 → B261-016CC0007 → END
B2-MCC-64601 | -P20 | 24 |  | PE-L1-4C4-17 | PE-L1-4C4-17 | BPSS-U3-006 |  |  | 1 | 742 | B2-MCC-64601-P2024 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-17 | 0.4 | 400 | N | 290 | STEAM | B2-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-27001 | HRSG #21 LP STEAM WARM-UP LINE DRAIN MOV (BEFORE CHECK V/V) | 1.1_MAIN BUILDING COMPLEX(HRSG#21) | L1, L2, L3, PE | B264-016CT0024 → B264-016CT0025 → B264-016CT0026 → B264-016CT0027 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L26 → M0406 → D0301-L22 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B215-016AT0050 → B215-016AT0051 → B215-016AT0064 → B215-016AT0065 → B215-016AT0066 → B215-016AT0055 → B215-016AT0056 → B261-016CC0008 → END
B2-MCC-64601 | -P20 | 25 |  | PE-L1-4C4-17 | PE-L1-4C4-17 | BPSS-U3-007 |  |  | 1 | 743 | B2-MCC-64601-P2025 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-17 | 0.4 | 400 | N | 290 | STEAM | B2-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-27003 | HRSG #21 LP STEAM WARM-UP LINE DRAIN MOV (AFTER CHECK V/V) | 1.1_MAIN BUILDING COMPLEX(HRSG#21) | L1, L2, L3, PE | B264-016CT0024 → B264-016CT0025 → B264-016CT0026 → B264-016CT0027 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L26 → M0406 → D0301-L22 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B215-016AT0050 → B215-016AT0051 → B215-016AT0064 → B215-016AT0065 → B215-016AT0066 → B215-016AT0055 → B261-016CC0009 → END
B2-MCC-64604 | -P20 | 05 |  | PE-L1-4C4-26 | PE-L1-4C4-26 | BPSS-U4-003 |  |  | 1 | 744 | B2-MCC-64604-P2005 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-26 | 0.4 | 400 | N | 270 | STEAM | B2-MCC-64604 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-26002 | HRSG #22 HP STEAM WARM-UP LINE DRAIN MOV (BEFORE CHECK V/V) | 1.1_MAIN BUILDING COMPLEX(HRSG#22) | L1, L2, L3, PE | B264-016CT0047 → B264-016CT0048 → B264-016CT0235 → B264-016CT0029 → B264-016CT0028 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L27 → M0406 → D0301-L21 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B215-016AT0050 → B215-016AT0051 → B215-016AT0064 → B215-016AT0065 → B261-016AC0033 → END
B2-MCC-64604 | -P20 | 06 |  | PE-L1-4C4-17 | PE-L1-4C4-17 | BPSS-U4-004 |  |  | 1 | 745 | B2-MCC-64604-P2006 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-17 | 0.4 | 400 | N | 240 | STEAM | B2-MCC-64604 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-26004 | HRSG #22 HP STEAM WARM-UP LINE DRAIN MOV (AFTER CHECK V/V) | 1.1_MAIN BUILDING COMPLEX(HRSG#22) | L1, L2, L3, PE | B264-016CT0047 → B264-016CT0048 → B264-016CT0235 → B264-016CT0029 → B264-016CT0028 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L27 → M0406 → D0301-L21 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B215-016AT0050 → B261-016AC0024 → END
B2-MCC-64604 | -P20 | 07 |  | PE-L1-4C4-17 | PE-L1-4C4-17 | BPSS-U4-006 |  |  | 1 | 746 | B2-MCC-64604-P2007 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-17 | 0.4 | 400 | N | 240 | STEAM | B2-MCC-64604 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-27002 | HRSG #22 LP STEAM WARM-UP LINE DRAIN MOV (BEFORE CHECK V/V) | 1.1_MAIN BUILDING COMPLEX(HRSG#22) | L1, L2, L3, PE | B264-016CT0047 → B264-016CT0048 → B264-016CT0235 → B264-016CT0029 → B264-016CT0028 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L27 → M0406 → D0301-L21 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B215-016AT0050 → B261-016AC0025 → END
B2-MCC-64604 | -P20 | 08 |  | PE-L1-4C4-17 | PE-L1-4C4-17 | BPSS-U4-007 |  |  | 1 | 747 | B2-MCC-64604-P2008 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-17 | 0.4 | 400 | N | 240 | STEAM | B2-MCC-64604 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-27004 | HRSG #22 LP STEAM WARM-UP LINE DRAIN MOV (AFTER CHECK V/V) | 1.1_MAIN BUILDING COMPLEX(HRSG#22) | L1, L2, L3, PE | B264-016CT0047 → B264-016CT0048 → B264-016CT0235 → B264-016CT0029 → B264-016CT0028 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L27 → M0406 → D0301-L21 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B215-016AT0050 → B261-016AC0023 → END
B1-MCC-59601 | -P20 | 16 |  | PE-L1-4C4-08 | PE-L1-4C4-08 | BPSS-B1-001 |  |  | 1 | 748 | B1-MCC-59601-P2016 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-08 | 0.4 | 400 | N | 80 | STEAM | B1-MCC-59601 | 400V MCC FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-MOV-26012 | COMMOM HP STEAM WARM-UP LINE DRAIN MOV | 1.1_MAIN BUILDING COMPLEX | L1, L2, L3, PE | B159-006AT0003 → B159-006AT0025 → D0326-L21 → M0316 → B113-996AT0012 → B113-016AT0011 → B113-016AT0002 → B113-016BC0007 → END
B1-MCC-59601 | -P20 | 17 |  | PE-L1-4C4-10 | PE-L1-4C4-10 | BPSS-B1-003 |  |  | 1 | 749 | B1-MCC-59601-P2017 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-10 | 0.75 | 400 | N | 190 | STEAM | B1-MCC-59601 | 400V MCC FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-MOV-26011 | COMMOM HP STEAM TO AUX. STEAM SUPPLY MOV | 1.1_MAIN BUILDING COMPLEX | L1, L2, L3, PE | B159-006AT0003 → B159-006AT0019 → B113-006CC0006 → M0317 → B113-006AC0007 → B113-016BC0038 → B114-016BT0102 → B114-016BT0101 → B114-016BT0040 → B114-016BT0041 → B161-016CC0009 → END
B1-MCC-59601 | -P20 | 18 |  | PE-L1-4C4-09 | PE-L1-4C4-09 | BPSS-B1-004 |  |  | 1 | 750 | B1-MCC-59601-P2018 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-09 | 0.75 | 400 | N | 120 | STEAM | B1-MCC-59601 | 400V MCC FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-MOV-26021 | HP STEAM DRAIN MOV FOR START-UP TO MAIN STOP V/V | 1.1_MAIN BUILDING COMPLEX(ST#1) | L1, L2, L3, PE | B159-006AT0003 → B159-006AT0025 → D0326-L21 → M0316 → B113-996AT0012 → B113-016AT0011 → B113-016AT0003 → B113-016AT0004 → B113-016AT0005 → B113-016AT0006 → B113-016AT0007 → B113-016BC0015 → END
B1-MCC-59601 | -P20 | 19 |  | PE-L1-4C4-09 | PE-L1-4C4-09 | BPSS-B1-006 |  |  | 1 | 751 | B1-MCC-59601-P2019 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-09 | 0.4 | 400 | N | 150 | STEAM | B1-MCC-59601 | 400V MCC FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-MOV-27011 | LP STEAM DRAIN MOV FOR START-UP | 1.1_MAIN BUILDING COMPLEX | L1, L2, L3, PE | B159-006AT0003 → B159-006AT0025 → D0326-L15 → M0316 → B113-996AT0012 → B113-016AT0011 → B113-016AT0003 → B113-016AT0004 → B113-016AT0005 → B113-016AT0006 → B113-016AT0007 → B113-016BC0034 → B113-006AC0013 → END
B1-MCC-59601 | -P20 | 20 |  | PE-L1-4C4-05 | PE-L1-4C4-05 | BPSS-B1-008 |  |  | 1 | 752 | B1-MCC-59601-P2020 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-05 | 0.4 | 400 | N | 200 | STEAM | B1-MCC-59601 | 400V MCC FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-MOV-28011 | AUX STEAM HEADER STOP MOV FORM BLOCK #2 HEADER | 1.1_MAIN BUILDING COMPLEX | L1, L2, L3, PE | B159-006AT0003 → B159-006AT0019 → B113-006CC0006 → M0317 → B113-006AC0007 → B113-016BC0038 → B114-016BT0102 → B114-016BT0101 → B114-016BT0040 → B114-016BT0041 → B161-016CC0012 → END
B1-MCC-59602 | -P20 | 18 |  | PE-L1-4C4-09 | PE-L1-4C4-09 | BPSS-B1-009 |  |  | 1 | 753 | B1-MCC-59602-P2018 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-09 | 0.4 | 400 | N | 190 | STEAM | B1-MCC-59602 | 400V MCC FOR ST #1 FOR BLOCK #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B0-MOV-28021 | AUX STEAM HEADER STOP MOV FORM AUX BOILER | 1.1_MAIN BUILDING COMPLEX | L1, L2, L3, PE | B159-006AT0006 → B159-006AT0019 → B113-006CC0006 → M0317 → B113-006AC0007 → B113-016BC0038 → B114-016BT0102 → B114-016BT0101 → B114-016BT0040 → B114-016BT0041 → B161-016CC0011 → END
B1-MCC-59602 | -P20 | 19 |  | PE-L1-4C4-09 | PE-L1-4C4-09 | BPSS-B1-010 |  |  | 1 | 754 | B1-MCC-59602-P2019 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-09 | 0.2 | 400 | N | 120 | STEAM | B1-MCC-59602 | 400V MCC FOR ST #1 FOR BLOCK #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-MOV-28012 | AUX STEAM TO TURBINE GLAND SEAL STEAM HEADER MOV | 1.1_MAIN BUILDING COMPLEX | L1, L2, L3, PE | B159-006AT0006 → B159-006AT0005 → B159-006AT0014 → B159-006AT0025 → D0326-L21 → M0316 → B113-016AT0007 → B113-016AT0006 → B113-016AT0005 → B113-016AT0004 → B113-016AT0003 → B113-016AT0011 → B113-996AT0012 → B113-016BC0025 → END
B1-MCC-59602 | -P20 | 20 |  | PE-L1-4C4-09 | PE-L1-4C4-09 | BPSS-B1-011 |  |  | 1 | 755 | B1-MCC-59602-P2020 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-09 | 0.2 | 400 | N | 110 | STEAM | B1-MCC-59602 | 400V MCC FOR ST #1 FOR BLOCK #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-MOV-28013 | TURBINE GLAND SEAL STEAM WARM-UP DRAIN MOV | 1.1_MAIN BUILDING COMPLEX | L1, L2, L3, PE | B159-006AT0006 → B159-006AT0005 → B159-006AT0014 → B159-006AT0025 → D0326-L15 → M0316 → B113-996AT0012 → B113-016AT0011 → B113-016AT0003 → B113-016AT0004 → B113-016AT0005 → B113-016AT0006 → B113-016AT0007 → B113-016BC0036 → END
B1-MCC-59602 | -P20 | 21 |  | PE-L1-4C4-07 | PE-L1-4C4-07 | BPSS-B1-012 |  |  | 1 | 756 | B1-MCC-59602-P2021 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-07 | 0.2 | 400 | N | 190 | STEAM | B1-MCC-59602 | 400V MCC FOR ST #1 FOR BLOCK #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, PE | B1-MOV-28001 | AUX STEAM PRDS BODY DRAIN | 1.1_MAIN BUILDING COMPLEX | L1, L2, L3, PE | B159-006AT0006 → B159-006AT0019 → B113-006CC0006 → M0317 → B113-006AC0007 → B113-016BC0038 → B114-016BT0102 → B114-016BT0101 → B114-016BT0040 → B114-016BT0041 → B161-016CC0010 → END
B2-MCC-59601 | -P20 | 17 |  | PE-L1-4C4-13 | PE-L1-4C4-13 | BPSS-B2-001 |  |  | 1 | 757 | B2-MCC-59601-P2017 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-13 | 0.4 | 400 | N | 80 | STEAM | B2-MCC-59601 | 400V MCC FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-MOV-26012 | COMMOM HP STEAM WARM-UP LINE DRAIN MOV | 1.1_MAIN BUILDING COMPLEX | L1, L2, L3, PE | B259-006AT0003 → B259-006AT0025 → D0325-L21 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0002 → B213-016BC0007 → END
B2-MCC-59601 | -P20 | 18 |  | PE-L1-4C4-17 | PE-L1-4C4-17 | BPSS-B2-003 |  |  | 1 | 758 | B2-MCC-59601-P2018 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-17 | 0.75 | 400 | N | 130 | STEAM | B2-MCC-59601 | 400V MCC FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-MOV-26011 | COMMOM HP STEAM TO AUX. STEAM SUPPLY MOV | 1.1_MAIN BUILDING COMPLEX | L1, L2, L3, PE | B259-006AT0003 → B259-006AT0019 → B213-006CC0006 → M0314 → B213-006AC0007 → B213-016BC0038 → B215-016BT0104 → B215-016BT0103 → B213-016BC0040 → END
B2-MCC-59601 | -P20 | 19 |  | PE-L1-4C4-17 | PE-L1-4C4-17 | BPSS-B2-004 |  |  | 1 | 759 | B2-MCC-59601-P2019 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-17 | 0.75 | 400 | N | 110 | STEAM | B2-MCC-59601 | 400V MCC FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-MOV-26021 | HP STEAM DRAIN MOV FOR START-UP TO MAIN STOP V/V | 1.1_MAIN BUILDING COMPLEX(ST#2) | L1, L2, L3, PE | B259-006AT0003 → B259-006AT0025 → D0325-L15 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0003 → B213-016AT0004 → B213-016AT0005 → B213-016AT0006 → B213-016AT0007 → B213-016BC0015 → END
B2-MCC-59601 | -P20 | 20 |  | PE-L1-4C4-12 | PE-L1-4C4-12 | BPSS-B2-006 |  |  | 1 | 760 | B2-MCC-59601-P2020 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-12 | 0.4 | 400 | N | 140 | STEAM | B2-MCC-59601 | 400V MCC FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-MOV-27011 | LP STEAM DRAIN MOV FOR START-UP | 1.1_MAIN BUILDING COMPLEX | L1, L2, L3, PE | B259-006AT0003 → B259-006AT0025 → D0325-L21 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0003 → B213-016AT0004 → B213-016AT0005 → B213-016AT0006 → B213-016AT0007 → B213-016BC0033 → B213-006AC0011 → END
B2-MCC-59601 | -P20 | 21 |  | PE-L1-4C4-17 | PE-L1-4C4-17 | BPSS-B2-008 |  |  | 1 | 761 | B2-MCC-59601-P2021 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-17 | 0.4 | 400 | N | 290 | STEAM | B2-MCC-59601 | 400V MCC FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-MOV-28011 | AUX STEAM HEADER STOP MOV FORM BLOCK #1 HEADER | 1.1_MAIN BUILDING COMPLEX | L1, L2, L3, PE | B259-006AT0003 → B259-006AT0019 → B213-006CC0006 → M0314 → B213-006AC0007 → B213-016BC0038 → B215-016BT0104 → B215-016BT0103 → B215-016BT0036 → B215-016BT0035 → B215-016BT0034 → B215-016BT0033 → B215-016BT0032 → B215-016BT0031 → B261-016AC0008 → END
B2-MCC-59602 | -P20 | 17 |  | PE-L1-4C4-06 | PE-L1-4C4-06 | BPSS-B2-010 |  |  | 1 | 762 | B2-MCC-59602-P2017 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-06 | 0.2 | 400 | N | 110 | STEAM | B2-MCC-59602 | 400V MCC FOR ST #2 FOR BLOCK #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-MOV-28012 | AUX STEAM TO TURBINE GLAND SEAL STEAM HEADER MOV | 1.1_MAIN BUILDING COMPLEX | L1, L2, L3, PE | B259-006AT0006 → B259-006AT0005 → B259-006AT0014 → B259-006AT0025 → D0325-L21 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0003 → B213-016AT0004 → B213-016AT0005 → B213-016AT0006 → B213-016AT0007 → B213-016BC0025 → END
B2-MCC-59602 | -P20 | 18 |  | PE-L1-4C4-17 | PE-L1-4C4-17 | BPSS-B2-011 |  |  | 1 | 763 | B2-MCC-59602-P2018 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-17 | 0.2 | 400 | N | 110 | STEAM | B2-MCC-59602 | 400V MCC FOR ST #2 FOR BLOCK #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-MOV-28013 | TURBINE GLAND SEAL STEAM WARM-UP DRAIN MOV | 1.1_MAIN BUILDING COMPLEX | L1, L2, L3, PE | B259-006AT0006 → B259-006AT0005 → B259-006AT0014 → B259-006AT0025 → D0325-L15 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0003 → B213-016AT0004 → B213-016AT0005 → B213-016AT0006 → B213-016AT0007 → B213-016BC0036 → END
B2-MCC-59602 | -P20 | 19 |  | PE-L1-4C4-14 | PE-L1-4C4-14 | BPSS-B2-012 |  |  | 1 | 764 | B2-MCC-59602-P2019 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-14 | 0.2 | 400 | N | 130 | STEAM | B2-MCC-59602 | 400V MCC FOR ST #2 FOR BLOCK #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, PE | B2-MOV-28001 | AUX STEAM PRDS BODY DRAIN | 1.1_MAIN BUILDING COMPLEX | L1, L2, L3, PE | B259-006AT0006 → B259-006AT0019 → B213-006CC0006 → M0314 → B213-006AC0007 → B213-016BC0038 → B215-016BT0104 → B215-016BT0103 → B213-016BC0039 → END
B0-MCC-64601 | -P20 | 02 |  | PE-L1-4C25/16-01 | PE-L1-4C25/16-01 | BPSS-B2-014 | DONE(9/28) | DONE | 1 | 765 | B0-MCC-64601-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 25sqmm + 1C X 16sqmm | PE-L1-4C25/16-01 | 15 | 400 | N | 340 | STEAM | B0-MCC-64601 | 400V MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | STB-TEMP-01 | MOV SPARE (MARTYR VALVE FOR HP STEAM BLOWING, TEMP) | 1.1_MAIN BUILDING COMPLEX / STG #1 | L1, L2, L3, PE | B064-016AT0012 → B064-996AT0020 → M0501 → D0517-L23 → M0510 → D0502-L35 → M0326 → D0320-L25 → M0325 → D0319-L31 → M0324 → D0327-L25 → M0321 → D0317-L14 → M0320 → D0323-L14 → M0319 → D0316-L14 → M0318 → D0315-L25 → M0315 → D0314-L25 → B159-006AT0017 → B159-006AT0018 → B159-006AT0005 → B159-006AT0014 → B159-006AT0025 → D0326-L13 → M0316 → B113-006AC0041 → END
B0-MCC-64601 | -P20 | 03 |  | PE-L1-4C25/16-01 | PE-L1-4C25/16-01 | BPSS-B2-015 |  |  | 1 | 766 | B0-MCC-64601-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 25sqmm + 1C X 16sqmm | PE-L1-4C25/16-01 | 11 | 400 | N | 430 | STEAM | B0-MCC-64601 | 400V MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | STB-TEMP-02 | MOV SPARE (MARTYR VALVE FOR LP STEAM BLOWING, TEMP) | 1.1_MAIN BUILDING COMPLEX / STG #2 | L1, L2, L3, PE | B064-016AT0012 → B064-996AT0020 → M0501 → D0517-L23 → M0510 → D0502-L35 → M0326 → D0320-L25 → M0325 → D0319-L31 → M0324 → D0327-L25 → M0321 → D0317-L14 → M0320 → D0323-L14 → M0319 → D0316-L14 → M0318 → D0315-L25 → M0315 → D0313-L11 → M0312 → D0311-L14 → M0311 → D0310-L21 → B259-006AT0017 → B259-006AT0018 → B259-006AT0005 → B259-006AT0014 → B259-006AT0025 → D0325-L13 → B213-996AT0012 → B213-016AT0011 → B213-016AT0003 → B213-016AT0004 → B213-016BC0057 → END
B1-MCC-64601 | -P20 | 24 |  | PE-L1-4C4-09 | PE-L1-4C4-09 | FWS-U1-001 |  |  | 1 | 767 | B1-MCC-64601-P2024 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-09 | 0.2 | 400 | N | 290 | FEEDWATER SYSTEM | B1-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-30001A | #11 BOILER FEED PUMP A INTERSTAGE DISCHARGE MOV | 1.1_MAIN BUILDING COMPLEX(HRSG#11) | L1, L2, L3, PE | B164-016AT0091 → B164-996AT0022 → M0504 → D0531-L43 → M0510 → D0517-L14 → M0501 → D0503-L43 → M0502 → D0504-L43 → M0503 → D0501-L43 → M0328 → D0324-L43 → M0329 → B114-996DT0081 → B114-016DT0082 → B114-016DT0083 → B114-016DT0084 → B114-016DT0096 → B114-016DT0097 → B114-016DT0098 → B161-016AC0010 → END
B1-MCC-64602 | -P20 | 27 |  | PE-L1-4C4-09 | PE-L1-4C4-09 | FWS-U1-002 |  |  | 1 | 768 | B1-MCC-64602-P2027 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-09 | 0.2 | 400 | N | 280 | FEEDWATER SYSTEM | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-30001B | #11 BOILER FEED PUMP B INTERSTAGE DISCHARGE MOV | 1.1_MAIN BUILDING COMPLEX(HRSG#11) | L1, L2, L3, PE | B164-016ET0106 → B164-996ET0022 → M0504 → D0531-L31 → M0510 → D0517-L22 → M0501 → D0503-L41 → M0502 → D0504-L41 → M0503 → D0501-L41 → M0328 → D0324-L41 → M0329 → B114-996DT0081 → B114-016DT0082 → B114-016DT0083 → B114-016DT0084 → B114-016DT0096 → B114-016DT0097 → B161-016AC0011 → END
B1-MCC-64602 | -P20 | 28 |  | PE-L1-4C4-09 | PE-L1-4C4-09 | FWS-U1-003 |  |  | 1 | 769 | B1-MCC-64602-P2028 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-09 | 2.2 | 400 | N | 290 | FEEDWATER SYSTEM | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-30002A | #11 BOILER FEED PUMP A HP DISCHARGE MOV | 1.1_MAIN BUILDING COMPLEX(HRSG#11) | L1, L2, L3, PE | B164-016ET0106 → B164-996ET0022 → M0504 → D0531-L43 → M0510 → D0517-L14 → M0501 → D0503-L43 → M0502 → D0504-L43 → M0503 → D0501-L43 → M0328 → D0324-L43 → M0329 → B114-996DT0081 → B114-016DT0082 → B114-016DT0083 → B114-016DT0084 → B114-016DT0096 → B114-016DT0097 → B114-016DT0098 → B161-016AC0012 → END
B1-MCC-64601 | -P20 | 25 |  | PE-L1-4C4-09 | PE-L1-4C4-09 | FWS-U1-004 |  |  | 1 | 770 | B1-MCC-64601-P2025 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-09 | 2.2 | 400 | N | 290 | FEEDWATER SYSTEM | B1-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-30002B | #11 BOILER FEED PUMP B HP DISCHARGE MOV | 1.1_MAIN BUILDING COMPLEX(HRSG#11) | L1, L2, L3, PE | B164-016AT0091 → B164-996AT0022 → M0504 → D0531-L34 → M0510 → D0517-L25 → M0501 → D0503-L44 → M0502 → D0504-L44 → M0503 → D0501-L44 → M0328 → D0324-L44 → M0329 → B114-996DT0081 → B114-016DT0082 → B114-016DT0083 → B114-016DT0084 → B114-016DT0096 → B114-016DT0097 → B114-016DT0098 → B161-016AC0013 → END
B1-MCC-64601 | -P20 | 26 |  | PE-L1-4C4-10 | PE-L1-4C4-10 | FWS-U1-005 |  |  | 1 | 771 | B1-MCC-64601-P2026 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-10 | 0.2 | 400 | N | 290 | FEEDWATER SYSTEM | B1-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-30003A | #11 BOILER FEED PUMP A HP DISCHARGE BYPASS MOV | 1.1_MAIN BUILDING COMPLEX(HRSG#11) | L1, L2, L3, PE | B164-016AT0091 → B164-996AT0022 → M0504 → D0531-L27 → M0510 → D0517-L26 → M0501 → D0503-L38 → M0502 → D0504-L38 → M0503 → D0501-L38 → M0328 → D0324-L38 → M0329 → B114-996DT0081 → B114-016DT0082 → B114-016DT0083 → B114-016DT0084 → B114-016DT0096 → B114-016DT0097 → B114-016DT0098 → B161-016AC0014 → END
B1-MCC-64602 | -P20 | 29 |  | PE-L1-4C4-10 | PE-L1-4C4-10 | FWS-U1-006 |  |  | 1 | 772 | B1-MCC-64602-P2029 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-10 | 0.2 | 400 | N | 290 | FEEDWATER SYSTEM | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-30003B | #11 BOILER FEED PUMP B HP DISCHARGE BYPASS MOV | 1.1_MAIN BUILDING COMPLEX(HRSG#11) | L1, L2, L3, PE | B164-016ET0106 → B164-996ET0022 → M0504 → D0531-L34 → M0510 → D0517-L25 → M0501 → D0503-L44 → M0502 → D0504-L44 → M0503 → D0501-L44 → M0328 → D0324-L44 → M0329 → B114-996DT0081 → B114-016DT0082 → B114-016DT0083 → B114-016DT0084 → B114-016DT0096 → B114-016DT0097 → B114-016DT0098 → B161-016AC0015 → END
B1-MCC-64604 | -P20 | 05 |  | PE-L1-4C4-10 | PE-L1-4C4-10 | FWS-U2-001 | DONE(10/6) | DONE | 1 | 773 | B1-MCC-64604-P2005 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-10 | 0.2 | 400 | N | 350 | FEEDWATER SYSTEM | B1-MCC-64604 | 400V MCC FOR GT/HRSG#2 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-31001A | #12 BOILER FEED PUMP A INTERSTAGE DISCHARGE MOV | 1.1_MAIN BUILDING COMPLEX(HRSG#12) | L1, L2, L3, PE | B164-016AT0118 → B164-016AT0117 → B164-016AT0116 → B164-996AT0023 → M0504 → D0531-L35 → M0510 → D0517-L26 → M0501 → D0503-L45 → M0502 → D0504-L45 → M0503 → D0501-L45 → M0328 → D0324-L45 → M0329 → B114-996CT0071 → B114-016CT0072 → B114-016CT0073 → B114-016CT0074 → B114-016CT0075 → B114-016CT0076 → B114-016CT0087 → B114-016CT0088 → B114-016CT0089 → B161-016CC0008 → END
B1-MCC-64604 | -P20 | 06 |  | PE-L1-4C4-10 | PE-L1-4C4-10 | FWS-U2-002 | DONE(10/6) | DONE | 1 | 774 | B1-MCC-64604-P2006 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-10 | 0.2 | 400 | N | 360 | FEEDWATER SYSTEM | B1-MCC-64604 | 400V MCC FOR GT/HRSG#2 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-31001B | #12 BOILER FEED PUMP B INTERSTAGE DISCHARGE MOV | 1.1_MAIN BUILDING COMPLEX(HRSG#12) | L1, L2, L3, PE | B164-016AT0118 → B164-016AT0117 → B164-016AT0116 → B164-996AT0023 → M0504 → D0531-L25 → M0510 → D0517-L14 → M0501 → D0503-L46 → M0502 → D0504-L46 → M0503 → D0501-L46 → M0328 → D0324-L46 → M0329 → B114-996CT0071 → B114-016CT0072 → B114-016CT0073 → B114-016CT0074 → B114-016CT0075 → B114-016CT0076 → B114-016CT0087 → B114-016CT0088 → B114-016CT0089 → B161-016CC0005 → END
B1-MCC-64604 | -P20 | 07 |  | PE-L1-4C4-10 | PE-L1-4C4-10 | FWS-U2-003 | DONE(10/6) | DONE | 1 | 775 | B1-MCC-64604-P2007 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-10 | 2.2 | 400 | N | 350 | FEEDWATER SYSTEM | B1-MCC-64604 | 400V MCC FOR GT/HRSG#2 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-31002A | #12 BOILER FEED PUMP A HP DISCHARGE MOV | 1.1_MAIN BUILDING COMPLEX(HRSG#12) | L1, L2, L3, PE | B164-016AT0118 → B164-016AT0117 → B164-016AT0116 → B164-996AT0023 → M0504 → D0531-L25 → M0510 → D0517-L24 → M0501 → D0503-L46 → M0502 → D0504-L46 → M0503 → D0501-L46 → M0328 → D0324-L46 → M0329 → B114-996CT0071 → B114-016CT0072 → B114-016CT0073 → B114-016CT0074 → B114-016CT0075 → B114-016CT0076 → B114-016CT0087 → B114-016CT0088 → B114-016CT0089 → B161-016CC0007 → END
B1-MCC-64604 | -P20 | 08 |  | PE-L1-4C4-11 | PE-L1-4C4-11 | FWS-U2-004 |  |  | 1 | 776 | B1-MCC-64604-P2008 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-11 | 2.2 | 400 | N | 350 | FEEDWATER SYSTEM | B1-MCC-64604 | 400V MCC FOR GT/HRSG#2 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-31002B | #12 BOILER FEED PUMP B HP DISCHARGE MOV | 1.1_MAIN BUILDING COMPLEX(HRSG#12) | L1, L2, L3, PE | B164-016AT0118 → B164-016AT0117 → B164-016AT0116 → B164-996AT0023 → M0504 → D0531-L25 → M0510 → D0517-L24 → M0501 → D0503-L46 → M0502 → D0504-L46 → M0503 → D0501-L46 → M0328 → D0324-L46 → M0329 → B114-996CT0071 → B114-016CT0072 → B114-016CT0073 → B114-016CT0074 → B114-016CT0075 → B114-016CT0076 → B114-016CT0087 → B114-016CT0088 → B114-016CT0089 → B161-016CC0006 → END
B1-MCC-64604 | -P20 | 09 |  | PE-L1-4C4-11 | PE-L1-4C4-11 | FWS-U2-005 |  |  | 1 | 777 | B1-MCC-64604-P2009 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-11 | 0.2 | 400 | N | 360 | FEEDWATER SYSTEM | B1-MCC-64604 | 400V MCC FOR GT/HRSG#2 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-31003A | #12 BOILER FEED PUMP A HP DISCHARGE BYPASS MOV | 1.1_MAIN BUILDING COMPLEX(HRSG#12) | L1, L2, L3, PE | B164-016AT0118 → B164-016AT0117 → B164-016AT0116 → B164-996AT0023 → M0504 → D0531-L35 → M0510 → D0517-L26 → M0501 → D0503-L45 → M0502 → D0504-L45 → M0503 → D0501-L45 → M0328 → D0324-L45 → M0329 → B114-996CT0071 → B114-016CT0072 → B114-016CT0073 → B114-016CT0074 → B114-016CT0075 → B114-016CT0076 → B114-016CT0087 → B114-016CT0088 → B114-016CT0089 → B161-016CC0030 → END
B1-MCC-64604 | -P20 | 10 |  | PE-L1-4C4-11 | PE-L1-4C4-11 | FWS-U2-006 |  |  | 1 | 778 | B1-MCC-64604-P2010 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-11 | 0.2 | 400 | N | 360 | FEEDWATER SYSTEM | B1-MCC-64604 | 400V MCC FOR GT/HRSG#2 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-31003B | #12 BOILER FEED PUMP B HP DISCHARGE BYPASS MOV | 1.1_MAIN BUILDING COMPLEX(HRSG#12) | L1, L2, L3, PE | B164-016AT0118 → B164-016AT0117 → B164-016AT0116 → B164-996AT0023 → M0504 → D0531-L24 → M0510 → D0517-L14 → M0501 → D0503-L46 → M0502 → D0504-L46 → M0503 → D0501-L35 → M0328 → D0324-L46 → M0329 → B114-996CT0071 → B114-016CT0072 → B114-016CT0073 → B114-016CT0074 → B114-016CT0075 → B114-016CT0076 → B114-016CT0087 → B114-016CT0088 → B114-016CT0089 → B161-016CC0031 → END
B2-MCC-64601 | -P20 | 26 |  | PE-L1-4C4-16 | PE-L1-4C4-16 | FWS-U3-001 |  |  | 1 | 779 | B2-MCC-64601-P2026 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-16 | 0.2 | 400 | N | 310 | FEEDWATER SYSTEM | B2-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-30001A | #21 BOILER FEED PUMP A INTERSTAGE DISCHARGE MOV | 1.1_MAIN BUILDING COMPLEX(HRSG#21) | L1, L2, L3, PE | B264-016CT0024 → B264-016CT0025 → B264-016CT0026 → B264-016CT0027 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L26 → M0406 → D0301-L22 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B215-016AT0050 → B215-016AT0051 → B215-016AT0064 → B215-016AT0065 → B215-016AT0066 → B215-016AT0055 → B215-016AT0056 → B215-016AT0057 → B261-016CC0010 → END
B2-MCC-64602 | -P20 | 25 |  | PE-L1-4C4-16 | PE-L1-4C4-16 | FWS-U3-002 |  |  | 1 | 780 | B2-MCC-64602-P2025 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-16 | 0.2 | 400 | N | 320 | FEEDWATER SYSTEM | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-30001B | #21 BOILER FEED PUMP B INTERSTAGE DISCHARGE MOV | 1.1_MAIN BUILDING COMPLEX(HRSG#21) | L1, L2, L3, PE | B264-016AT0045 → B264-016AT0046 → B264-016AT0209 → B264-016AT0026 → B264-016AT0027 → B264-016AT0225 → B264-996AT0011 → M0405 → D0421-L26 → M0406 → D0301-L22 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B215-016AT0050 → B215-016AT0051 → B215-016AT0064 → B215-016AT0065 → B215-016AT0066 → B215-016AT0055 → B215-016AT0056 → B261-016CC0011 → END
B2-MCC-64602 | -P20 | 26 |  | PE-L1-4C4-16 | PE-L1-4C4-16 | FWS-U3-003 |  |  | 1 | 781 | B2-MCC-64602-P2026 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-16 | 2.2 | 400 | N | 320 | FEEDWATER SYSTEM | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-30002A | #21 BOILER FEED PUMP A HP DISCHARGE MOV | 1.1_MAIN BUILDING COMPLEX(HRSG#21) | L1, L2, L3, PE | B264-016AT0045 → B264-016AT0046 → B264-016AT0209 → B264-016AT0026 → B264-016AT0027 → B264-016AT0225 → B264-996AT0011 → M0405 → D0421-L26 → M0406 → D0301-L22 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B215-016AT0050 → B215-016AT0051 → B215-016AT0064 → B215-016AT0065 → B215-016AT0066 → B215-016AT0055 → B215-016AT0056 → B215-016AT0057 → B261-016CC0012 → END
B2-MCC-64601 | -P20 | 27 |  | PE-L1-4C4-16 | PE-L1-4C4-16 | FWS-U3-004 |  |  | 1 | 782 | B2-MCC-64601-P2027 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-16 | 2.2 | 400 | N | 310 | FEEDWATER SYSTEM | B2-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-30002B | #21 BOILER FEED PUMP B HP DISCHARGE MOV | 1.1_MAIN BUILDING COMPLEX(HRSG#21) | L1, L2, L3, PE | B264-016CT0024 → B264-016CT0025 → B264-016CT0026 → B264-016CT0027 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L26 → M0406 → D0301-L22 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B215-016AT0050 → B215-016AT0051 → B215-016AT0064 → B215-016AT0065 → B215-016AT0066 → B215-016AT0055 → B215-016AT0056 → B215-016AT0057 → B261-016CC0013 → END
B2-MCC-64601 | -P20 | 28 |  | PE-L1-4C4-16 | PE-L1-4C4-16 | FWS-U3-005 |  |  | 1 | 783 | B2-MCC-64601-P2028 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-16 | 0.2 | 400 | N | 310 | FEEDWATER SYSTEM | B2-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-30003A | #21 BOILER FEED PUMP A HP DISCHARGE BYPASS MOV | 1.1_MAIN BUILDING COMPLEX(HRSG#21) | L1, L2, L3, PE | B264-016CT0024 → B264-016CT0025 → B264-016CT0026 → B264-016CT0027 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L26 → M0406 → D0301-L22 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B215-016AT0050 → B215-016AT0051 → B215-016AT0064 → B215-016AT0065 → B215-016AT0066 → B215-016AT0055 → B215-016AT0056 → B215-016AT0057 → B261-016CC0014 → END
B2-MCC-64602 | -P20 | 27 |  | PE-L1-4C4-16 | PE-L1-4C4-16 | FWS-U3-006 |  |  | 1 | 784 | B2-MCC-64602-P2027 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-16 | 0.2 | 400 | N | 320 | FEEDWATER SYSTEM | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-30003B | #21 BOILER FEED PUMP B HP DISCHARGE BYPASS MOV | 1.1_MAIN BUILDING COMPLEX(HRSG#21) | L1, L2, L3, PE | B264-016AT0045 → B264-016AT0046 → B264-016AT0209 → B264-016AT0026 → B264-016AT0027 → B264-016AT0225 → B264-996AT0011 → M0405 → D0421-L26 → M0406 → D0301-L22 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B215-016AT0050 → B215-016AT0051 → B215-016AT0064 → B215-016AT0065 → B215-016AT0066 → B215-016AT0056 → B215-016AT0057 → END → B261-016CC0015 → END
B2-MCC-64603 | -P20 | 07 |  | PE-L1-4C4-14 | PE-L1-4C4-14 | FWS-U4-001 |  |  | 1 | 785 | B2-MCC-64603-P2007 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-14 | 0.2 | 400 | N | 220 | FEEDWATER SYSTEM | B2-MCC-64603 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-31001A | #22 BOILER FEED PUMP A INTERSTAGE DISCHARGE MOV | 1.1_MAIN BUILDING COMPLEX(HRSG#22) | L1, L2, L3, PE | B264-016CT0027 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L27 → M0406 → D0301-L21 → M0301 → B215-996BT0001 → B215-016BT0002 → B215-016BT0003 → B215-016BT0004 → B261-016AC0007 → END
B2-MCC-64603 | -P20 | 08 |  | PE-L1-4C4-14 | PE-L1-4C4-14 | FWS-U4-002 |  |  | 1 | 786 | B2-MCC-64603-P2008 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-14 | 0.2 | 400 | N | 220 | FEEDWATER SYSTEM | B2-MCC-64603 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-31001B | #22 BOILER FEED PUMP B INTERSTAGE DISCHARGE MOV | 1.1_MAIN BUILDING COMPLEX(HRSG#22) | L1, L2, L3, PE | B264-016CT0027 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L27 → M0406 → D0301-L21 → M0301 → B215-996BT0001 → B215-016BT0002 → B215-016BT0003 → B215-016BT0004 → B261-016AC0004 → END
B2-MCC-64603 | -P20 | 09 |  | PE-L1-4C4-14 | PE-L1-4C4-14 | FWS-U4-003 |  |  | 1 | 787 | B2-MCC-64603-P2009 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-14 | 2.2 | 400 | N | 220 | FEEDWATER SYSTEM | B2-MCC-64603 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-31002A | #22 BOILER FEED PUMP A HP DISCHARGE MOV | 1.1_MAIN BUILDING COMPLEX(HRSG#22) | L1, L2, L3, PE | B264-016CT0027 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L27 → M0406 → D0301-L21 → M0301 → B215-996BT0001 → B215-016BT0002 → B215-016BT0003 → B215-016BT0004 → B261-016AC0006 → END
B2-MCC-64603 | -P20 | 10 |  | PE-L1-4C4-14 | PE-L1-4C4-14 | FWS-U4-004 |  |  | 1 | 788 | B2-MCC-64603-P2010 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-14 | 2.2 | 400 | N | 210 | FEEDWATER SYSTEM | B2-MCC-64603 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-31002B | #22 BOILER FEED PUMP B HP DISCHARGE MOV | 1.1_MAIN BUILDING COMPLEX(HRSG#22) | L1, L2, L3, PE | B264-016CT0027 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L27 → M0406 → D0301-L21 → M0301 → B215-996BT0001 → B215-016BT0002 → B215-016BT0003 → B215-016BT0004 → B261-016AC0005 → END
B2-MCC-64603 | -P20 | 11 |  | PE-L1-4C4-15 | PE-L1-4C4-15 | FWS-U4-005 |  |  | 1 | 789 | B2-MCC-64603-P2011 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-15 | 0.2 | 400 | N | 220 | FEEDWATER SYSTEM | B2-MCC-64603 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-31003A | #22 BOILER FEED PUMP A HP DISCHARGE BYPASS MOV | 1.1_MAIN BUILDING COMPLEX(HRSG#22) | L1, L2, L3, PE | B264-016CT0027 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L27 → M0406 → D0301-L21 → M0301 → B215-996BT0001 → B215-016BT0002 → B215-016BT0003 → B215-016BT0004 → B261-016AC0026 → END
B2-MCC-64603 | -P20 | 12 |  | PE-L1-4C4-23 | PE-L1-4C4-23 | FWS-U4-006 |  |  | 1 | 790 | B2-MCC-64603-P2012 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-23 | 0.2 | 400 | N | 220 | FEEDWATER SYSTEM | B2-MCC-64603 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-31003B | #22 BOILER FEED PUMP B HP DISCHARGE BYPASS MOV | 1.1_MAIN BUILDING COMPLEX(HRSG#22) | L1, L2, L3, PE | B264-016CT0027 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L27 → M0406 → D0301-L21 → M0301 → B215-996BT0001 → B215-016BT0002 → B215-016BT0003 → B215-016BT0004 → B261-016AC0027 → END
B0-MCC-64601 | -P20 | 04 |  | PE-L1-4C95/50-15 | HOLD (B1,B2위치 정정에 따른 Route 변경필요) | HWDS-B1-001 |  |  | 1 | 791 | B0-MCC-64601-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | HOLD (B1,B2위치 정정에 따른 Route 변경필요) | 75 | 400 | N | 350 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64601 | 400V MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-P-34001 | #1 HOT WATER SUPPLY PUMP A | 32_HOT WATER SUPPLY BUILDING | L1, L2, L3, PE | B064-016BT0012 → B064-016BT0013 → B064-016BT0014 → B064-016BT0015 → B064-016BT0016 → B064-016BT0309 → B064-016BT0037 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0055 → B025-996DT0019 → B025-016DT0056 → B025-016DT0057 → B025-016DT0135 → B078-016AC0012 → B078-006AC0043 → B078-006AC0026 → END
B0-MCC-64601 | -P20 | 05 |  | PE-L1-3C4-12 | HOLD (B1,B2위치 정정에 따른 Route 변경필요) | HWDS-B1-002 |  |  | 1 | 792 | B0-MCC-64601-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | HOLD (B1,B2위치 정정에 따른 Route 변경필요) | 0.11 | 230 | N | 350 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64601 | 400V MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-P-34001 | #1 HOT WATER SUPPLY PUMP A SPACE HEATER | 32_HOT WATER SUPPLY BUILDING | L1, N, PE | B064-016BT0012 → B064-016BT0013 → B064-016BT0014 → B064-016BT0015 → B064-016BT0016 → B064-016BT0309 → B064-016BT0037 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016CT0090 → B025-016CT0089 → B025-016CT0067 → B025-016CT0066 → B025-016CT0065 → B025-016CT0064 → B025-016CT0063 → B025-016CT0062 → B025-016CT0061 → B025-016CT0060 → B025-996CT0020 → B025-016CT0059 → B025-016CT0055 → B025-996CT0019 → B025-016CT0056 → B025-016CT0133 → B078-016AC0012 → B078-006AC0043 → B078-007AC0004 → END
B0-MCC-64602 | -P20 | 04 |  | PE-L1-4C95/50-08 | HOLD (B1,B2위치 정정에 따른 Route 변경필요) | HWDS-B1-003 |  |  | 1 | 793 | B0-MCC-64602-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | HOLD (B1,B2위치 정정에 따른 Route 변경필요) | 75 | 400 | N | 340 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64602 | 400V MCC FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-P-34002 | #1 HOT WATER SUPPLY PUMP B | 32_HOT WATER SUPPLY BUILDING | L1, L2, L3, PE | B064-016BT0032 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0055 → B025-996DT0019 → B025-016DT0056 → B025-016DT0057 → B025-016DT0135 → B078-016AC0011 → B078-006AC0044 → B078-006AC0027 → END
B0-MCC-64602 | -P20 | 05 |  | PE-L1-3C4-12 | HOLD (B1,B2위치 정정에 따른 Route 변경필요) | HWDS-B1-004 |  |  | 1 | 794 | B0-MCC-64602-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | HOLD (B1,B2위치 정정에 따른 Route 변경필요) | 0.11 | 230 | N | 330 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64602 | 400V MCC FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-P-34002 | #1 HOT WATER SUPPLY PUMP B SPACE HEATER | 32_HOT WATER SUPPLY BUILDING | L1, N, PE | B064-016BT0032 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016CT0090 → B025-016CT0089 → B025-016CT0067 → B025-016CT0066 → B025-016CT0065 → B025-016CT0064 → B025-016CT0063 → B025-016CT0062 → B025-016CT0061 → B025-016CT0060 → B025-996CT0020 → B025-016CT0059 → B025-016CT0055 → B025-996CT0019 → B025-016CT0056 → B025-016CT0133 → B078-016AC0011 → B078-006AC0044 → B078-007AC0005 → END
B0-MCC-64601 | -P20 | 06 |  | PE-L1-4C120/70-01 | HOLD (B1,B2위치 정정에 따른 Route 변경필요) | HWDS-B1-005 |  |  | 1 | 795 | B0-MCC-64601-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 120sqmm + 1C X 70sqmm | HOLD (B1,B2위치 정정에 따른 Route 변경필요) | 75 | 400 | N | 370 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64601 | 400V MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-P-34003 | #1 HOT WATER SUPPLY PUMP C | 32_HOT WATER SUPPLY BUILDING | L1, L2, L3, PE | B064-016AT0012 → B064-016AT0011 → B064-016AT0212 → B064-016AT0213 → B064-016AT0045 → B064-016AT0046 → B064-016AT0047 → B064-016AT0048 → B064-016AT0049 → B064-016AT0240 → B064-016AT0290 → B064-016AT0068 → B064-016AT0067 → B064-016AT0277 → B064-016AT0278 → B064-016AT0094 → B064-016AT0296 → B064-016AT0110 → B064-016AT0109 → B064-016AT0285 → B025-016CT0090 → B025-016CT0089 → B025-016CT0067 → B025-016CT0066 → B025-016CT0065 → B025-016CT0064 → B025-016CT0063 → B025-016CT0062 → B025-016CT0061 → B025-016CT0060 → B025-996CT0020 → B025-016CT0059 → B025-016CT0055 → B025-996CT0019 → B025-016CT0056 → B025-016CT0133 → B078-016AC0010 → B078-006AC0045 → B078-006AC0028 → END
B0-MCC-64601 | -P20 | 07 |  | PE-L1-3C4-12 | HOLD (B1,B2위치 정정에 따른 Route 변경필요) | HWDS-B1-006 |  |  | 1 | 796 | B0-MCC-64601-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | HOLD (B1,B2위치 정정에 따른 Route 변경필요) | 0.11 | 230 | N | 340 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64601 | 400V MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-P-34003 | #1 HOT WATER SUPPLY PUMP C SPACE HEATER | 32_HOT WATER SUPPLY BUILDING | L1, N, PE | B064-016BT0012 → B064-016BT0013 → B064-016BT0014 → B064-016BT0015 → B064-016BT0016 → B064-016BT0309 → B064-016BT0037 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016CT0090 → B025-016CT0089 → B025-016CT0067 → B025-016CT0066 → B025-016CT0065 → B025-016CT0064 → B025-016CT0063 → B025-016CT0062 → B025-016CT0061 → B025-016CT0060 → B025-996CT0020 → B025-016CT0059 → B025-016CT0055 → B025-996CT0019 → B025-016CT0056 → B025-016CT0133 → B078-016AC0010 → B078-006AC0045 → B078-007AC0006 → END
B0-MCC-64601 | -P20 | 08 |  | PE-L1-4C4-11 | PE-L1-4C4-11 | HWDS-B1-007 | DONE(10/12) | DONE | 1 | 797 | B0-MCC-64601-P2008 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-11 | 0.75 | 400 | N | 350 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64601 | 400V MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-34001 | #1 HOT WATER SUPPLY PUMP A DISCHARGE MOV | 32_HOT WATER SUPPLY BUILDING | L1, L2, L3, PE | B064-016BT0012 → B064-016BT0013 → B064-016BT0014 → B064-016BT0015 → B064-016BT0016 → B064-016BT0309 → B064-016BT0037 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0055 → B025-996DT0019 → B025-016DT0056 → B025-016DT0057 → B025-016DT0135 → B078-016AC0012 → B078-006AC0043 → B078-006AC0020 → END
B0-MCC-64602 | -P20 | 06 |  | PE-L1-4C4-11 | PE-L1-4C4-11 | HWDS-B1-008 | DONE(10/27) | DONE | 1 | 798 | B0-MCC-64602-P2006 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-11 | 0.75 | 400 | N | 330 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64602 | 400V MCC FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-34002 | #1 HOT WATER SUPPLY PUMP B DISCHARGE MOV | 32_HOT WATER SUPPLY BUILDING | L1, L2, L3, PE | B064-016BT0032 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016CT0090 → B025-016CT0089 → B025-016CT0067 → B025-016CT0066 → B025-016CT0065 → B025-016CT0064 → B025-016CT0063 → B025-016CT0062 → B025-016CT0061 → B025-016CT0060 → B025-996CT0020 → B025-016CT0059 → B025-016CT0055 → B025-996CT0019 → B025-016CT0056 → B025-016CT0133 → B078-016AC0011 → B078-006AC0044 → B078-006AC0021 → END
B0-MCC-64601 | -P20 | 09 |  | PE-L1-4C4-12 | PE-L1-4C4-12 | HWDS-B1-009 | DONE(10/27) | DONE | 1 | 799 | B0-MCC-64601-P2009 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-12 | 0.75 | 400 | N | 340 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64601 | 400V MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-34003 | #1 HOT WATER SUPPLY PUMP C DISCHARGE MOV | 32_HOT WATER SUPPLY BUILDING | L1, L2, L3, PE | B064-016BT0012 → B064-016BT0013 → B064-016BT0014 → B064-016BT0015 → B064-016BT0016 → B064-016BT0309 → B064-016BT0037 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016CT0090 → B025-016CT0089 → B025-016CT0067 → B025-016CT0066 → B025-016CT0065 → B025-016CT0064 → B025-016CT0063 → B025-016CT0062 → B025-016CT0061 → B025-016CT0060 → B025-996CT0020 → B025-016CT0059 → B025-016CT0055 → B025-996CT0019 → B025-016CT0056 → B025-016CT0133 → B078-016AC0010 → B078-006AC0045 → B078-006AC0022 → END
B1-MCC-64602 | -P20 | 30 |  | PE-L1-4C4-12 | PE-L1-4C4-12 | HWDS-B1-010 |  |  | 1 | 800 | B1-MCC-64602-P2030 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-12 | 0.2 | 400 | N | 240 | HOT WATER DISTRIBUTION SYSTEM | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-34004 | #1 HOT WATER HEAD TANK MAKE-UP LINE MOV | 1.1_MAIN BUILDING COMPLEX | L1, L2, L3, PE | B164-016ET0106 → B164-996ET0022 → M0504 → D0531-L27 → M0510 → D0517-L16 → M0501 → D0503-L38 → M0502 → D0504-L38 → M0503 → D0501-L38 → M0328 → D0324-L38 → M0329 → B114-996BT0046 → B114-016BT0045 → B114-016BT0044 → B161-016AC0016 → END
B0-MCC-64601 | -P20 | 10 |  | PE-L1-4C4-12 | PE-L1-4C4-12 | HWDS-B1-011 | DONE(10/27) | DONE | 1 | 801 | B0-MCC-64601-P2010 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-12 | 0.4 | 400 | N | 360 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64601 | 400V MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-34005 | #1 STEAM HEATER A TUBE SIDE INLET MOV | 32_HOT WATER SUPPLY BUILDING | L1, L2, L3, PE | B064-016BT0012 → B064-016BT0013 → B064-016BT0014 → B064-016BT0015 → B064-016BT0016 → B064-016BT0309 → B064-016BT0037 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0055 → B025-996DT0019 → B025-016DT0056 → B025-016DT0057 → B025-016DT0135 → B078-016AC0004 → B078-006AC0015 → B078-006AC0009 → END
B0-MCC-64601 | -P20 | 11 |  | PE-L1-4C4-12 | PE-L1-4C4-12 | HWDS-B1-012 | DONE(10/27) | DONE | 1 | 802 | B0-MCC-64601-P2011 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-12 | 0.4 | 400 | N | 360 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64601 | 400V MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-34008 | #1 STEAM HEATER B TUBE SIDE INLET MOV | 32_HOT WATER SUPPLY BUILDING | L1, L2, L3, PE | B064-016BT0012 → B064-016BT0013 → B064-016BT0014 → B064-016BT0015 → B064-016BT0016 → B064-016BT0309 → B064-016BT0037 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0055 → B025-996DT0019 → B025-016DT0056 → B025-016DT0057 → B025-016DT0135 → B078-016AC0005 → B078-006AC0016 → B078-006AC0012 → END
B0-MCC-64601 | -P20 | 12 |  | PE-L1-4C4-12 | PE-L1-4C4-12 | HWDS-B1-013 | DONE(10/27) | DONE | 1 | 803 | B0-MCC-64601-P2012 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-12 | 0.4 | 400 | N | 360 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64601 | 400V MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-34006 | #1 STEAM HEATER A SHELL SIDE INLET MOV | 32_HOT WATER SUPPLY BUILDING | L1, L2, L3, PE | B064-016BT0012 → B064-016BT0013 → B064-016BT0014 → B064-016BT0015 → B064-016BT0016 → B064-016BT0309 → B064-016BT0037 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0055 → B025-996DT0019 → B025-016DT0056 → B025-016DT0057 → B025-016DT0135 → B078-016AC0004 → B078-006AC0015 → B078-006AC0007 → END
B0-MCC-64601 | -P20 | 13 |  | PE-L1-4C4-13 | PE-L1-4C4-13 | HWDS-B1-014 | DONE(10/27) | DONE | 1 | 804 | B0-MCC-64601-P2013 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-13 | 0.4 | 400 | N | 360 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64601 | 400V MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-34009 | #1 STEAM HEATER B SHELL SIDE INLET MOV | 32_HOT WATER SUPPLY BUILDING | L1, L2, L3, PE | B064-016BT0012 → B064-016BT0013 → B064-016BT0014 → B064-016BT0015 → B064-016BT0016 → B064-016BT0309 → B064-016BT0037 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0055 → B025-996DT0019 → B025-016DT0056 → B025-016DT0057 → B025-016DT0135 → B078-016AC0005 → B078-006AC0016 → B078-006AC0010 → END
B0-MCC-64601 | -P20 | 14 |  | PE-L1-4C4-13 | PE-L1-4C4-13 | HWDS-B1-015 | DONE(10/27) | DONE | 1 | 805 | B0-MCC-64601-P2014 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-13 | 0.4 | 400 | N | 360 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64601 | 400V MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-34011 | #1 STEAM HEATER A TUBE SIDE OUTLET MOV | 32_HOT WATER SUPPLY BUILDING | L1, L2, L3, PE | B064-016BT0012 → B064-016BT0013 → B064-016BT0014 → B064-016BT0015 → B064-016BT0016 → B064-016BT0309 → B064-016BT0037 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0055 → B025-996DT0019 → B025-016DT0056 → B025-016DT0057 → B025-016DT0135 → B078-016AC0004 → B078-006AC0015 → B078-006AC0008 → END
B0-MCC-64601 | -P20 | 15 |  | PE-L1-4C4-13 | PE-L1-4C4-13 | HWDS-B1-016 | DONE(10/27) | DONE | 1 | 806 | B0-MCC-64601-P2015 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-13 | 0.4 | 400 | N | 360 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64601 | 400V MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-34013 | #1 STEAM HEATER B TUBE SIDE OUTLET MOV | 32_HOT WATER SUPPLY BUILDING | L1, L2, L3, PE | B064-016BT0012 → B064-016BT0013 → B064-016BT0014 → B064-016BT0015 → B064-016BT0016 → B064-016BT0309 → B064-016BT0037 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0055 → B025-996DT0019 → B025-016DT0056 → B025-016DT0057 → B025-016DT0135 → B078-016AC0005 → B078-006AC0016 → B078-006AC0011 → END
B1-MCC-64602 | -P20 | 31 |  | PE-L1-4C4-12 | PE-L1-4C4-12 | HWDS-B1-019 |  |  | 1 | 807 | B1-MCC-64602-P2031 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-12 | 0.75 | 400 | N | 160 | HOT WATER DISTRIBUTION SYSTEM | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-34015 | #11 GT AIR INTAKE SYSTEM HOT WATER INLET MOV | 1.1_MAIN BUILDING COMPLEX(GT#11) | L1, L2, L3, PE | B164-016ET0106 → B164-996ET0022 → M0504 → D0531-L42 → M0510 → D0502-L32 → M0326 → D0320-L25 → M0325 → D0319-L22 → M0324 → B161-006BC0001 → END
B1-MCC-64604 | -P20 | 11 |  | PE-L1-4C4-13 | PE-L1-4C4-13 | HWDS-B1-020 |  | DONE | 1 | 808 | B1-MCC-64604-P2011 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-13 | 0.75 | 400 | N | 220 | HOT WATER DISTRIBUTION SYSTEM | B1-MCC-64604 | 400V MCC FOR GT/HRSG#2 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-34017 | #12 GT AIR INTAKE SYSTEM HOT WATER INLET MOV | 1.1_MAIN BUILDING COMPLEX(GT#12) | L1, L2, L3, PE | B164-016AT0118 → B164-016AT0117 → B164-016AT0116 → B164-996AT0023 → M0504 → D0531-L32 → M0510 → D0502-L32 → M0326 → D0320-L36 → M0325 → D0319-L32 → M0324 → D0327-L26 → M0321 → D0317-L15 → M0320 → B161-006DC0001 → END
B0-MCC-64601 | -P20 | 16 |  | PE-L1-4C4-13 | PE-L1-4C4-13 | HWDS-B1-021 | DONE(10/27) | DONE | 1 | 809 | B0-MCC-64601-P2016 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-13 | 0.2 | 400 | N | 370 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64601 | 400V MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-34007 | #1 STEAM HEATER A SHELL SIDE BYPASS VENT MOV | 32_HOT WATER SUPPLY BUILDING | L1, L2, L3, PE | B064-016BT0012 → B064-016BT0013 → B064-016BT0014 → B064-016BT0015 → B064-016BT0016 → B064-016BT0309 → B064-016BT0037 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0055 → B025-996DT0019 → B025-016DT0056 → B025-016DT0057 → B025-016DT0058 → B078-016AC0001 → B078-006AC0013 → B078-006AC0032 → END
B0-MCC-64601 | -P20 | 17 |  | PE-L1-4C4-24 | PE-L1-4C4-24 | HWDS-B1-022 | DONE(10/27) | DONE | 1 | 810 | B0-MCC-64601-P2017 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-24 | 0.2 | 400 | N | 380 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64601 | 400V MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-34010 | #1 STEAM HEATER B SHELL SIDE BYPASS VENT MOV | 32_HOT WATER SUPPLY BUILDING | L1, L2, L3, PE | B064-016BT0012 → B064-016BT0013 → B064-016BT0014 → B064-016BT0015 → B064-016BT0016 → B064-016BT0309 → B064-016BT0037 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0055 → B025-996DT0019 → B025-016DT0056 → B025-016DT0057 → B025-016DT0058 → B078-016AC0002 → B078-006AC0014 → B078-006AC0034 → END
B0-MCC-64601 | -P20 | 18 |  | PE-L1-4C4-24 | PE-L1-4C4-24 | HWDS-B1-022-1 | DONE(10/27) | DONE | 1 | 811 | B0-MCC-64601-P2018 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-24 | 0.2 | 400 | N | 370 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64601 | 400V MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-34012 | #1 STEAM HEATER A SHELL SIDE OUTLET MOV | 32_HOT WATER SUPPLY BUILDING | L1, L2, L3, PE | B064-016BT0012 → B064-016BT0013 → B064-016BT0014 → B064-016BT0015 → B064-016BT0016 → B064-016BT0309 → B064-016BT0037 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0055 → B025-996DT0019 → B025-016DT0056 → B025-016DT0057 → B025-016DT0058 → B078-016AC0001 → B078-006AC0013 → B078-006AC0033 → END
B0-MCC-64601 | -P20 | 19 |  | PE-L1-4C4-14 | PE-L1-4C4-14 | HWDS-B1-022-2 | DONE(10/27) | DONE | 1 | 812 | B0-MCC-64601-P2019 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-14 | 0.2 | 400 | N | 380 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64601 | 400V MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-MOV-34014 | #1 STEAM HEATER B SHELL SIDE OUTLET MOV | 32_HOT WATER SUPPLY BUILDING | L1, L2, L3, PE | B064-016BT0012 → B064-016BT0013 → B064-016BT0014 → B064-016BT0015 → B064-016BT0016 → B064-016BT0309 → B064-016BT0037 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0055 → B025-996DT0019 → B025-016DT0056 → B025-016DT0057 → B025-016DT0058 → B078-016AC0002 → B078-006AC0014 → B078-006AC0035 → END
B0-MCC-64602 | -P20 | 07 |  | PE-L1-4C95/50-19 | HOLD (B1,B2위치 정정에 따른 Route 변경필요) | HWDS-B2-001 |  |  | 1 | 813 | B0-MCC-64602-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | HOLD (B1,B2위치 정정에 따른 Route 변경필요) | 75 | 400 | N | 350 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64602 | 400V MCC FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B2-P-34001 | #2 HOT WATER SUPPLY PUMP A | 32_HOT WATER SUPPLY BUILDING | L1, L2, L3, PE | B064-016BT0032 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0055 → B025-996DT0019 → B025-016DT0056 → B025-016DT0057 → B025-016DT0135 → B078-016AC0007 → B078-006AC0040 → B078-006AC0023 → END
B0-MCC-64602 | -P20 | 08 | HOLD (B1,B2위치 정정에 따른 Route 변경필요) | PE-L1-3C4-12 | PE-L1-3C4-12 | HWDS-B2-002 | DONE(10/27) | DONE | 1 | 814 | B0-MCC-64602-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-12 | 0.11 | 230 | N | 350 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64602 | 400V MCC FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B2-P-34001 | #2 HOT WATER SUPPLY PUMP A SPACE HEATER | 32_HOT WATER SUPPLY BUILDING | L1, N, PE | B064-016BT0032 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0055 → B025-996DT0019 → B025-016DT0056 → B025-016DT0057 → B025-016DT0135 → B078-016AC0007 → B078-006AC0040 → B078-007AC0001 → END
B0-MCC-64601 | -P20 | 20 |  | PE-L1-4C95/50-18 | HOLD (B1,B2위치 정정에 따른 Route 변경필요) | HWDS-B2-003 |  |  | 1 | 815 | B0-MCC-64601-P2020 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | HOLD (B1,B2위치 정정에 따른 Route 변경필요) | 75 | 400 | N | 350 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64601 | 400V MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B2-P-34002 | #2 HOT WATER SUPPLY PUMP B | 32_HOT WATER SUPPLY BUILDING | L1, L2, L3, PE | B064-016BT0012 → B064-016BT0013 → B064-016BT0014 → B064-016BT0015 → B064-016BT0016 → B064-016BT0309 → B064-016BT0037 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0055 → B025-996DT0019 → B025-016DT0056 → B025-016DT0057 → B025-016DT0135 → B078-016AC0008 → B078-006AC0041 → B078-006AC0024 → END
B0-MCC-64601 | -P20 | 21 |  | PE-L1-3C4-13 | HOLD (B1,B2위치 정정에 따른 Route 변경필요) | HWDS-B2-004 |  |  | 1 | 816 | B0-MCC-64601-P2021 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | HOLD (B1,B2위치 정정에 따른 Route 변경필요) | 0.11 | 230 | N | 360 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64601 | 400V MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B2-P-34002 | #2 HOT WATER SUPPLY PUMP B SPACE HEATER | 32_HOT WATER SUPPLY BUILDING | L1, N, PE | B064-016BT0012 → B064-016BT0013 → B064-016BT0014 → B064-016BT0015 → B064-016BT0016 → B064-016BT0309 → B064-016BT0037 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0055 → B025-996DT0019 → B025-016DT0056 → B025-016DT0057 → B025-016DT0135 → B078-016AC0008 → B078-006AC0041 → B078-007AC0002 → END
B0-MCC-64602 | -P20 | 09 |  | PE-L1-4C120/70-02 | HOLD (B1,B2위치 정정에 따른 Route 변경필요) | HWDS-B2-005 |  |  | 1 | 817 | B0-MCC-64602-P2009 | 0.6/1kV CU/XLPE/LSZH | 3C x 120sqmm + 1C X 70sqmm | HOLD (B1,B2위치 정정에 따른 Route 변경필요) | 75 | 400 | N | 360 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64602 | 400V MCC FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B2-P-34003 | #2 HOT WATER SUPPLY PUMP C | 32_HOT WATER SUPPLY BUILDING | L1, L2, L3, PE | B064-016AT0032 → B064-016AT0213 → B064-016AT0045 → B064-016AT0046 → B064-016AT0047 → B064-016AT0048 → B064-016AT0049 → B064-016AT0240 → B064-016AT0290 → B064-016AT0068 → B064-016AT0067 → B064-016AT0277 → B064-016AT0278 → B064-016AT0094 → B064-016AT0296 → B064-016AT0110 → B064-016AT0109 → B064-016AT0285 → B025-016CT0090 → B025-016CT0089 → B025-016CT0067 → B025-016CT0066 → B025-016CT0065 → B025-016CT0064 → B025-016CT0063 → B025-016CT0062 → B025-016CT0061 → B025-016CT0060 → B025-996CT0020 → B025-016CT0059 → B025-016CT0055 → B025-996CT0019 → B025-016CT0056 → B025-016CT0133 → B078-016AC0009 → B078-006AC0042 → B078-006AC0025 → END
B0-MCC-64602 | -P20 | 10 |  | PE-L1-3C4-13 | HOLD (B1,B2위치 정정에 따른 Route 변경필요) | HWDS-B2-006 |  |  | 1 | 818 | B0-MCC-64602-P2010 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | HOLD (B1,B2위치 정정에 따른 Route 변경필요) | 0.11 | 230 | N | 340 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64602 | 400V MCC FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B2-P-34003 | #2 HOT WATER SUPPLY PUMP C SPACE HEATER | 32_HOT WATER SUPPLY BUILDING | L1, N, PE | B064-016BT0032 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0055 → B025-996DT0019 → B025-016DT0056 → B025-016DT0057 → B025-016DT0135 → B078-016AC0009 → B078-006AC0042 → B078-007AC0003 → END
B0-MCC-64602 | -P20 | 11 |  | PE-L1-4C4-21 | PE-L1-4C4-21 | HWDS-B2-007 | DONE(10/12) | DONE | 1 | 819 | B0-MCC-64602-P2011 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-21 | 0.75 | 400 | N | 340 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64602 | 400V MCC FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B2-MOV-34001 | #2 HOT WATER SUPPLY PUMP A DISCHARGE MOV | 32_HOT WATER SUPPLY BUILDING | L1, L2, L3, PE | B064-016BT0032 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0055 → B025-996DT0019 → B025-016DT0056 → B025-016DT0057 → B025-016DT0135 → B078-016AC0007 → B078-006AC0040 → B078-006AC0017 → END
B0-MCC-64601 | -P20 | 22 |  | PE-L1-4C4-21 | PE-L1-4C4-21 | HWDS-B2-008 | DONE(10/12) | DONE | 1 | 820 | B0-MCC-64601-P2022 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-21 | 0.75 | 400 | N | 350 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64601 | 400V MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B2-MOV-34002 | #2 HOT WATER SUPPLY PUMP B DISCHARGE MOV | 32_HOT WATER SUPPLY BUILDING | L1, L2, L3, PE | B064-016BT0012 → B064-016BT0013 → B064-016BT0014 → B064-016BT0015 → B064-016BT0016 → B064-016BT0309 → B064-016BT0037 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0055 → B025-996DT0019 → B025-016DT0056 → B025-016DT0057 → B025-016DT0135 → B078-016AC0008 → B078-006AC0041 → B078-006AC0018 → END
B0-MCC-64602 | -P20 | 12 |  | PE-L1-4C4-21 | PE-L1-4C4-21 | HWDS-B2-009 | DONE(10/12) | DONE | 1 | 821 | B0-MCC-64602-P2012 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-21 | 0.75 | 400 | N | 340 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64602 | 400V MCC FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B2-MOV-34003 | #2 HOT WATER SUPPLY PUMP C DISCHARGE MOV | 32_HOT WATER SUPPLY BUILDING | L1, L2, L3, PE | B064-016BT0032 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0055 → B025-996DT0019 → B025-016DT0056 → B025-016DT0057 → B025-016DT0135 → B078-016AC0009 → B078-006AC0042 → B078-006AC0019 → END
B2-MCC-64601 | -P20 | 29 |  | PE-L1-4C4-21 | PE-L1-4C4-21 | HWDS-B2-010 |  |  | 1 | 822 | B2-MCC-64601-P2029 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-21 | 0.2 | 400 | N | 280 | HOT WATER DISTRIBUTION SYSTEM | B2-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-34004 | #2 HOT WATER HEAD TANK MAKE-UP LINE MOV | 1.1_MAIN BUILDING COMPLEX | L1, L2, L3, PE | B264-016CT0024 → B264-016CT0025 → B264-016CT0026 → B264-016CT0027 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L31 → M0406 → D0301-L37 → M0301 → B215-996BT0001 → B215-016BT0002 → B215-016BT0003 → B215-016BT0004 → B215-016BT0005 → B215-016BT0031 → B215-016BT0032 → B261-016AC0010 → END
B0-MCC-64602 | -P20 | 13 |  | PE-L1-4C4-20 | PE-L1-4C4-20 | HWDS-B2-011 | DONE(10/27) | DONE | 1 | 823 | B0-MCC-64602-P2013 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-20 | 0.4 | 400 | N | 360 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64602 | 400V MCC FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B2-MOV-34005 | #2 STEAM HEATER A TUBE SIDE INLET MOV | 32_HOT WATER SUPPLY BUILDING | L1, L2, L3, PE | B064-016BT0032 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0055 → B025-996DT0019 → B025-016DT0056 → B025-016DT0057 → B025-016DT0058 → B078-016AC0002 → B078-006AC0014 → B078-006AC0003 → END
B0-MCC-64602 | -P20 | 14 |  | PE-L1-4C4-20 | PE-L1-4C4-20 | HWDS-B2-012 | DONE(10/27) | DONE | 1 | 824 | B0-MCC-64602-P2014 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-20 | 0.4 | 400 | N | 360 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64602 | 400V MCC FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B2-MOV-34008 | #2 STEAM HEATER B TUBE SIDE INLET MOV | 32_HOT WATER SUPPLY BUILDING | L1, L2, L3, PE | B064-016BT0032 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0055 → B025-996DT0019 → B025-016DT0056 → B025-016DT0057 → B025-016DT0058 → B078-016AC0001 → B078-006AC0013 → B078-006AC0006 → END
B0-MCC-64602 | -P20 | 15 |  | PE-L1-4C4-20 | PE-L1-4C4-20 | HWDS-B2-013 | DONE(10/27) | DONE | 1 | 825 | B0-MCC-64602-P2015 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-20 | 0.4 | 400 | N | 360 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64602 | 400V MCC FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B2-MOV-34006 | #2 STEAM HEATER A SHELL SIDE INLET MOV | 32_HOT WATER SUPPLY BUILDING | L1, L2, L3, PE | B064-016BT0032 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0055 → B025-996DT0019 → B025-016DT0056 → B025-016DT0057 → B025-016DT0058 → B078-016AC0001 → B078-006AC0013 → B078-006AC0001 → END
B0-MCC-64602 | -P20 | 16 |  | PE-L1-4C4-20 | PE-L1-4C4-20 | HWDS-B2-014 | DONE(10/27) | DONE | 1 | 826 | B0-MCC-64602-P2016 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-20 | 0.4 | 400 | N | 360 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64602 | 400V MCC FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B2-MOV-34009 | #2 STEAM HEATER B SHELL SIDE INLET MOV | 32_HOT WATER SUPPLY BUILDING | L1, L2, L3, PE | B064-016BT0032 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0055 → B025-996DT0019 → B025-016DT0056 → B025-016DT0057 → B025-016DT0058 → B078-016AC0002 → B078-006AC0014 → B078-006AC0004 → END
B0-MCC-64602 | -P20 | 17 |  | PE-L1-4C4-20 | PE-L1-4C4-20 | HWDS-B2-015 | DONE(10/27) | DONE | 1 | 827 | B0-MCC-64602-P2017 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-20 | 0.4 | 400 | N | 360 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64602 | 400V MCC FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B2-MOV-34011 | #2 STEAM HEATER A TUBE SIDE OUTLET MOV | 32_HOT WATER SUPPLY BUILDING | L1, L2, L3, PE | B064-016BT0032 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0055 → B025-996DT0019 → B025-016DT0056 → B025-016DT0057 → B025-016DT0058 → B078-016AC0001 → B078-006AC0013 → B078-006AC0002 → END
B0-MCC-64602 | -P20 | 18 |  | PE-L1-4C4-19 | PE-L1-4C4-19 | HWDS-B2-016 | DONE(10/27) | DONE | 1 | 828 | B0-MCC-64602-P2018 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-19 | 0.4 | 400 | N | 360 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64602 | 400V MCC FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B2-MOV-34013 | #2 STEAM HEATER B TUBE SIDE OUTLET MOV | 32_HOT WATER SUPPLY BUILDING | L1, L2, L3, PE | B064-016BT0032 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0055 → B025-996DT0019 → B025-016DT0056 → B025-016DT0057 → B025-016DT0058 → B078-016AC0002 → B078-006AC0014 → B078-006AC0005 → END
B2-MCC-64601 | -P20 | 30 |  | PE-L1-4C4-19 | PE-L1-4C4-19 | HWDS-B2-019 |  |  | 1 | 829 | B2-MCC-64601-P2030 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-19 | 0.75 | 400 | N | 130 | HOT WATER DISTRIBUTION SYSTEM | B2-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-34015 | #21 GT AIR INTAKE SYSTEM HOT WATER INLET MOV | 1.1_MAIN BUILDING COMPLEX(GT#21) | L1, L2, L3, PE | B264-016AT0025 → B264-016AT0026 → B264-016AT0027 → B264-016AT0028 → B264-996AT0012 → M0407 → D0302-L31 → M0302 → D0303-L31 → M0303 → D0305-L22 → M0306 → B261-006DC0001 → END
B2-MCC-64604 | -P20 | 09 |  | PE-L1-4C4-19 | PE-L1-4C4-19 | HWDS-B2-020 |  |  | 1 | 830 | B2-MCC-64604-P2009 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-19 | 0.75 | 400 | N | 60 | HOT WATER DISTRIBUTION SYSTEM | B2-MCC-64604 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, PE | B2-MOV-34017 | #22 GT AIR INTAKE SYSTEM HOT WATER INLET MOV | 1.1_MAIN BUILDING COMPLEX(GT#22) | L1, L2, L3, PE | B264-016CT0047 → B264-996CT0017 → M0407 → D0302-L41 → M0302 → B261-006BC0001 → END
B0-MCC-64602 | -P20 | 19 |  | PE-L1-4C4-19 | PE-L1-4C4-19 | HWDS-B2-021 | DONE(10/27) | DONE | 1 | 831 | B0-MCC-64602-P2019 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-19 | 0.2 | 400 | N | 350 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64602 | 400V MCC FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B2-MOV-34007 | #2 STEAM HEATER A SHELL SIDE BYPASS VENT MOV | 32_HOT WATER SUPPLY BUILDING | L1, L2, L3, PE | B064-016BT0032 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0055 → B025-996DT0019 → B025-016DT0056 → B025-016DT0057 → B025-016DT0135 → B078-016AC0004 → B078-006AC0015 → B078-006AC0036 → END
B0-MCC-64602 | -P20 | 20 |  | PE-L1-4C4-19 | PE-L1-4C4-19 | HWDS-B2-022 | DONE(10/27) | DONE | 1 | 832 | B0-MCC-64602-P2020 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-19 | 0.2 | 400 | N | 350 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64602 | 400V MCC FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B2-MOV-34010 | #2 STEAM HEATER B SHELL SIDE BYPASS VENT MOV | 32_HOT WATER SUPPLY BUILDING | L1, L2, L3, PE | B064-016BT0032 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0055 → B025-996DT0019 → B025-016DT0056 → B025-016DT0057 → B025-016DT0135 → B078-016AC0005 → B078-006AC0016 → B078-006AC0038 → END
B0-MCC-64602 | -P20 | 21 |  | PE-L1-4C4-19 | PE-L1-4C4-19 | HWDS-B2-023 | DONE(10/27) | DONE | 1 | 833 | B0-MCC-64602-P2021 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-19 | 0.2 | 400 | N | 350 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64602 | 400V MCC FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B2-MOV-34012 | #2 STEAM HEATER A SHELL SIDE OUTLET MOV | 32_HOT WATER SUPPLY BUILDING | L1, L2, L3, PE | B064-016BT0032 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0055 → B025-996DT0019 → B025-016DT0056 → B025-016DT0057 → B025-016DT0135 → B078-016AC0004 → B078-006AC0015 → B078-006AC0037 → END
B0-MCC-64602 | -P20 | 22 |  | PE-L1-4C4-19 | PE-L1-4C4-19 | HWDS-B2-024 | DONE(10/27) | DONE | 1 | 834 | B0-MCC-64602-P2022 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-19 | 0.2 | 400 | N | 350 | HOT WATER DISTRIBUTION SYSTEM | B0-MCC-64602 | 400V MCC FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B2-MOV-34014 | #2 STEAM HEATER B SHELL SIDE OUTLET MOV | 32_HOT WATER SUPPLY BUILDING | L1, L2, L3, PE | B064-016BT0032 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B064-016BT0295 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0055 → B025-996DT0019 → B025-016DT0056 → B025-016DT0057 → B025-016DT0135 → B078-016AC0005 → B078-006AC0016 → B078-006AC0039 → END
B1-MCC-64603 | -P20 | 11 | PE-L1-5C120/70-03 유지(10/6) | PE-L1-5C120/70-03 | PE-L1-5C120/70-03 | CRA-C-001 |  |  | 1 | 835 | B1-MCC-64603-P2011 | 0.6/1kV CU/XLPE/LSZH | 4C x 120sqmm + 1C X 70sqmm | PE-L1-5C120/70-03 | 57.75 | 400 | N | 360 | CRANE & HOIST | B1-MCC-64603 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B0-HO-55010 | OVERHEAD CRANE FOR GAS TURBINE #A | 1.1_MAIN BUILDING COMPLEX | L1, L2, L3, N, PE | B164-016AT0094 → B164-016AT0093 → B164-016AT0092 → B164-996AT0022 → M0504 → D0531-L44 → M0510 → D0502-L34 → M0326 → D0320-L34 → M0325 → D0319-L25 → M0324 → D0327-L25 → M0321 → D0317-L25 → M0320 → D0323-L15 → M0319 → D0316-L22 → M0318 → D0315-L21 → M0315 → D0313-L11 → M0312 → B213-006CC0024 → B213-016CC0003 → END
B1-MCC-64602 | -P20 | 32 |  | PE-L1-5C4-01 | PE-L1-5C4-01 | CRA-C-003 |  | DONE | 1 | 836 | B1-MCC-64602-P2032 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-01 | 4.57 | 400 | N | 110 | CRANE & HOIST | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B1-HO-55011 | JIB CRANE FOR GT AIR INLET FILTER #1A | 1.1_MAIN BUILDING COMPLEX (NEARBY INLET FILTER, ON THE ROOF OF BLDG) | L1, L2, L3, N, PE | B164-016ET0106 → B164-996ET0022 → M0504 → D0531-L26 → M0510 → D0502-L26 → M0326 → D0320-L26 → M0325 → B161-006BC0011 → END
B2-MCC-64602 | -P20 | 28 | From변경 | PE-L1-5C6-02 | PE-L1-5C6-02 | CRA-C-004-001 | B2-MCC-64602-P2028 |  | 1 | 837 | B2-MCC-64604-P2028 | 0.6/1kV CU/XLPE/LSZH | 5C x 6sqmm | PE-L1-5C6-02 | 4.57 | 400 | N | 80 | CRANE & HOIST | B2-MCC-64604 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, N, PE | B2-HO-55012 | JIB CRANE FOR GT AIR INLET FILTER #2A | 1.1_MAIN BUILDING COMPLEX (NEARBY INLET FILTER, ON THE ROOF OF BLDG) | L1, L2, L3, N, PE | B264-016BT0047 → B264-996BT0013 → M0407 → D0302-L34 → M0302 → D0303-L34 → M0303 → B261-006BC0011 → END
B1-MCC-59602 | -P20 | 22 | 재배정 'PE-L1-5C70/35유지(10/6) | PE-L1-5C70/35-02 | PE-L1-5C70/35-01 | CRA-C-005 |  |  | 1 | 838 | B1-MCC-59602-P2022 | 0.6/1kV CU/XLPE/LSZH | 4C x 70sqmm + 1C X 35sqmm | PE-L1-5C70/35-01 | 61.75 | 400 | N | 130 | CRANE & HOIST | B1-MCC-59602 | 400V MCC FOR ST #1 FOR BLOCK #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, N, PE | B0-HO-55030 | OVERHEAD CRANE FOR STEAM TURBINE | 1.1_MAIN BUILDING COMPLEX / STEAM TURBINE (ST) | L1, L2, L3, N, PE | B159-006AT0006 → B159-006AT0018 → B159-006AT0017 → D0314-L22 → M0315 → D0313-L12 → M0312 → D0330-L21 → M0314 → B213-006CC0022 → END
B0-MCC-72602 | -P20 | 04 |  | PE-L1-5C6-02 | PE-L1-5C6-02 | CRA-C-006 |  |  | 1 | 839 | B0-MCC-72602-P2004 | 0.6/1kV CU/XLPE/LSZH | 5C x 6sqmm | PE-L1-5C6-02 | 8.15 | 400 | N | 100 | CRANE & HOIST | B0-MCC-72602 | 400V MCC FOR WORKSHOP - B | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, L2, L3, N, PE | B0-HO-55040 | SUSPENSION CRANE FOR WORKSHOP & STORAGE | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, L2, L3, N, PE | B071-006AT0001 → B071-006BT0002 → B071-016AC0005 → B071-016AC0003 → B071-016AC0007 → END
B1-MCC-64602 | -P20 | 33 |  | PE-L1-5C6-01 | PE-L1-5C6-01 | CRA-C-010-001 |  |  | 1 | 840 | B1-MCC-64602-P2033 | 0.6/1kV CU/XLPE/LSZH | 5C x 6sqmm | PE-L1-5C6-01 | 7.75 | 400 | N | 155 | CRANE & HOIST | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B1-HO-55021 | SUSPENSION CRANE FOR GENERATOR COOLER #A | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, L2, L3, N, PE | B164-016ET0106 → B164-996ET0022 → M0504 → D0531-L26 → M0510 → D0502-L26 → M0326 → D0320-L26 → M0325 → D0319-L22 → M0324 → B161-006BC0002 → B161-006BC0024 → END
B1-MCC-64604 | -P20 | 12 |  | PE-L1-5C10-01 | PE-L1-5C10-01 | CRA-C-010-002 |  | DONE | 1 | 841 | B1-MCC-64604-P2012 | 0.6/1kV CU/XLPE/LSZH | 5C x 10sqmm | PE-L1-5C10-01 | 7.75 | 400 | N | 210 | CRANE & HOIST | B1-MCC-64604 | 400V MCC FOR GT/HRSG#2 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B1-HO-55022 | SUSPENSION CRANE FOR GENERATOR COOLER #B | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, L2, L3, N, PE | B164-016AT0118 → B164-016AT0117 → B164-016AT0116 → B164-996AT0023 → M0504 → D0531-L25 → M0510 → D0502-L25 → M0326 → D0320-L35 → M0325 → D0319-L31 → M0324 → D0327-L25 → M0321 → D0317-L25 → M0320 → B161-006DC0024 → END
B2-MCC-64602 | -P20 | 29 |  | PE-L1-5C10-02 | PE-L1-5C10-02 | CRA-C-010-003 |  |  | 1 | 842 | B2-MCC-64602-P2029 | 0.6/1kV CU/XLPE/LSZH | 5C x 10sqmm | PE-L1-5C10-02 | 7.75 | 400 | N | 150 | CRANE & HOIST | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, N, PE | B2-HO-55023 | SUSPENSION CRANE FOR GENERATOR COOLER #C | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, L2, L3, N, PE | B264-016BT0045 → B264-016BT0046 → B264-016BT0047 → B264-996BT0013 → M0407 → D0302-L33 → M0302 → D0303-L33 → M0303 → D0305-L24 → M0306 → B261-006DC0002 → B261-006DC0024 → END
B2-MCC-64604 | -P20 | 10 |  | PE-L1-5C6-02 | PE-L1-5C6-02 | CRA-C-010-004 |  |  | 1 | 843 | B2-MCC-64604-P2010 | 0.6/1kV CU/XLPE/LSZH | 5C x 6sqmm | PE-L1-5C6-02 | 7.75 | 400 | N | 70 | CRANE & HOIST | B2-MCC-64604 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, N, PE | B2-HO-55024 | SUSPENSION CRANE FOR GENERATOR COOLER #D | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, L2, L3, N, PE | B264-016CT0047 → B264-996CT0017 → M0407 → D0302-L26 → M0302 → B261-006BC0002 → B261-006BC0024 → END
B1-MCC-64602 | -P20 | 34 | From변경 | PE-L1-5C16-01 | PE-L1-5C16-01 | CRA-C-011 | B1-MCC-64602-P2034 |  | 1 | 844 | B1-MCC-64601-P2034 | 0.6/1kV CU/XLPE/LSZH | 5C x 16sqmm | PE-L1-5C16-01 | 9.55 | 400 | N | 280 | CRANE & HOIST | B1-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B1-HO-55066 | ELECTRIC HOIST FOR HRSG FEEDWATER PUMP #A | 1.1_MAIN BUILDING COMPLEX / HRSG #11 | L1, L2, L3, N, PE | B164-016AT0091 → B164-996AT0022 → M0504 → D0531-L24 → M0510 → D0517-L14 → M0501 → D0503-L35 → M0502 → D0504-L35 → M0503 → D0501-L35 → M0328 → D0324-L35 → M0329 → B114-996DT0081 → B114-016DT0082 → B114-016DT0083 → B114-016DT0084 → B114-016DT0096 → B114-016DT0097 → B161-016AC0002 → END
B1-MCC-64603 | -P20 | 12 |  | PE-L1-5C16-01 | PE-L1-5C16-01 | CRA-C-012 |  |  | 1 | 845 | B1-MCC-64603-P2012 | 0.6/1kV CU/XLPE/LSZH | 5C x 16sqmm | PE-L1-5C16-01 | 9.55 | 400 | N | 340 | CRANE & HOIST | B1-MCC-64603 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B1-HO-55067 | ELECTRIC HOIST FOR HRSG FEEDWATER PUMP #B | 1.1_MAIN BUILDING COMPLEX / HRSG #12 | L1, L2, L3, N, PE | B164-016AT0094 → B164-016AT0093 → B164-016AT0092 → B164-996AT0022 → M0504 → D0531-L25 → M0510 → D0517-L15 → M0501 → D0503-L36 → M0502 → D0504-L36 → M0503 → D0501-L36 → M0328 → D0324-L36 → M0329 → B114-996CT0071 → B114-016CT0072 → B114-016CT0073 → B114-016CT0074 → B114-016CT0075 → B114-016CT0076 → B114-016CT0087 → B161-016CC0002 → END
B2-MCC-64602 | -P20 | 30 |  | PE-L1-5C16-01 | PE-L1-5C16-01 | CRA-C-013 |  |  | 1 | 846 | B2-MCC-64602-P2030 | 0.6/1kV CU/XLPE/LSZH | 5C x 16sqmm | PE-L1-5C16-01 | 9.55 | 400 | N | 310 | CRANE & HOIST | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, N, PE | B2-HO-55068 | ELECTRIC HOIST FOR HRSG FEEDWATER PUMP #C | 1.1_MAIN BUILDING COMPLEX / HRSG #21 | L1, L2, L3, N, PE | B264-016AT0045 → B264-016AT0046 → B264-016AT0209 → B264-016AT0026 → B264-016AT0027 → B264-016AT0225 → B264-996AT0011 → M0405 → D0421-L31 → M0406 → D0301-L37 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B215-016AT0050 → B215-016AT0051 → B215-016AT0064 → B215-016AT0065 → B215-016AT0066 → B215-016AT0055 → B261-016CC0002 → END
B2-MCC-64604 | -P20 | 11 |  | PE-L1-5C16-02 | PE-L1-5C16-02 | CRA-C-014 |  |  | 1 | 847 | B2-MCC-64604-P2011 | 0.6/1kV CU/XLPE/LSZH | 5C x 16sqmm | PE-L1-5C16-02 | 9.55 | 400 | N | 250 | CRANE & HOIST | B2-MCC-64604 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, N, PE | B2-HO-55069 | ELECTRIC HOIST FOR HRSG FEEDWATER PUMP #D | 1.1_MAIN BUILDING COMPLEX / HRSG #22 | L1, L2, L3, N, PE | B264-016CT0047 → B264-016CT0209 → B264-016CT0026 → B264-016CT0027 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L32 → M0406 → D0301-L36 → M0301 → B215-996BT0001 → B215-016BT0002 → B215-016BT0003 → B215-016BT0004 → B261-016AC0002 → END
B1-MCC-69603 | -P20 | 11 |  | PE-L1-5C4-01 | PE-L1-5C4-01 | CRA-C-016 |  |  | 1 | 848 | B1-MCC-69603-P2011 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-01 | 9.55 | 400 | N | 80 | CRANE & HOIST | B1-MCC-69603 | 400V MCC FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, L2, L3, N, PE | B1-HO-55070 | ELECTRIC HOIST FOR CEP #A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, N, PE | B169-006AT0009 → B169-006AT0010 → B169-006AT0011 → B169-006AT0012 → B169-006AT0013 → B169-006AT0014 → B016-006AC0011 → END
B2-MCC-69601 | -P20 | 12 |  | PE-L1-5C4-03 | PE-L1-5C4-03 | CRA-C-017 |  |  | 1 | 849 | B2-MCC-69601-P2012 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-03 | 9.55 | 400 | N | 50 | CRANE & HOIST | B2-MCC-69601 | 400V MCC FOR ACC#2 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, N, PE | B2-HO-55071 | ELECTRIC HOIST FOR CEP #B | 16_CEP BUILDING W/ACC LER | L1, L2, L3, N, PE | B169-006AT0020 → B169-006AT0021 → B016-006BC0011 → END
B1-MCC-64602 | -P20 | 35 | From변경 | PE-L1-5C6-01 | PE-L1-5C6-01 | CRA-C-021-001 | B1-MCC-64602-P2035 |  | 1 | 850 | B1-MCC-64601-P2035 | 0.6/1kV CU/XLPE/LSZH | 5C x 6sqmm | PE-L1-5C6-01 | 3.97 | 400 | N | 255 | CRANE & HOIST | B1-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B1-HO-55061 | ELECTRIC HOIST FOR HRSG #1 Drum Area Hoist | 1.1_MAIN BUILDING COMPLEX / HRSG #11 (Above Drum level) | L1, L2, L3, N, PE | B164-016AT0091 → B164-996AT0022 → M0504 → D0531-L24 → M0510 → D0517-L14 → M0501 → D0503-L35 → M0502 → D0504-L35 → M0503 → D0501-L35 → M0328 → D0324-L35 → M0329 → B114-996DT0081 → B114-016DT0082 → B114-016DT0083 → B114-016DT0084 → B114-016DT0096 → B114-016DT0097 → B161-016AC0019 → END
B1-MCC-64604 | -P20 | 13 |  | PE-L1-5C10-01 | PE-L1-5C10-01 | CRA-C-021-002 |  |  | 1 | 851 | B1-MCC-64604-P2013 | 0.6/1kV CU/XLPE/LSZH | 5C x 10sqmm | PE-L1-5C10-01 | 3.97 | 400 | N | 350 | CRANE & HOIST | B1-MCC-64604 | 400V MCC FOR GT/HRSG#2 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B1-HO-55062 | ELECTRIC HOIST FOR HRSG #2 Drum Area Hoist | 1.1_MAIN BUILDING COMPLEX / HRSG #12 (Above Drum level) | L1, L2, L3, N, PE | B164-016AT0118 → B164-016AT0117 → B164-016AT0116 → B164-996AT0023 → M0504 → D0531-L25 → M0510 → D0517-L15 → M0501 → D0503-L36 → M0502 → D0504-L36 → M0503 → D0501-L36 → M0328 → D0324-L36 → M0329 → B114-996CT0071 → B114-016CT0072 → B114-016CT0073 → B114-016CT0074 → B114-016CT0075 → B114-016CT0076 → B114-016CT0087 → B114-016CT0088 → B114-016CT0089 → B161-016CC0021 → END
B2-MCC-64602 | -P20 | 31 | From변경 | PE-L1-5C10-02 | PE-L1-5C10-02 | CRA-C-021-003 | B2-MCC-64602-P2031 |  | 1 | 852 | B2-MCC-64604-P2031 | 0.6/1kV CU/XLPE/LSZH | 5C x 10sqmm | PE-L1-5C10-02 | 3.97 | 400 | N | 310 | CRANE & HOIST | B2-MCC-64604 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, N, PE | B2-HO-55063 | ELECTRIC HOIST FOR HRSG #3 Drum Area Hoist | 1.1_MAIN BUILDING COMPLEX / HRSG #21 (Above Drum level) | L1, L2, L3, N, PE | B264-016AT0047 → B264-016AT0209 → B264-016AT0026 → B264-016AT0027 → B264-016AT0225 → B264-996AT0011 → M0405 → D0421-L31 → M0406 → D0301-L37 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B215-016AT0050 → B215-016AT0051 → B215-016AT0064 → B215-016AT0065 → B215-016AT0066 → B215-016AT0055 → B215-016AT0056 → B215-016AT0057 → B261-016CC0016 → END
B2-MCC-64604 | -P20 | 12 |  | PE-L1-5C6-02 | PE-L1-5C6-02 | CRA-C-021-004 |  |  | 1 | 853 | B2-MCC-64604-P2012 | 0.6/1kV CU/XLPE/LSZH | 5C x 6sqmm | PE-L1-5C6-02 | 3.97 | 400 | N | 220 | CRANE & HOIST | B2-MCC-64604 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, N, PE | B2-HO-55064 | ELECTRIC HOIST FOR HRSG #4 Drum Area Hoist | 1.1_MAIN BUILDING COMPLEX / HRSG #22 (Above Drum level) | L1, L2, L3, N, PE | B264-016CT0047 → B264-016CT0209 → B264-016CT0026 → B264-016CT0027 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L31 → M0406 → D0301-L37 → M0301 → B215-996BT0001 → B215-016BT0002 → B215-016BT0003 → B215-016BT0004 → B261-016AC0017 → END
B0-MCC-49602 | -P20 | 27 |  | PE-L1-5C16-02 | PE-L1-5C16-02 | CRA-C-022 | DONE(10/12) | DONE | 1 | 854 | B0-MCC-49602-P2027 | 0.6/1kV CU/XLPE/LSZH | 5C x 16sqmm | PE-L1-5C16-02 | 7.75 | 400 | N | 350 | CRANE & HOIST | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, N, PE | B0-HO-55050 | SUSPENSION CRANE FOR WATER DISTRIBUTION PUMP STATION | 15.1_WATER DISTRIBUTION PUMP STATION | L1, L2, L3, N, PE | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L16 → M0207 → D0203-L22 → M0206 → D0205-L22 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B025-016ET0030 → B025-016ET0031 → B025-016ET0032 → B025-016ET0033 → B025-016ET0034 → B025-996ET0006 → M0202 → D0201-L13 → M0201 → B079-006AC0013 → END
B0-MCC-49602 | -P20 | 28 |  | PE-L1-5C10-01 | PE-L1-5C10-01 | CRA-C-023 |  |  | 1 | 855 | B0-MCC-49602-P2028 | 0.6/1kV CU/XLPE/LSZH | 5C x 10sqmm | PE-L1-5C10-01 | 5.19 | 400 | N | 180 | CRANE & HOIST | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, N, PE | B0-HO-55051 | SUSPENSION CRANE FOR WATER SUPPLY PUMPING STATION | 13.4_WATER SUPPLY PUMPING STATION | L1, L2, L3, N, PE | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L14 → M0207 → D0206-L11 → M0208 → D0207-L11 → M0210 → D0209-L11 → M0209 → B038-006BC0010 → END
B0-MCC-49602 | -P20 | 29 |  | PE-L1-5C10-01 | PE-L1-5C10-01 | CRA-C-024 | DONE(10/27) | DONE | 1 | 856 | B0-MCC-49602-P2029 | 0.6/1kV CU/XLPE/LSZH | 5C x 10sqmm | PE-L1-5C10-01 | 7.75 | 400 | N | 210 | CRANE & HOIST | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, N, PE | B0-HO-55053 | SUSPENSION CRANE FOR RAW WATER & FIRE WATER PUMP HOUSE | 12.1_RAW WATER&FIRE WATER PUMP HOUSE | L1, L2, L3, N, PE | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L16 → M0207 → D0203-L22 → M0206 → D0205-L22 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B038-016AC0004 → END
B1-MCC-64601 | -P20 | 27 |  | PE-L1-5C10-01 | PE-L1-5C10-01 | CRA-C-025-001 | DONE(10/6) | DONE | 1 | 857 | B1-MCC-64601-P2027 | 0.6/1kV CU/XLPE/LSZH | 5C x 10sqmm | PE-L1-5C10-01 | 7.75 | 400 | N | 180 | CRANE & HOIST | B1-MCC-64601 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B1-HO-55052 | SUSPENSION CRANE FOR CCW PUMP BUILDING | 8.1_CCW PUMP/HEAT EXCHANGER BUILDING | L1, L2, L3, N, PE | B164-016AT0090 → B164-016AT0216 → B164-016AT0215 → B164-016AT0055 → B164-016AT0056 → B164-016AT0057 → B164-016AT0058 → B164-016AT0059 → B164-016AT0060 → B164-016AT0254 → B164-016AT0253 → B164-016AT0252 → B164-996AT0021 → M0505 → D0524-L11 → M0506 → D0505-L11 → M0507 → D0506-L11 → M0508 → B132-006AC0051 → END
B2-MCC-64602 | -P20 | 32 |  | PE-L1-5C6-02 | PE-L1-5C6-02 | CRA-C-025-002 |  |  | 1 | 858 | B2-MCC-64602-P2032 | 0.6/1kV CU/XLPE/LSZH | 5C x 6sqmm | PE-L1-5C6-02 | 7.75 | 400 | N | 160 | CRANE & HOIST | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, N, PE | B2-HO-55054 | SUSPENSION CRANE FOR CCW PUMP BUILDING | 8.2_CCW PUMP/HEAT EXCHANGER BUILDING | L1, L2, L3, N, PE | B264-016BT0045 → B264-016BT0205 → B264-016BT0024 → B264-016BT0206 → B264-996BT0001 → M0401 → D0403-L11 → M0402 → D0402-L11 → M0424 → D0401-L11 → M0404 → B232-006AC0051 → END
B0-MCC-49602 | -P20 | 30 |  | PE-L1-5C25/16-01 | PE-L1-5C25/16-01 | CRA-C-027 |  |  | 1 | 859 | B0-MCC-49602-P2030 | 0.6/1kV CU/XLPE/LSZH | 4C x 25sqmm + 1C X 16sqmm | PE-L1-5C25/16-01 | 8.15 | 400 | N | 400 | CRANE & HOIST | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, N, PE | B0-HO-55060 | SUSPENSION CRANE FOR DIESEL OIL PUMP STATION | 21_DIESEL OIL PUMP STATION | L1, L2, L3, N, PE | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L15 → M0207 → D0203-L21 → M0206 → D0205-L21 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B025-016ET0020 → B025-016ET0019 → B025-016ET0018 → B025-016ET0017 → B025-016ET0016 → B025-996ET0003 → M0103 → B070-006AC0010 → END
B1-MCC-64602 | -P20 | 36 |  | PE-L1-5C4-01 | PE-L1-5C4-01 | CRA-C-028-001 |  |  | 1 | 860 | B1-MCC-64602-P2036 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-01 | 4.87 | 400 | N | 120 | CRANE & HOIST | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B1-HO-55015 | ELECTRIC HOIST FOR GT GCB #1A | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, L2, L3, N, PE | B164-016ET0106 → B164-996ET0022 → M0504 → D0531-L37 → M0510 → D0502-L41 → M0326 → D0320-L41 → M0325 → B161-006BC0016 → END
B2-MCC-64602 | -P20 | 33 | From변경 | PE-L1-5C6-02 | PE-L1-5C6-02 | CRA-C-028-003 | B2-MCC-64602-P2033 |  | 1 | 861 | B2-MCC-64604-P2033 | 0.6/1kV CU/XLPE/LSZH | 5C x 6sqmm | PE-L1-5C6-02 | 4.87 | 400 | N | 100 | CRANE & HOIST | B2-MCC-64604 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, N, PE | B2-HO-55016 | ELECTRIC HOIST FOR GT GCB #2A | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, L2, L3, N, PE | B264-016BT0047 → B264-996BT0013 → M0407 → D0302-L41 → M0302 → D0303-L41 → M0303 → B261-006BC0016 → END
B1-MCC-64602 | -P20 | 37 |  | PE-L1-5C16-01 | PE-L1-5C16-01 | SUM-C-094 |  |  | 1 | 862 | B1-MCC-64602-P2037 | 0.6/1kV CU/XLPE/LSZH | 5C x 16sqmm | PE-L1-5C16-01 | 15.5 | 400 | N | 200 | WASTE WATER TRANSFER SYSTEM | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B0-LCP-3901 | HRSG #1 BLOWDOWN TANK AREA SUMP PUMP_LCP | 1.1_MAIN BUILDING COMPLEX / HRSG BLOWDOWN PIT | L1, L2, L3, N, PE | B164-016ET0106 → B164-996ET0022 → M0504 → D0531-L24 → M0510 → D0517-L14 → M0501 → D0503-L35 → M0502 → D0504-L35 → M0503 → D0501-L35 → M0328 → D0324-L35 → M0329 → B161-006AC0006 → B161-016AC0019 → B161-016AC0022 → END
B0-LCP-3901 | -P20 | 01 |  | PE-L1-4C4-26 | PE-L1-4C4-26 | SUM-C-095 |  |  | 1 | 863 | B0-LCP-3901-P2001 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-26 | 7.5 | 400 | N | 20 | WASTE WATER TRANSFER SYSTEM | B0-LCP-3901 | SUMP LCP | HRSG #1 BLOWDOWN TANK AREA SUMP PUMP_LCP | L1, L2, L3, PE | B0-M-39001A | UNIT #11 HRSG BLOWDOWN AREA CHEMICAL SUMP PUMP #1_MOTOR (FROM LCP, CABLE ONLY) | 1.1_MAIN BUILDING COMPLEX / HRSG BLOWDOWN PIT | L1, L2, L3, PE | B161-016AC0025 → END
B0-LCP-3901 | -P20 | 02 |  | PE-L1-3C4-24 | PE-L1-3C4-24 | SUM-C-095-1 |  |  | 1 | 864 | B0-LCP-3901-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-24 | 0.03 | 230 | N | 20 | WASTE WATER TRANSFER SYSTEM | B0-LCP-3901 | SUMP LCP | HRSG #1 BLOWDOWN TANK AREA SUMP PUMP_LCP | L1, N, PE | B0-M-39001A | UNIT #11 HRSG BLOWDOWN AREA CHEMICAL SUMP PUMP #1_MOTOR S/H (FROM LCP, CABLE ONLY) | 1.1_MAIN BUILDING COMPLEX / HRSG BLOWDOWN PIT | L1, N, PE | B161-017AC0007 → END
B0-LCP-3901 | -P20 | 03 |  | PE-L1-4C4-26 | PE-L1-4C4-26 | SUM-C-096 |  |  | 1 | 865 | B0-LCP-3901-P2003 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-26 | 7.5 | 400 | N | 20 | WASTE WATER TRANSFER SYSTEM | B0-LCP-3901 | SUMP LCP | HRSG #1 BLOWDOWN TANK AREA SUMP PUMP_LCP | L1, L2, L3, PE | B0-M-39001B | UNIT #1 HRSG BLOWDOWN TANK AREA SUMP PUMP #2_MOTOR (FROM LCP, CABLE ONLY) | 1.1_MAIN BUILDING COMPLEX / HRSG BLOWDOWN PIT | L1, L2, L3, PE | B161-016AC0026 → END
B0-LCP-3901 | -P20 | 04 |  | PE-L1-3C4-24 | PE-L1-3C4-24 | SUM-C-096-1 |  |  | 1 | 866 | B0-LCP-3901-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-24 | 0.03 | 230 | N | 20 | WASTE WATER TRANSFER SYSTEM | B0-LCP-3901 | SUMP LCP | HRSG #1 BLOWDOWN TANK AREA SUMP PUMP_LCP | L1, N, PE | B0-M-39001B | UNIT #11 HRSG BLOWDOWN AREA CHEMICAL SUMP PUMP #2_MOTOR S/H (FROM LCP, CABLE ONLY) | 1.1_MAIN BUILDING COMPLEX / HRSG BLOWDOWN PIT | L1, N, PE | B161-017AC0008 → END
B1-MCC-64603 | -P20 | 13 |  | PE-L1-5C25/16-01 | PE-L1-5C25/16-01 | SUM-C-097 |  |  | 1 | 867 | B1-MCC-64603-P2013 | 0.6/1kV CU/XLPE/LSZH | 4C x 25sqmm + 1C X 16sqmm | PE-L1-5C25/16-01 | 15.5 | 400 | N | 310 | WASTE WATER TRANSFER SYSTEM | B1-MCC-64603 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B0-LCP-3903 | HRSG #2 BLOWDOWN TANK AREA SUMP PUMP_LCP | 1.1_MAIN BUILDING COMPLEX / HRSG BLOWDOWN PIT | L1, L2, L3, N, PE | B164-016AT0094 → B164-016AT0093 → B164-016AT0092 → B164-996AT0022 → M0504 → D0531-L25 → M0510 → D0517-L15 → M0501 → D0503-L36 → M0502 → D0504-L36 → M0503 → D0501-L36 → M0328 → D0324-L36 → M0329 → B114-996CT0071 → B114-016CT0072 → B114-016CT0073 → B114-016CT0074 → B114-016CT0075 → B161-016CC0026 → B161-006CC0006 → B161-016CC0022 → B161-016CC0015 → END
B0-LCP-3903 | -P20 | 01 |  | PE-L1-4C4-26 | PE-L1-4C4-26 | SUM-C-098 |  |  | 1 | 868 | B0-LCP-3903-P2001 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-26 | 7.5 | 400 | N | 20 | WASTE WATER TRANSFER SYSTEM | B0-LCP-3903 | SUMP LCP | HRSG #2 BLOWDOWN TANK AREA SUMP PUMP_LCP | L1, L2, L3, PE | B0-M-39003A | UNIT #2 HRSG BLOWDOWN TANK AREA SUMP PUMP #1_MOTOR (FROM LCP, CABLE ONLY) | 1.1_MAIN BUILDING COMPLEX / HRSG BLOWDOWN PIT | L1, L2, L3, PE | B161-016CC0036 → END
B0-LCP-3903 | -P20 | 02 |  | PE-L1-3C4-24 | PE-L1-3C4-24 | SUM-C-098-1 |  |  | 1 | 869 | B0-LCP-3903-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-24 | 0.03 | 230 | N | 20 | WASTE WATER TRANSFER SYSTEM | B0-LCP-3903 | SUMP LCP | HRSG #2 BLOWDOWN TANK AREA SUMP PUMP_LCP | L1, N, PE | B0-M-39003A | UNIT #2 HRSG BLOWDOWN AREA CHEMICAL SUMP PUMP #1_MOTOR S/H (FROM LCP, CABLE ONLY) | 1.1_MAIN BUILDING COMPLEX / HRSG BLOWDOWN PIT | L1, N, PE | B161-017CC0007 → END
B0-LCP-3903 | -P20 | 03 |  | PE-L1-4C4-26 | PE-L1-4C4-26 | SUM-C-099 |  |  | 1 | 870 | B0-LCP-3903-P2003 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-26 | 7.5 | 400 | N | 20 | WASTE WATER TRANSFER SYSTEM | B0-LCP-3903 | SUMP LCP | HRSG #2 BLOWDOWN TANK AREA SUMP PUMP_LCP | L1, L2, L3, PE | B0-M-39003B | UNIT #2 HRSG BLOWDOWN TANK AREA SUMP PUMP #2_MOTOR (FROM LCP, CABLE ONLY) | 1.1_MAIN BUILDING COMPLEX / HRSG BLOWDOWN PIT | L1, L2, L3, PE | B161-016CC0037 → END
B0-LCP-3903 | -P20 | 04 |  | PE-L1-3C4-25 | PE-L1-3C4-25 | SUM-C-099-1 |  |  | 1 | 871 | B0-LCP-3903-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-25 | 0.03 | 230 | N | 20 | WASTE WATER TRANSFER SYSTEM | B0-LCP-3903 | SUMP LCP | HRSG #2 BLOWDOWN TANK AREA SUMP PUMP_LCP | L1, N, PE | B0-M-39003B | UNIT #2 HRSG BLOWDOWN AREA CHEMICAL SUMP PUMP #2_MOTOR S/H (FROM LCP, CABLE ONLY) | 1.1_MAIN BUILDING COMPLEX / HRSG BLOWDOWN PIT | L1, N, PE | B161-017CC0008 → END
B2-MCC-64602 | -P20 | 34 |  | PE-L1-5C25/16-04 | PE-L1-5C25/16-04 | SUM-C-100 |  |  | 1 | 872 | B2-MCC-64602-P2034 | 0.6/1kV CU/XLPE/LSZH | 4C x 25sqmm + 1C X 16sqmm | PE-L1-5C25/16-04 | 15.5 | 400 | N | 340 | WASTE WATER TRANSFER SYSTEM | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, N, PE | B0-LCP-3905 | HRSG #3 BLOWDOWN TANK AREA SUMP PUMP_LCP | 1.1_MAIN BUILDING COMPLEX / HRSG BLOWDOWN PIT | L1, L2, L3, N, PE | B264-016AT0045 → B264-016AT0046 → B264-016AT0209 → B264-016AT0026 → B264-016AT0027 → B264-016AT0225 → B264-996AT0011 → M0405 → D0421-L31 → M0406 → D0301-L37 → M0301 → B215-996BT0001 → B215-016BT0002 → B215-016BT0003 → B215-016BT0004 → B215-016BT0005 → B215-016BT0031 → B215-016BT0032 → B215-016BT0033 → B261-016CC0025 → B261-006CC0006 → B261-016CC0019 → B261-016CC0024 → END
B0-LCP-3905 | -P20 | 01 |  | PE-L1-4C4-26 | PE-L1-4C4-26 | SUM-C-101 |  |  | 1 | 873 | B0-LCP-3905-P2001 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-26 | 7.5 | 400 | N | 20 | WASTE WATER TRANSFER SYSTEM | B0-LCP-3905 | SUMP LCP | HRSG #3 BLOWDOWN TANK AREA SUMP PUMP_LCP | L1, L2, L3, PE | B0-M-39005A | UNIT #3 HRSG BLOWDOWN TANK AREA SUMP PUMP #1_MOTOR (FROM LCP, CABLE ONLY) | 1.1_MAIN BUILDING COMPLEX / HRSG BLOWDOWN PIT | L1, L2, L3, PE | B261-016AC0031 → END
B0-LCP-3905 | -P20 | 02 |  | PE-L1-3C4-25 | PE-L1-3C4-25 | SUM-C-101-1 |  |  | 1 | 874 | B0-LCP-3905-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-25 | 0.03 | 230 | N | 20 | WASTE WATER TRANSFER SYSTEM | B0-LCP-3905 | SUMP LCP | HRSG #3 BLOWDOWN TANK AREA SUMP PUMP_LCP | L1, N, PE | B0-M-39005A | UNIT #21 HRSG BLOWDOWN AREA CHEMICAL SUMP PUMP #1_MOTOR S/H (FROM LCP, CABLE ONLY) | 1.1_MAIN BUILDING COMPLEX / HRSG BLOWDOWN PIT | L1, N, PE | B261-017AC0007 → END
B0-LCP-3905 | -P20 | 03 |  | PE-L1-4C4-26 | PE-L1-4C4-26 | SUM-C-102 |  |  | 1 | 875 | B0-LCP-3905-P2003 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-26 | 7.5 | 400 | N | 20 | WASTE WATER TRANSFER SYSTEM | B0-LCP-3905 | SUMP LCP | HRSG #3 BLOWDOWN TANK AREA SUMP PUMP_LCP | L1, L2, L3, PE | B0-M-39005B | UNIT #3 HRSG BLOWDOWN TANK AREA SUMP PUMP #2_MOTOR (FROM LCP, CABLE ONLY) | 1.1_MAIN BUILDING COMPLEX / HRSG BLOWDOWN PIT | L1, L2, L3, PE | B261-016AC0032 → END
B0-LCP-3905 | -P20 | 04 |  | PE-L1-3C4-25 | PE-L1-3C4-25 | SUM-C-102-1 |  |  | 1 | 876 | B0-LCP-3905-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-25 | 0.03 | 230 | N | 20 | WASTE WATER TRANSFER SYSTEM | B0-LCP-3905 | SUMP LCP | HRSG #3 BLOWDOWN TANK AREA SUMP PUMP_LCP | L1, N, PE | B0-M-39005B | UNIT #21 HRSG BLOWDOWN AREA CHEMICAL SUMP PUMP #2_MOTOR S/H (FROM LCP, CABLE ONLY) | 1.1_MAIN BUILDING COMPLEX / HRSG BLOWDOWN PIT | L1, N, PE | B261-017AC0008 → END
B2-MCC-64603 | -P20 | 13 |  | PE-L1-5C16-01 | PE-L1-5C16-01 | SUM-C-103 |  |  | 1 | 877 | B2-MCC-64603-P2013 | 0.6/1kV CU/XLPE/LSZH | 5C x 16sqmm | PE-L1-5C16-01 | 15.5 | 400 | N | 270 | WASTE WATER TRANSFER SYSTEM | B2-MCC-64603 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, N, PE | B0-LCP-3907 | HRSG #4 BLOWDOWN TANK AREA SUMP PUMP_LCP | 1.1_MAIN BUILDING COMPLEX / HRSG BLOWDOWN PIT | L1, L2, L3, N, PE | B264-016CT0028 → B264-016CT0221 → B264-996CT0009 → M0405 → D0421-L32 → M0406 → D0301-L36 → M0301 → B215-996AT0026 → B215-016AT0048 → B215-016AT0049 → B215-016AT0050 → B215-016AT0051 → B215-016AT0064 → B215-016AT0065 → B261-016AC0022 → B261-006AC0006 → B261-016AC0018 → B261-016AC0011 → END
B0-LCP-3907 | -P20 | 01 |  | PE-L1-4C4-26 | PE-L1-4C4-26 | SUM-C-104 |  |  | 1 | 878 | B0-LCP-3907-P2001 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-26 | 7.5 | 400 | N | 20 | WASTE WATER TRANSFER SYSTEM | B0-LCP-3907 | SUMP LCP | HRSG #4 BLOWDOWN TANK AREA SUMP PUMP_LCP | L1, L2, L3, PE | B0-M-39007A | UNIT #4 HRSG BLOWDOWN TANK AREA SUMP PUMP #1_MOTOR (FROM LCP, CABLE ONLY) | 1.1_MAIN BUILDING COMPLEX / HRSG BLOWDOWN PIT | L1, L2, L3, PE | B261-016CC0032 → END
B0-LCP-3907 | -P20 | 02 |  | PE-L1-3C4-25 | PE-L1-3C4-25 | SUM-C-104-1 |  |  | 1 | 879 | B0-LCP-3907-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-25 | 0.03 | 230 | N | 20 | WASTE WATER TRANSFER SYSTEM | B0-LCP-3907 | SUMP LCP | HRSG #4 BLOWDOWN TANK AREA SUMP PUMP_LCP | L1, N, PE | B0-M-39007A | UNIT #22 HRSG BLOWDOWN AREA CHEMICAL SUMP PUMP #1_MOTOR S/H (FROM LCP, CABLE ONLY) | 1.1_MAIN BUILDING COMPLEX / HRSG BLOWDOWN PIT | L1, N, PE | B261-017CC0007 → END
B0-LCP-3907 | -P20 | 03 |  | PE-L1-4C4-26 | PE-L1-4C4-26 | SUM-C-105 |  |  | 1 | 880 | B0-LCP-3907-P2003 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-26 | 7.5 | 400 | N | 20 | WASTE WATER TRANSFER SYSTEM | B0-LCP-3907 | SUMP LCP | HRSG #4 BLOWDOWN TANK AREA SUMP PUMP_LCP | L1, L2, L3, PE | B0-M-39007B | UNIT #4 HRSG BLOWDOWN TANK AREA SUMP PUMP #2_MOTOR (FROM LCP, CABLE ONLY) | 1.1_MAIN BUILDING COMPLEX / HRSG BLOWDOWN PIT | L1, L2, L3, PE | B261-016CC0033 → END
B0-LCP-3907 | -P20 | 04 |  | PE-L1-3C4-25 | PE-L1-3C4-25 | SUM-C-105-1 |  |  | 1 | 881 | B0-LCP-3907-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-25 | 0.03 | 230 | N | 20 | WASTE WATER TRANSFER SYSTEM | B0-LCP-3907 | SUMP LCP | HRSG #4 BLOWDOWN TANK AREA SUMP PUMP_LCP | L1, N, PE | B0-M-39007B | UNIT #22 HRSG BLOWDOWN AREA CHEMICAL SUMP PUMP #2_MOTOR S/H (FROM LCP, CABLE ONLY) | 1.1_MAIN BUILDING COMPLEX / HRSG BLOWDOWN PIT | L1, N, PE | B261-017CC0008 → END
B1-MCC-59601 | -P20 | 21 |  | PE-L1-5C10-01 | PE-L1-5C10-01 | SUM-C-106 |  |  | 1 | 882 | B1-MCC-59601-P2021 | 0.6/1kV CU/XLPE/LSZH | 5C x 10sqmm | PE-L1-5C10-01 | 15.5 | 400 | N | 120 | WASTE WATER TRANSFER SYSTEM | B1-MCC-59601 | 400V MCC FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, N, PE | B0-LCP-3909 | BLOCK #1 TURBINE AREA SUMP_LOCAL CONTROL PANEL | 1.1_MAIN BUILDING COMPLEX / FLASH TANK PIT | L1, L2, L3, N, PE | B159-006AT0003 → B159-006AT0025 → D0326-L21 → M0316 → B113-996AT0012 → B113-016AT0011 → B113-016AT0004 → B113-016AT0003 → B113-016AT0005 → B113-016AT0006 → B113-016AT0007 → B113-006AC0004 → B113-016AC0013 → B113-016AC0010 → END
B0-LCP-3909 | -P20 | 01 |  | PE-L1-4C4-26 | PE-L1-4C4-26 | SUM-C-107 |  |  | 1 | 883 | B0-LCP-3909-P2001 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-26 | 7.5 | 400 | N | 20 | WASTE WATER TRANSFER SYSTEM | B0-LCP-3909 | SUMP LCP | BLOCK #1 TURBINE AREA SUMP_LOCAL CONTROL PANEL | L1, L2, L3, PE | B0-M-39009A | BLOCK #1 TURBINE AREA SUMP PUMP #1_MOTOR (FROM LCP, CABLE ONLY) | 1.1_MAIN BUILDING COMPLEX / FLASH TANK PIT | L1, L2, L3, PE | B113-016AC0015 → END
B0-LCP-3909 | -P20 | 02 |  | PE-L1-3C4-26 | PE-L1-3C4-26 | SUM-C-107-1 |  |  | 1 | 884 | B0-LCP-3909-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-26 | 0.03 | 230 | N | 20 | WASTE WATER TRANSFER SYSTEM | B0-LCP-3909 | SUMP LCP | BLOCK #1 TURBINE AREA SUMP_LOCAL CONTROL PANEL | L1, N, PE | B0-M-39009A | BLOCK #1 FLASH TANK AREA CHEMICAL SUMP PUMP #1_MOTOR S/H (FROM LCP, CABLE ONLY) | 1.1_MAIN BUILDING COMPLEX / FLASH TANK PIT | L1, N, PE | B113-017AC0001 → END
B0-LCP-3909 | -P20 | 03 |  | PE-L1-4C4-26 | PE-L1-4C4-26 | SUM-C-108 |  |  | 1 | 885 | B0-LCP-3909-P2003 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-26 | 7.5 | 400 | N | 20 | WASTE WATER TRANSFER SYSTEM | B0-LCP-3909 | SUMP LCP | BLOCK #1 TURBINE AREA SUMP_LOCAL CONTROL PANEL | L1, L2, L3, PE | B0-M-39009B | BLOCK #1 TURBINE AREA SUMP PUMPP #2_MOTOR (FROM LCP, CABLE ONLY) | 1.1_MAIN BUILDING COMPLEX / FLASH TANK PIT | L1, L2, L3, PE | B113-016AC0016 → END
B0-LCP-3909 | -P20 | 04 |  | PE-L1-3C4-27 | PE-L1-3C4-29 | SUM-C-108-1 |  |  | 1 | 886 | B0-LCP-3909-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-29 | 0.03 | 230 | N | 20 | WASTE WATER TRANSFER SYSTEM | B0-LCP-3909 | SUMP LCP | BLOCK #1 TURBINE AREA SUMP_LOCAL CONTROL PANEL | L1, N, PE | B0-M-39009B | BLOCK #1 FLASH TANK AREA CHEMICAL SUMP PUMP #2_MOTOR S/H (FROM LCP, CABLE ONLY) | 1.1_MAIN BUILDING COMPLEX / FLASH TANK PIT | L1, N, PE | B113-017AC0002 → END
B2-MCC-59602 | -P20 | 20 |  | PE-L1-5C10-02 | PE-L1-5C10-02 | SUM-C-112 |  |  | 1 | 887 | B2-MCC-59602-P2020 | 0.6/1kV CU/XLPE/LSZH | 5C x 10sqmm | PE-L1-5C10-02 | 15.5 | 400 | N | 120 | WASTE WATER TRANSFER SYSTEM | B2-MCC-59602 | 400V MCC FOR ST #2 FOR BLOCK #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, L2, L3, N, PE | B0-LCP-3913 | BLOCK #2 TURBINE AREA SUMP_LOCAL CONTROL PANEL | 1.1_MAIN BUILDING COMPLEX / FLASH TANK PIT | L1, L2, L3, N, PE | B259-006AT0006 → B259-006AT0005 → B259-006AT0014 → B259-006AT0025 → D0325-L21 → M0313 → B213-996AT0012 → B213-016AT0011 → B213-016AT0004 → B213-016AT0003 → B213-016AT0005 → B213-016AT0006 → B213-016AT0007 → B213-006AC0004 → B213-016AC0013 → B213-016AC0010 → END
B0-LCP-3913 | -P20 | 01 |  | PE-L1-4C4-26 | PE-L1-4C4-26 | SUM-C-113 |  |  | 1 | 888 | B0-LCP-3913-P2001 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-26 | 7.5 | 400 | N | 20 | WASTE WATER TRANSFER SYSTEM | B0-LCP-3913 | SUMP LCP | BLOCK #2 TURBINE AREA SUMP_LOCAL CONTROL PANEL | L1, L2, L3, PE | B0-M-39013A | BLOCK #2 TURBINE AREA SUMP PUMP #1_MOTOR (FROM LCP, CABLE ONLY) | 1.1_MAIN BUILDING COMPLEX / FLASH TANK PIT | L1, L2, L3, PE | B213-016AC0015 → END
B0-LCP-3913 | -P20 | 02 |  | PE-L1-3C4-27 | PE-L1-3C4-29 | SUM-C-113-1 |  |  | 1 | 889 | B0-LCP-3913-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-29 | 0.03 | 230 | N | 20 | WASTE WATER TRANSFER SYSTEM | B0-LCP-3913 | SUMP LCP | BLOCK #2 TURBINE AREA SUMP_LOCAL CONTROL PANEL | L1, N, PE | B0-M-39013A | BLOCK #2 FLASH TANK AREA CHEMICAL SUMP PUMP #1_MOTOR S/H (FROM LCP, CABLE ONLY) | 1.1_MAIN BUILDING COMPLEX / FLASH TANK PIT | L1, N, PE | B213-017AC0001 → END
B0-LCP-3913 | -P20 | 03 |  | PE-L1-4C4-26 | PE-L1-4C4-26 | SUM-C-114 |  |  | 1 | 890 | B0-LCP-3913-P2003 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-26 | 7.5 | 400 | N | 20 | WASTE WATER TRANSFER SYSTEM | B0-LCP-3913 | SUMP LCP | BLOCK #2 TURBINE AREA SUMP_LOCAL CONTROL PANEL | L1, L2, L3, PE | B0-M-39013B | BLOCK #2 TURBINE AREA SUMP PUMPP #2_MOTOR (FROM LCP, CABLE ONLY) | 1.1_MAIN BUILDING COMPLEX / FLASH TANK PIT | L1, L2, L3, PE | B213-016AC0016 → END
B0-LCP-3913 | -P20 | 04 |  | PE-L1-3C4-27 | PE-L1-3C4-29 | SUM-C-114-1 |  |  | 1 | 891 | B0-LCP-3913-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-29 | 0.03 | 230 | N | 20 | WASTE WATER TRANSFER SYSTEM | B0-LCP-3913 | SUMP LCP | BLOCK #2 TURBINE AREA SUMP_LOCAL CONTROL PANEL | L1, N, PE | B0-M-39013B | BLOCK #2 FLASH TANK AREA CHEMICAL SUMP PUMP #2_MOTOR S/H (FROM LCP, CABLE ONLY) | 1.1_MAIN BUILDING COMPLEX / FLASH TANK PIT | L1, N, PE | B213-017AC0002 → END
B1-MCC-64602 | -P20 | 38 |  | PE-L1-5C25/16-01 | PE-L1-5C25/16-01 | CDS-C-001 |  |  | 1 | 892 | B1-MCC-64602-P2038 | 0.6/1kV CU/XLPE/LSZH | 4C x 25sqmm + 1C X 16sqmm | PE-L1-5C25/16-01 | 22 | 400 | N | 290 | CHEMICAL DOSING SYSTEM | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B1-LCP-4201 | CHEMICAL DOSING SYSTEM FOR BLOCK#1 | 1.1_MAIN BUILDING COMPLEX (CHEMICAL DOSING SKID) | L1, L2, L3, N, PE | B164-016AT0115 → B164-996AT0023 → M0504 → D0531-L24 → M0510 → D0517-L14 → M0501 → D0503-L35 → M0502 → D0504-L35 → M0503 → D0501-L35 → M0328 → D0324-L35 → M0329 → B114-996CT0071 → B114-016CT0072 → B114-016CT0073 → B114-016CT0074 → B114-016CT0075 → B161-016CC0020 → B161-006CC0014 → END
B2-MCC-64602 | -P20 | 35 |  | PE-L1-5C25/16-03 | PE-L1-5C25/16-03 | CDS-C-002 |  |  | 1 | 893 | B2-MCC-64602-P2035 | 0.6/1kV CU/XLPE/LSZH | 4C x 25sqmm + 1C X 16sqmm | PE-L1-5C25/16-03 | 22 | 400 | N | 330 | CHEMICAL DOSING SYSTEM | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, N, PE | B2-LCP-4202 | CHEMICAL DOSING SYSTEM FOR BLOCK#2 | 1.1_MAIN BUILDING COMPLEX (CHEMICAL DOSING SKID) | L1, L2, L3, N, PE | B264-016AT0045 → B264-016AT0046 → B264-016AT0209 → B264-016AT0026 → B264-016AT0027 → B264-016AT0225 → B264-996AT0011 → M0405 → D0421-L31 → M0406 → D0301-L37 → M0301 → B215-996BT0001 → B215-016BT0002 → B215-016BT0003 → B215-016BT0004 → B215-016BT0005 → B215-016BT0031 → B215-016BT0032 → B215-016BT0033 → B261-016AC0016 → B261-006AC0012 → END
B1-MCC-64601 | -P20 | 28 | From변경 | PE-L1-5C16-02 | PE-L1-5C16-02 | SWA-B1-001 | B1-MCC-64601-P2028 |  | 1 | 894 | B1-MCC-64602-P2044 | 0.6/1kV CU/XLPE/LSZH | 5C x 16sqmm | PE-L1-5C16-02 | 18 | 400 | N | 270 | STEAM AND WATER ANALYSIS SYSTEM | B1-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B1-LCP-4101 | STEAM AND WATER ANALYSIS SYSTEM FOR BLOCK#1 | 23.1_EMERGENCY LUBE OIL PIT FOR GT BLOCK#1 (SWAS CONTAINER) | L1, L2, L3, N, PE | B164-016ET0106 → B164-996ET0022 → M0504 → D0531-L26 → M0510 → D0517-L16 → M0501 → D0503-L37 → M0502 → D0504-L37 → M0503 → D0501-L37 → M0328 → D0324-L37 → M0329 → B114-996CT0071 → B114-016CT0072 → B114-016CT0073 → B114-016CT0074 → B114-016CT0075 → B161-016CC0013 → B161-006CC0012 → END
B1-UPSP-64701 | -P20 | 04 |  | PE-L1-3C16-02 | PE-L1-3C16-02 | SWA-B1-002 |  |  | 1 | 895 | B1-UPSP-64701-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 16sqmm | PE-L1-3C16-02 | 2 | 230 | U | 260 | STEAM AND WATER ANALYSIS SYSTEM | B1-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-LCP-4101 | STEAM AND WATER ANALYSIS SYSTEM FOR BLOCK#1 | 23.1_EMERGENCY LUBE OIL PIT FOR GT BLOCK#1 (SWAS CONTAINER) | L1, N, PE | B164-006GT0201 → B164-006GT0001 → B164-006GT0002 → B164-006GT0003 → B064-006AC0007 → M0501 → D0503-L38 → M0502 → D0504-L38 → M0503 → D0501-L38 → M0328 → D0324-L38 → M0329 → B114-996BT0046 → B114-016BT0045 → B114-016BT0044 → B114-016BT0043 → B114-016BT0042 → B114-016BT0041 → B161-016CC0014 → B161-006CC0013 → END
B0-UPSP-64701 | -P20 | 03 |  | PE-L1-3C16-02 | PE-L1-3C16-02 | SWA-B1-003 |  |  | 1 | 896 | B0-UPSP-64701-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 16sqmm | PE-L1-3C16-02 | 1.5 | 230 | U | 380 | HOT WATER SYSTEM | B0-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-A-4101 | GLYCOL ANALYZER CABINET (B #1) | 32_HOT WATER SUPPLY BUILDING | L1, N, PE | B064-006FT0205 → B064-006FT0003 → B064-006AC0008 → M0501 → B064-996AT0120 → B064-016AT0033 → B064-016AT0034 → B064-016AT0233 → B064-016AT0234 → B064-016AT0048 → B064-016AT0049 → B064-016AT0240 → B064-016AT0290 → B064-016AT0068 → B064-016AT0067 → B064-016AT0277 → B064-016AT0278 → B064-016AT0094 → B064-016AT0296 → B064-016AT0110 → B064-016AT0109 → B064-016AT0285 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0055 → B025-996DT0019 → B025-016DT0056 → B025-016DT0057 → B025-016DT0135 → B078-016AC0011 → B078-006AC0044 → B078-007AC0007 → END
B2-MCC-64602 | -P20 | 36 |  | PE-L1-5C25/16-03 | PE-L1-5C25/16-03 | SWA-B2-001 |  |  | 1 | 897 | B2-MCC-64602-P2036 | 0.6/1kV CU/XLPE/LSZH | 4C x 25sqmm + 1C X 16sqmm | PE-L1-5C25/16-03 | 18 | 400 | N | 330 | B2-MCC-64602 | B2-MCC-64602 | 400V MCC FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, N, PE | B2-LCP-4101 | STEAM AND WATER ANALYSIS SYSTEM FOR BLOCK#2 | 23.1_EMERGENCY LUBE OIL PIT FOR GT BLOCK#2 (SWAS CONTAINER) | L1, L2, L3, N, PE | B264-016AT0045 → B264-016AT0046 → B264-016AT0209 → B264-016AT0026 → B264-016AT0027 → B264-016AT0225 → B264-996AT0011 → M0405 → D0421-L33 → M0406 → D0301-L35 → M0301 → B215-996BT0001 → B215-016BT0002 → B215-016BT0003 → B215-016BT0004 → B215-016BT0005 → B215-016BT0031 → B215-016BT0032 → B215-016BT0033 → B215-016BT0034 → B261-016CC0022 → B261-006CC0012 → END
B2-UPSP-64701 | -P20 | 04 |  | PE-L1-3C16-02 | PE-L1-3C16-02 | SWA-B2-002 |  |  | 1 | 898 | B2-UPSP-64701-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 16sqmm | PE-L1-3C16-02 | 2 | 230 | U | 330 | STEAM AND WATER ANALYSIS SYSTEM | B2-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-LCP-4101 | STEAM AND WATER ANALYSIS SYSTEM FOR BLOCK#2 | 23.1_EMERGENCY LUBE OIL PIT FOR GT BLOCK#2 (SWAS CONTAINER) | L1, N, PE | B264-016FT0061 → B264-016FT0060 → B264-006AC0001 → M0405 → D0421-L33 → M0406 → D0301-L35 → M0301 → B215-996BT0001 → B215-016BT0002 → B215-016BT0003 → B215-016BT0004 → B215-016BT0005 → B215-016BT0031 → B215-016BT0032 → B215-016BT0033 → B215-016BT0034 → B261-016CC0023 → B261-006CC0013 → END
B0-MCC-49602 | -P20 | 31 |  | PE-L1-5C25/16-03 | PE-L1-5C25/16-03 | SWA-B2-002-001 |  |  | 1 | 899 | B0-MCC-49602-P2031 | 0.6/1kV CU/XLPE/LSZH | 4C x 25sqmm + 1C X 16sqmm | PE-L1-5C25/16-03 | 35 | 400 | N | 170 | POTABLE WATER SYSTEM | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, N, PE | B0-E-37001 | POTABLE WATER CHILLER UNIT | 13.4_WATER SUPPLY PUMPING STATION | L1, L2, L3, N, PE | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L14 → M0207 → D0206-L11 → M0208 → D0207-L11 → M0210 → D0209-L11 → M0209 → B038-006BC0001 → END
B0-UPSP-64702 | -P20 | 04 |  | PE-L1-3C16-03 | PE-L1-3C16-03 | SWA-B2-003 |  |  | 1 | 900 | B0-UPSP-64702-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 16sqmm | PE-L1-3C16-03 | 1.5 | 230 | U | 360 | HOT WATER SYSTEM | B0-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B2-A-4101 | GLYCOL ANALYZER CABINET (B #2) | 32_HOT WATER SUPPLY BUILDING | L1, N, PE | B164-006HT0206 → B164-006HT0009 → B164-006HT0010 → B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0008 → M0501 → B064-996BT0019 → B064-016BT0013 → B064-016BT0014 → B064-016BT0015 → B064-016BT0016 → B064-016BT0309 → B064-016BT0037 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B025-016CT0090 → B025-016CT0089 → B025-016CT0067 → B025-016CT0066 → B025-016CT0065 → B025-016CT0064 → B025-016CT0063 → B025-016CT0062 → B025-016CT0061 → B025-016CT0060 → B025-996CT0020 → B025-016CT0059 → B025-016CT0055 → B025-996CT0019 → B025-016CT0056 → B025-016CT0133 → B078-016AC0010 → B078-006AC0045 → B078-007AC0008 → END
B0-MCC-72601 | -P20 | 04 |  | PE-L1-5C6-02 | PE-L1-5C6-02 | MWE-C-001 |  |  | 1 | 901 | B0-MCC-72601-P2004 | 0.6/1kV CU/XLPE/LSZH | 5C x 6sqmm | PE-L1-5C6-02 | 11.2 | 400 | N | 80 | WORKSHOP EQUIPMENT | B0-MCC-72601 | 400V MCC FOR WORKSHOP - A | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, L2, L3, N, PE | MWE-C-001 | MILLING MACHINE (C1) | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, L2, L3, N, PE | B071-006AT0001 → B071-006BT0002 → B071-016AC0005 → B071-006AC0007 → END
B0-MCC-72602 | -P20 | 05 |  | PE-L1-5C4-01 | PE-L1-5C4-01 | MWE-C-002 |  |  | 1 | 902 | B0-MCC-72602-P2005 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-01 | 5 | 400 | N | 80 | WORKSHOP EQUIPMENT | B0-MCC-72602 | 400V MCC FOR WORKSHOP - B | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, L2, L3, N, PE | MWE-C-002 | LATHE MACHINE (C2) | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, L2, L3, N, PE | B071-006AT0001 → B071-006BT0002 → B071-016AC0005 → B071-006AC0006 → END
B0-MCC-72602 | -P20 | 06 |  | PE-L1-5C4-01 | PE-L1-5C4-01 | MWE-C-003 |  |  | 1 | 903 | B0-MCC-72602-P2006 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-01 | 1.5 | 400 | N | 110 | WORKSHOP EQUIPMENT | B0-MCC-72602 | 400V MCC FOR WORKSHOP - B | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, L2, L3, N, PE | MWE-C-003 | HACKSAW (3) | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, L2, L3, N, PE | B071-006AT0001 → B071-006BT0002 → B071-016AC0005 → B071-016AC0003 → B071-006AC0008 → END
B0-MCC-72601 | -P20 | 05 | 재배정 | PE-L1-5C4-01 | PE-L1-5C4-02 | MWE-C-004 |  |  | 1 | 904 | B0-MCC-72601-P2005 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-02 | 2 | 400 | N | 80 | WORKSHOP EQUIPMENT | B0-MCC-72601 | 400V MCC FOR WORKSHOP - A | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, L2, L3, N, PE | MWE-C-004 | POWER SOCKET FOR GRINDING MACHINE (P1) | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, L2, L3, N, PE | B071-006AT0001 → B071-006BT0002 → B071-016AC0005 → B071-006AC0005 → END
B0-DB-72601 | -P20 | 01 |  | PE-L1-3C4-21 | PE-L1-3C4-21 | MWE-C-005 |  |  | 1 | 905 | B0-DB-72601-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-21 | 1 | 230 | N | 80 | WORKSHOP EQUIPMENT | B0-DB-72601 | 400V-230V DIST. BOARD FOR WORKSHOP - A | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, N, PE | MWE-C-005 | POWER SOCKET FOR DRILLING MACHINE (P2) | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, N, PE | B071-006AT0001 → B071-006BT0002 → B071-016AC0005 → B071-007AC0003 → END
B0-MCC-72602 | -P20 | 07 |  | PE-L1-5C6-02 | PE-L1-5C6-02 | MWE-C-006 |  |  | 1 | 906 | B0-MCC-72602-P2007 | 0.6/1kV CU/XLPE/LSZH | 5C x 6sqmm | PE-L1-5C6-02 | 11 | 400 | N | 140 | WORKSHOP EQUIPMENT | B0-MCC-72602 | 400V MCC FOR WORKSHOP - B | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, L2, L3, N, PE | MWE-C-006 | POWER SOCKET FOR ARGON ARC WELDING MACHINE (P3) | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, L2, L3, N, PE | B071-006AT0001 → B071-006BT0002 → B071-016AC0005 → B071-016AC0002 → B071-016AC0001 → B071-006AC0009 → END
B0-MCC-72601 | -P20 | 06 |  | PE-L1-5C6-02 | PE-L1-5C6-02 | MWE-C-007 |  |  | 1 | 907 | B0-MCC-72601-P2006 | 0.6/1kV CU/XLPE/LSZH | 5C x 6sqmm | PE-L1-5C6-02 | 12 | 400 | N | 120 | WORKSHOP EQUIPMENT | B0-MCC-72601 | 400V MCC FOR WORKSHOP - A | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, L2, L3, N, PE | MWE-C-007 | POWER SOCKET FOR ELECTRICAL WELDING MACHINE (P4) | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, L2, L3, N, PE | B071-006AT0001 → B071-006BT0002 → B071-016AC0005 → B071-016AC0002 → B071-016AC0001 → B071-006AC0010 → END
B0-DB-72601 | -P20 | 02 |  | PE-L1-3C4-21 | PE-L1-3C4-21 | MWE-C-008 |  |  | 1 | 908 | B0-DB-72601-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-21 | 1 | 230 | N | 140 | WORKSHOP EQUIPMENT | B0-DB-72601 | 400V-230V DIST. BOARD FOR WORKSHOP - A | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, N, PE | MWE-C-008 | POWER SOCKET FOR DRYING OVEN (P5) | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, N, PE | B071-006AT0001 → B071-006BT0002 → B071-016AC0005 → B071-016AC0002 → B071-016AC0001 → B071-007AC0009 → END
B0-DB-72602 | -P20 | 01 |  | PE-L1-3C6-05 | PE-L1-3C6-05 | MWE-C-009 |  |  | 1 | 909 | B0-DB-72602-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-05 | 2.2 | 230 | N | 110 | WORKSHOP EQUIPMENT | B0-DB-72602 | 400V-230V DIST. BOARD FOR WORKSHOP - B | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, N, PE | MWE-C-009 | POWER SOCKET FOR HYDROSTATIC TESTING MACHINE (P6) | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, N, PE | B071-006AT0001 → B071-006BT0002 → B071-016AC0004 → B071-016AC0003 → B071-007AC0004 → END
B0-DB-72601 | -P20 | 03 |  | PE-L1-3C6-05 | PE-L1-3C6-05 | MWE-C-010 |  |  | 1 | 910 | B0-DB-72601-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-05 | 2 | 230 | N | 110 | WORKSHOP EQUIPMENT | B0-DB-72601 | 400V-230V DIST. BOARD FOR WORKSHOP - A | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, N, PE | MWE-C-010 | POWER SOCKET FOR STEAM CLEANING MACHINE (P7) | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, N, PE | B071-006AT0001 → B071-006BT0002 → B071-016AC0004 → B071-016AC0003 → B071-007AC0005 → END
B0-DB-72602 | -P20 | 02 |  | PE-L1-3C6-05 | PE-L1-3C6-05 | MWE-C-011 |  |  | 1 | 911 | B0-DB-72602-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-05 | 2 | 230 | N | 110 | WORKSHOP EQUIPMENT | B0-DB-72602 | 400V-230V DIST. BOARD FOR WORKSHOP - B | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, N, PE | MWE-C-011 | POWER SOCKET FOR WATER JET MACHINE (P8) | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, N, PE | B071-006AT0001 → B071-006BT0002 → B071-016AC0004 → B071-016AC0003 → B071-007AC0006 → END
B0-DB-72601 | -P20 | 04 |  | PE-L1-3C4-21 | PE-L1-3C4-21 | MWE-C-012 |  |  | 1 | 912 | B0-DB-72601-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-21 | 1 | 230 | N | 110 | WORKSHOP EQUIPMENT | B0-DB-72601 | 400V-230V DIST. BOARD FOR WORKSHOP - A | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, N, PE | MWE-C-012 | POWER SOCKET FOR VACUUM CLEANER (P9) | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, N, PE | B071-006AT0001 → B071-006BT0002 → B071-016AC0004 → B071-016AC0003 → B071-007AC0007 → END
B0-DB-72602 | -P20 | 03 |  | PE-L1-3C4-21 | PE-L1-3C4-21 | MWE-C-013 |  |  | 1 | 913 | B0-DB-72602-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-21 | 1 | 230 | N | 110 | WORKSHOP EQUIPMENT | B0-DB-72602 | 400V-230V DIST. BOARD FOR WORKSHOP - B | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, N, PE | MWE-C-013 | POWER SOCKET FOR VACUUM CLEANER (P10) | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, N, PE | B071-006AT0001 → B071-006BT0002 → B071-016AC0004 → B071-016AC0002 → B071-007AC0008 → END
B0-DB-72601 | -P20 | 05 |  | PE-L1-3C6-05 | PE-L1-3C6-05 | MWE-C-014 |  |  | 1 | 914 | B0-DB-72601-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-05 | 2 | 230 | N | 140 | WORKSHOP EQUIPMENT | B0-DB-72601 | 400V-230V DIST. BOARD FOR WORKSHOP - A | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, N, PE | MWE-C-014 | POWER SOCKET FOR WELDING DUST COLLECTOR (P11) | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, N, PE | B071-006AT0001 → B071-006BT0002 → B071-016AC0005 → B071-016AC0002 → B071-016AC0001 → B071-007AC0010 → END
B0-DB-72602 | -P20 | 04 |  | PE-L1-3C16-01 | PE-L1-3C16-01 | MWE-C-015 |  |  | 1 | 915 | B0-DB-72602-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 16sqmm | PE-L1-3C16-01 | 5 | 230 | N | 90 | WORKSHOP EQUIPMENT | B0-DB-72602 | 400V-230V DIST. BOARD FOR WORKSHOP - B | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, N, PE | MWE-C-015 | POWER SOCKET FOR INSTRUMENT WORKBENCH (P12) | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, N, PE | B071-006AT0001 → B071-006BT0002 → B071-017AC0001 → B071-007AC0001 → END
B0-DB-72601 | -P20 | 06 |  | PE-L1-3C16-01 | PE-L1-3C16-01 | MWE-C-016 |  |  | 1 | 916 | B0-DB-72601-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 16sqmm | PE-L1-3C16-01 | 5 | 230 | N | 100 | WORKSHOP EQUIPMENT | B0-DB-72601 | 400V-230V DIST. BOARD FOR WORKSHOP - A | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, N, PE | MWE-C-016 | POWER SOCKET FOR PNEMATIC WORKBENCH (P13) | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, N, PE | B071-006AT0001 → B071-006BT0002 → B071-017AC0001 → B071-007AC0002 → END
B0-UPSP-64702 | -P20 | 05 |  | PE-L1-3C25/16-01 | PE-L1-3C25/16-01 | INC-0001 |  | DONE | 1 | 917 | B0-UPSP-64702-P2005 | 0.6/1kV CU/XLPE/LSZH | 2C x 25sqmm + 1C X 16sqmm | PE-L1-3C25/16-01 | 5.5 | 230 | U | 120 | DCS | B0-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-PDP-0003 | COMMON DCS (CER) PDP PRIMARY | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-006FT0206 → B064-006FT0009 → B064-006FT0208 → B064-006FT0207 → B064-006FT0005 → B064-006AC0014 → M0501 → B064-996GT0020 → B064-016GT0033 → B064-016GT0229 → B064-016GT0230 → B064-016GT0047 → B064-016GT0048 → B064-016GT0239 → B064-996GT0013 → B064-996GT0053 → B064-996GT0073 → B064-037AT0214 → B064-037AT0213 → B064-037AT0212 → B064-037AT0211 → B064-037AT0210 → B064-037AT0015 → B064-037AT0014 → END
B0-UPSP-64701 | -P20 | 04 |  | PE-L1-3C25/16-01 | PE-L1-3C25/16-01 | INC-0002 |  | DONE | 1 | 918 | B0-UPSP-64701-P2004 | 0.6/1kV CU/XLPE/LSZH | 2C x 25sqmm + 1C X 16sqmm | PE-L1-3C25/16-01 | 5.5 | 230 | U | 80 | DCS | B0-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-PDP-0003 | COMMON DCS (CER) PDP SECONDARY | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B164-006HT0205 → B164-006HT0004 → B164-006HT0005 → B064-006AC0015 → M0501 → B064-996AT0020 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0014 → END
B0-DB-64602 | -P20 | 01 |  | PE-L1-3C25/16-01 | PE-L1-3C25/16-01 | INC-0003 |  | DONE | 1 | 919 | B0-DB-64602-P2001 | 0.6/1kV CU/XLPE/LSZH | 2C x 25sqmm + 1C X 16sqmm | PE-L1-3C25/16-01 | 11 | 230 | N | 90 | DCS | B0-DB-64602 | 400V-230V DIST. BOARD FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-PDP-0003 | COMMON DCS (CER) NORMAL | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0032 → B064-016AT0033 → B064-016AT0034 → B064-016AT0232 → B064-016AT0013 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0014 → END
B0-UPSP-64701 | -P20 | 05 |  | PE-L1-3C50/25-02 | PE-L1-3C50/25-02 | INC-0004 |  |  | 1 | 920 | B0-UPSP-64701-P2005 | 0.6/1kV CU/XLPE/LSZH | 2C x 50sqmm + 1C X 25sqmm | PE-L1-3C50/25-02 | 3 | 230 | U | 580 | DCS | B0-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-D-0011 | WT/WWT DCS CONTROLLER CABINET PRIMARY | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, N, PE | B064-006FT0205 → B064-006FT0003 → B064-006AC0011 → M0501 → D0503-L37 → M0502 → D0504-L37 → M0503 → D0501-L37 → M0328 → D0324-L37 → M0329 → B114-997AT0021 → B114-017AT0020 → B114-017AT0025 → B025-017ET0042 → B025-017ET0041 → B025-017ET0040 → B025-017ET0016 → B025-017ET0039 → B025-017ET0038 → B025-017ET0036 → B025-017ET0035 → B025-017ET0033 → B025-017ET0032 → B025-017ET0031 → B025-017ET0030 → B025-017ET0021 → B025-017ET0022 → B025-997ET0004 → M0205 → D0205-L23 → M0206 → D0203-L23 → M0207 → D0204-L17 → B049-007AT0001 → B049-007AT0003 → B049-007AT0012 → B049-006AC0001 → END
B0-UPSP-64702 | -P20 | 06 |  | PE-L1-3C50/25-03 | PE-L1-3C50/25-03 | INC-0005 |  |  | 1 | 921 | B0-UPSP-64702-P2006 | 0.6/1kV CU/XLPE/LSZH | 2C x 50sqmm + 1C X 25sqmm | PE-L1-3C50/25-03 | 3 | 230 | U | 590 | DCS | B0-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-D-0011 | WT/WWT DCS CONTROLLER CABINET SECONDARY | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, N, PE | B164-006HT0206 → B164-006HT0205 → B164-006HT0004 → B164-006HT0005 → B064-006AC0011 → M0501 → D0503-L38 → M0502 → D0504-L38 → M0503 → D0501-L38 → M0328 → D0324-L38 → M0329 → B114-996AT0021 → B114-016AT0020 → B114-016AT0025 → B025-016FT0042 → B025-016FT0041 → B025-016FT0040 → B025-996FT0016 → B025-016FT0039 → B025-016FT0038 → B025-016FT0036 → B025-016FT0035 → B025-016FT0033 → B025-016FT0032 → B025-016FT0031 → B025-016FT0030 → B025-016FT0028 → B025-016FT0029 → B025-996FT0005 → M0205 → D0205-L23 → M0206 → D0203-L22 → M0207 → D0204-L17 → B049-006AT0002 → B049-006AT0003 → B049-006AT0012 → B049-996AT0013 → B049-996AT0017 → B049-016AT0018 → B049-016AT0019 → B049-016AT0020 → B049-016AT0027 → B049-016AT0028 → B049-016AT0029 → END
B0-DB-49601 | -P20 | 01 |  | PE-L1-3C4-13 | PE-L1-3C4-13 | INC-0006 |  |  | 1 | 922 | B0-DB-49601-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-13 | 2 | 230 | N | 60 | DCS | B0-DB-49601 | 400V-230V DIST. BOARD FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, N, PE | B0-D-0011 | WT/WWT DCS CONTROLLER CABINET NORMAL | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, N, PE | B049-006AT0004 → B049-006AT0012 → B049-996AT0013 → B049-996AT0017 → B049-016AT0018 → B049-016AT0019 → B049-016AT0020 → B049-016AT0027 → B049-016AT0028 → B049-016AT0029 → END
B1-UPSP-73701 | -P20 | 04 |  | PE-L1-3C16-01 | PE-L1-3C16-01 | INC-0010 |  |  | 1 | 923 | B1-UPSP-73701-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 16sqmm | PE-L1-3C16-01 | 10 | 230 | U | 20 | DCS | B1-UPSP-73701 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ADMIN. - BLOCK#1 - A | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B1-PDP-0001 | BLOCK #1 DCS (SERVER ROOM) PDP PRIMARY | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B073-017AT0013 → END
B1-UPSP-73702 | -P20 | 04 |  | PE-L1-3C16-01 | PE-L1-3C16-01 | INC-0011 |  |  | 1 | 924 | B1-UPSP-73702-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 16sqmm | PE-L1-3C16-01 | 10 | 230 | U | 20 | DCS | B1-UPSP-73702 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ADMIN. - BLOCK#1 - B | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B1-PDP-0001 | BLOCK #1 DCS (SERVER ROOM) PDP SECONDARY | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B073-016AT0013 → END
B2-UPSP-73701 | -P20 | 03 |  | PE-L1-3C16-01 | PE-L1-3C16-01 | INC-0013 |  |  | 1 | 925 | B2-UPSP-73701-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 16sqmm | PE-L1-3C16-01 | 10 | 230 | U | 20 | DCS | B2-UPSP-73701 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ADMIN. - BLOCK#2 - A | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B2-PDP-0001 | BLOCK #2 DCS (SERVER ROOM) PDP PRIMARY | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B073-017AT0013 → END
B2-UPSP-73702 | -P20 | 03 |  | PE-L1-3C16-01 | PE-L1-3C16-01 | INC-0014 |  |  | 1 | 926 | B2-UPSP-73702-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 16sqmm | PE-L1-3C16-01 | 10 | 230 | U | 20 | DCS | B2-UPSP-73702 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ADMIN. - BLOCK#2 - B | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B2-PDP-0001 | BLOCK #2 DCS (SERVER ROOM) PDP SECONDARY | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B073-016AT0013 → END
B1-UPSP-64702 | -P20 | 04 |  | PE-L1-3C25/16-01 | PE-L1-3C25/16-01 | INC-0016 |  | DONE | 1 | 927 | B1-UPSP-64702-P2004 | 0.6/1kV CU/XLPE/LSZH | 2C x 25sqmm + 1C X 16sqmm | PE-L1-3C25/16-01 | 6 | 230 | U | 140 | DCS | B1-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-PDP-0011 | BLOCK #1 DCS (LER) PDP PRIMARY | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B164-006GT0202 → B164-006GT0201 → B164-006GT0001 → B164-006GT0002 → B164-006GT0003 → B064-006AC0014 → M0501 → B064-996GT0020 → B064-016GT0033 → B064-016GT0229 → B064-016GT0230 → B064-016GT0047 → B064-016GT0048 → B064-016GT0239 → B064-016GT0239 → B064-996GT0013 → B064-996GT0053 → B064-996GT0073 → B064-037AT0214 → B064-037AT0213 → B064-037AT0212 → B064-037AT0211 → B064-037AT0210 → B064-037AT0016 → B064-037AT0017 → B064-037AT0018 → END
B1-UPSP-64701 | -P20 | 05 |  | PE-L1-3C25/16-01 | PE-L1-3C25/16-01 | INC-0017 |  | DONE | 1 | 928 | B1-UPSP-64701-P2005 | 0.6/1kV CU/XLPE/LSZH | 2C x 25sqmm + 1C X 16sqmm | PE-L1-3C25/16-01 | 6 | 230 | U | 110 | DCS | B1-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-PDP-0011 | BLOCK #1 DCS (LER) PDP SECONDARY | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B164-006HT0202 → B164-006HT0007 → B164-006HT0008 → B164-006HT0009 → B164-006HT0010 → B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0015 → M0501 → B064-996AT0020 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0014 → B064-036AT0015 → B064-036AT0016 → B064-036AT0017 → B064-036AT0018 → END
B1-DB-64604 | -P20 | 02 |  | PE-L1-3C25/16-01 | PE-L1-3C25/16-01 | INC-0018 |  | DONE | 1 | 929 | B1-DB-64604-P2002 | 0.6/1kV CU/XLPE/LSZH | 2C x 25sqmm + 1C X 16sqmm | PE-L1-3C25/16-01 | 6 | 230 | N | 160 | DCS | B1-DB-64604 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-PDP-0011 | BLOCK #1 DCS (LER) PDP NORMAL | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0111 → B064-016AT0296 → B064-016AT0094 → B064-016AT0278 → B064-016AT0277 → B064-016AT0067 → B064-016AT0068 → B064-016AT0290 → B064-016AT0240 → B064-016AT0049 → B064-016AT0048 → B064-016AT0234 → B064-016AT0233 → B064-016AT0232 → B064-016AT0013 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0014 → B064-036AT0015 → B064-036AT0016 → B064-036AT0017 → B064-036AT0018 → END
B2-UPSP-64702 | -P20 | 04 |  | PE-L1-3C25/16-01 | PE-L1-3C25/16-03 | INC-0019 |  |  | 1 | 930 | B2-UPSP-64702-P2004 | 0.6/1kV CU/XLPE/LSZH | 2C x 25sqmm + 1C X 16sqmm | PE-L1-3C25/16-03 | 8 | 230 | U | 90 | DCS | B2-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-PDP-0011 | BLOCK #2 DCS (LER) PDP PRIMARY | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016ET0061 → B264-016ET0248 → B264-016ET0062 → B264-006AC0006 → M0407 → B264-996BT0013 → B264-016BT0048 → B264-016BT0049 → B264-016BT0050 → B264-016BT0240 → B264-016BT0055 → B264-016BT0242 → END
B2-UPSP-64701 | -P20 | 05 |  | PE-L1-3C25/16-01 | PE-L1-3C25/16-03 | INC-0020 |  |  | 1 | 931 | B2-UPSP-64701-P2005 | 0.6/1kV CU/XLPE/LSZH | 2C x 25sqmm + 1C X 16sqmm | PE-L1-3C25/16-03 | 8 | 230 | U | 100 | DCS | B2-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-PDP-0011 | BLOCK #2 DCS (LER) PDP SECONDARY | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016DT0061 → B264-016DT0248 → B264-016ET0062 → B264-006AC0006 → M0407 → B264-996AT0013 → B264-016AT0048 → B264-016AT0049 → B264-016AT0050 → B264-016AT0240 → B264-016AT0055 → B264-016AT0056 → B264-016AT0243 → END
B2-DB-64604 | -P20 | 03 | From변경 | PE-L1-3C16-01 | PE-L1-3C16-01 | INC-0021 | B2-DB-64604-P2003 |  | 1 | 932 | B2-DB-64603-P2020 | 0.6/1kV CU/XLPE/LSZH | 3C x 16sqmm | PE-L1-3C16-01 | 8 | 230 | N | 40 | DCS | B2-DB-64603 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-PDP-0011 | BLOCK #2 DCS (LER) PDP NORMAL | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016AT0029 → B264-016AT0030 → B264-016AT0031 → B264-016AT0032 → B264-016AT0241 → END
B1-UPSP-59701 | -P20 | 03 |  | PE-L1-3C4-13 | PE-L1-3C4-13 | INC-0022 |  |  | 1 | 933 | B1-UPSP-59701-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-13 | 1 | 230 | U | 40 | DCS | B1-UPSP-59701 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR STG #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-D-0030 | STG #1 DCS CONTROLLER CABINET PRIMARY | 1.1_MAIN BUILDING COMPLEX (STG LER #1) | L1, N, PE | B159-007AT0003 → B159-007AT0004 → B159-007AT0020 → B159-007AT0009 → B159-007AT0021 → END
B1-UPSP-59702 | -P20 | 03 |  | PE-L1-3C4-13 | PE-L1-3C4-13 | INC-0023 |  |  | 1 | 934 | B1-UPSP-59702-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-13 | 1 | 230 | U | 50 | DCS | B1-UPSP-59702 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR STG #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-D-0030 | STG #1 DCS CONTROLLER CABINET SECONDARY | 1.1_MAIN BUILDING COMPLEX (STG LER #1) | L1, N, PE | B159-006BT0003 → B159-006BT0019 → B159-006BT0006 → B159-006BT0018 → B159-006BT0010 → END
B1-DB-59601 | -P20 | 11 |  | PE-L1-3C4-13 | PE-L1-3C4-13 | INC-0024 |  |  | 1 | 935 | B1-DB-59601-P2011 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-13 | 1 | 230 | N | 50 | DCS | B1-DB-59601 | 400V-230V DIST. BOARD FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-D-0030 | STG #1 DCS CONTROLLER CABINET NORMAL | 1.1_MAIN BUILDING COMPLEX (STG LER #1) | L1, N, PE | B159-006BT0003 → B159-006BT0019 → B159-006BT0006 → B159-006BT0018 → B159-006BT0010 → END
B2-UPSP-59701 | -P20 | 03 |  | PE-L1-3C4-14 | PE-L1-3C4-14 | INC-0025 |  |  | 1 | 936 | B2-UPSP-59701-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-14 | 1 | 230 | U | 50 | DCS | B2-UPSP-59701 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR STG #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B2-D-0030 | STG #2 DCS CONTROLLER CABINET PRIMARY | 1.1_MAIN BUILDING COMPLEX (STG LER #2) | L1, N, PE | B259-007AT0003 → B259-007AT0004 → B259-007AT0020 → B259-007AT0009 → B259-007AT0021 → B259-007AT0010 → END
B2-UPSP-59702 | -P20 | 02 |  | PE-L1-3C4-14 | PE-L1-3C4-14 | INC-0026 |  |  | 1 | 937 | B2-UPSP-59702-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-14 | 1 | 230 | U | 50 | DCS | B2-UPSP-59702 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR STG #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B2-D-0030 | STG #2 DCS CONTROLLER CABINET SECONDARY | 1.1_MAIN BUILDING COMPLEX (STG LER #2) | L1, N, PE | B259-006BT0003 → B259-006BT0019 → B259-006BT0006 → B259-006BT0018 → B259-006BT0010 → END
B2-DB-59601 | -P20 | 10 |  | PE-L1-3C4-14 | PE-L1-3C4-14 | INC-0027 |  |  | 1 | 938 | B2-DB-59601-P2010 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-14 | 1 | 230 | N | 50 | DCS | B2-DB-59601 | 400V-230V DIST. BOARD FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B2-D-0030 | STG #2 DCS CONTROLLER CABINET NORMAL | 1.1_MAIN BUILDING COMPLEX (STG LER #2) | L1, N, PE | B259-006BT0003 → B259-006BT0019 → B259-006BT0006 → B259-006BT0018 → B259-006BT0010 → END
B0-UPSP-69702 | -P20 | 01 |  | PE-L1-3C6-03 | PE-L1-3C6-03 | INC-0028 |  |  | 1 | 939 | B0-UPSP-69702-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-03 | 3 | 230 | U | 60 | DCS | B0-UPSP-69702 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ACC - B | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-D-0040 | ACC #1 DCS REMOTE IO CABINET PRIMARY | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-007AT0005 → B169-007AT0006 → B169-007AT0007 → B169-007AT0040 → B169-007AT0041 → END
B0-UPSP-69701 | -P20 | 01 |  | PE-L1-3C6-03 | PE-L1-3C6-03 | INC-0029 |  |  | 1 | 940 | B0-UPSP-69701-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-03 | 3 | 230 | U | 40 | DCS | B0-UPSP-69701 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ACC - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-D-0040 | ACC #1 DCS REMOTE IO CABINET SECONDARY | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0013 → B169-006AT0014 → B169-006AT0040 → END
B1-DB-69601 | -P20 | 15 |  | PE-L1-3C4-13 | PE-L1-3C4-13 | INC-0030 |  |  | 1 | 941 | B1-DB-69601-P2015 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-13 | 2 | 230 | N | 80 | DCS | B1-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-D-0040 | ACC #1 DCS REMOTE IO CABINET NORMAL | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0017 → B169-006AT0018 → B169-006AT0019 → B169-006AT0020 → B169-006AT0021 → B169-006AT0039 → B169-006AT0040 → END
B0-UPSP-69701 | -P20 | 02 |  | PE-L1-3C6-02 | PE-L1-3C6-02 | INC-0031 |  |  | 1 | 942 | B0-UPSP-69701-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-02 | 3 | 230 | U | 60 | DCS | B0-UPSP-69701 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ACC - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-D-0040 | ACC #2 DCS REMOTE IO CABINET PRIMARY | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-007AT0005 → B169-007AT0006 → B169-007AT0007 → B169-007AT0039 → B169-007AT0038 → B169-007AT0037 → END
B0-UPSP-69702 | -P20 | 02 |  | PE-L1-3C6-02 | PE-L1-3C6-02 | INC-0032 |  |  | 1 | 943 | B0-UPSP-69702-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-02 | 3 | 230 | U | 50 | DCS | B0-UPSP-69702 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ACC - B | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-D-0040 | ACC #2 DCS REMOTE IO CABINET SECONDARY | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0013 → B169-006AT0014 → B169-006AT0039 → B169-006AT0038 → END
B2-DB-69601 | -P20 | 15 | 재배정 | PE-L1-3C4-09 | PE-L1-3C4-15 | INC-0033 |  |  | 1 | 944 | B2-DB-69601-P2015 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 2 | 230 | N | 40 | DCS | B2-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-D-0040 | ACC #2 DCS REMOTE IO CABINET NORMAL | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0020 → B169-006AT0021 → B169-006AT0038 → END
B0-UPSP-64701 | -P20 | 06 |  | PE-L1-3C35/25-01 | PE-L1-3C35/25-01 | INC-0035 | DONE(10/27) | DONE | 1 | 945 | B0-UPSP-64701-P2006 | 0.6/1kV CU/XLPE/LSZH | 2C x 35sqmm + 1C X 25sqmm | PE-L1-3C35/25-01 | 3 | 230 | U | 450 | GAS METERING SYSTEM | B0-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-FM-4401 | GAS METERING PANEL (COMMON) PRIMARY | 18_AUXILIARY BOILER / LER | L1, N, PE | B064-006FT0205 → B064-006FT0003 → B064-006AC0005 → M0501 → B064-996BT0020 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B064-016BT0294 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0054 → B025-016DT0053 → B025-016DT0050 → B025-016DT0049 → B025-016DT0048 → B025-016DT0047 → B025-996DT0008 → M0521 → D0528-L11 → B078-006AT0001 → END
B0-UPSP-64702 | -P20 | 07 |  | PE-L1-3C35/25-01 | PE-L1-3C35/25-01 | INC-0036 | DONE(10/27) | DONE | 1 | 946 | B0-UPSP-64702-P2007 | 0.6/1kV CU/XLPE/LSZH | 2C x 35sqmm + 1C X 25sqmm | PE-L1-3C35/25-01 | 3 | 230 | U | 520 | GAS METERING SYSTEM | B0-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-FM-4401 | GAS METERING PANEL (COMMON) SEONDARY | 18_AUXILIARY BOILER / LER | L1, N, PE | B164-006HT0206 → B164-006HT0205 → B164-006HT0004 → B164-006HT0005 → B064-006AC0010 → M0501 → B064-996AT0120 → B064-016AT0033 → B064-016AT0034 → B064-016AT0233 → B064-016AT0234 → B064-016AT0048 → B064-016AT0049 → B064-016AT0050 → B064-016AT0051 → B064-016AT0312 → B064-016AT0071 → B064-016AT0070 → B064-016AT0069 → B064-016AT0068 → B064-016AT0067 → B064-016AT0277 → B064-016AT0278 → B064-016AT0094 → B064-016AT0296 → B064-016AT0110 → B064-016AT0109 → B064-016AT0285 → B025-016CT0090 → B025-016CT0089 → B025-016CT0067 → B025-016CT0066 → B025-016CT0065 → B025-016CT0064 → B025-016CT0063 → B025-016CT0062 → B025-016CT0061 → B025-016CT0060 → B025-996CT0020 → B025-016CT0059 → B025-016CT0054 → B025-016CT0053 → B025-016CT0050 → B025-016CT0049 → B025-016CT0048 → B025-016CT0047 → B025-996CT0008 → M0521 → D0528-L12 → B078-006BT0001 → END
B0-DB-64601 | -P20 | 01 |  | PE-L1-3C16-01 | PE-L1-3C16-01 | INC-0037 |  |  | 1 | 947 | B0-DB-64601-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 16sqmm | PE-L1-3C16-01 | 1 | 230 | N | 520 | GAS METERING SYSTEM | B0-DB-64601 | 400V-230V DIST. BOARD FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-FM-4401 | GAS METERING PANEL (COMMON) NORMAL | 18_AUXILIARY BOILER / LER | L1, N, PE | B064-016AT0012 → B064-016AT0013 → B064-016AT0232 → B064-016AT0233 → B064-016AT0234 → B064-016AT0048 → B064-016AT0049 → B064-016AT0050 → B064-016AT0051 → B064-016AT0312 → B064-016AT0071 → B064-016AT0070 → B064-016AT0069 → B064-016AT0068 → B064-016AT0067 → B064-016AT0277 → B064-016AT0278 → B064-016AT0094 → B064-016AT0296 → B064-016AT0110 → B064-016AT0109 → B064-016AT0285 → B025-016DT0068 → B025-016DT0067 → B025-016DT0066 → B025-016DT0065 → B025-016DT0064 → B025-016DT0063 → B025-016DT0062 → B025-016DT0061 → B025-016DT0060 → B025-996DT0020 → B025-016DT0059 → B025-016DT0054 → B025-016DT0053 → B025-016DT0051 → B025-996DT0018 → B025-016DT0052 → B025-016DT0050 → B025-016DT0049 → B025-016DT0048 → B025-016DT0047 → B025-996DT0008 → M0521 → D0528-L11 → B078-006AT0001 → END
B1-UPSP-64701 | -P20 | 06 |  | PE-L1-3C10-02 | PE-L1-3C10-02 | INC-0037-1 |  | DONE | 1 | 948 | B1-UPSP-64701-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 10sqmm | PE-L1-3C10-02 | 3 | 230 | U | 110 | GAS METERING SYSTEM | B1-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-FM-4402 | GAS METERING PANEL (BLOCK #1) PRIMARY | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B164-006GT0201 → B164-006GT0001 → B164-006GT0002 → B164-006GT0003 → B064-006AC0018 → M0501 → B064-996GT0020 → B064-016GT0033 → B064-016GT0229 → B064-016GT0230 → B064-016GT0047 → B064-016GT0048 → B064-016GT0239 → B064-996GT0013 → B064-996GT0053 → B064-996GT0073 → B064-037AT0214 → B064-037AT0039 → B064-037AT0040 → B064-037AT0041 → B064-037AT0228 → B064-037AT0227 → END
B1-UPSP-64702 | -P20 | 05 |  | PE-L1-3C10-02 | PE-L1-3C10-02 | INC-0037-2 |  | DONE | 1 | 949 | B1-UPSP-64702-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 10sqmm | PE-L1-3C10-02 | 3 | 230 | U | 120 | GAS METERING SYSTEM | B1-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-FM-4402 | GAS METERING PANEL (BLOCK #1) SECONDARY | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B164-006HT0202 → B164-006HT0007 → B164-006HT0008 → B164-006HT0009 → B164-006HT0010 → B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0019 → M0501 → B064-996AT0020 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0014 → B064-036AT0015 → B064-036AT0016 → B064-036AT0217 → B064-036AT0218 → B064-036AT0219 → B064-036AT0030 → B064-036AT0031 → END
B1-DB-64603 | -P20 | 03 | 재배정 | PE-L1-3C4-13 | PE-L1-3C4-16 | INC-0037-3 |  | DONE | 1 | 950 | B1-DB-64603-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-16 | 1 | 230 | N | 160 | GAS METERING SYSTEM | B1-DB-64603 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-FM-4402 | GAS METERING PANEL (BLOCK #1) NORMAL | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0095 → B064-016AT0094 → B064-016AT0278 → B064-016AT0277 → B064-016AT0067 → B064-016AT0068 → B064-016AT0290 → B064-016AT0240 → B064-016AT0049 → B064-016AT0048 → B064-016AT0234 → B064-016AT0233 → B064-016AT0232 → B064-016AT0013 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0014 → B064-036AT0015 → B064-036AT0016 → B064-036AT0217 → B064-036AT0218 → B064-036AT0219 → B064-036AT0030 → B064-036AT0031 → END
B2-UPSP-64701 | -P20 | 06 |  | PE-L1-3C16-01 | PE-L1-3C16-01 | INC-0037-4 |  |  | 1 | 951 | B2-UPSP-64701-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 16sqmm | PE-L1-3C16-01 | 3 | 230 | U | 100 | GAS METERING SYSTEM | B2-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-FM-4403 | GAS METERING PANEL (BLOCK #2) PRIMARY | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016DT0061 → B264-016DT0248 → B264-016ET0062 → B264-006AC0015 → M0407 → B264-996AT0013 → B264-016AT0048 → B264-016AT0049 → B264-016AT0050 → B264-016AT0240 → B264-016AT0055 → B264-016AT0056 → B264-016AT0243 → END
B2-UPSP-64702 | -P20 | 05 |  | PE-L1-3C10-02 | PE-L1-3C10-02 | INC-0037-5 | DONE(10/27) | DONE | 1 | 952 | B2-UPSP-64702-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 10sqmm | PE-L1-3C10-02 | 3 | 230 | U | 100 | GAS METERING SYSTEM | B2-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-FM-4403 | GAS METERING PANEL (BLOCK #2) SECONDARY | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016ET0061 → B264-016ET0248 → B264-016ET0062 → B264-006AC0015 → M0407 → B264-996BT0013 → B264-016BT0048 → B264-016BT0049 → B264-016BT0050 → B264-016BT0240 → B264-016BT0055 → B264-016BT0056 → B264-016BT0243 → END
B2-DB-64603 | -P20 | 02 |  | PE-L1-3C4-19 | PE-L1-3C4-19 | INC-0037-6 |  |  | 1 | 953 | B2-DB-64603-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-19 | 1 | 230 | N | 50 | GAS METERING SYSTEM | B2-DB-64603 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-FM-4403 | GAS METERING PANEL (BLOCK #2) NORMAL | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016AT0027 → B264-016AT0028 → B264-016AT0029 → B264-016AT0030 → B264-016AT0031 → B264-016AT0032 → END
B0-UPSP-64702 | -P20 | 08 |  | PE-L1-3C50/25-01 | PE-L1-3C50/25-01 | INC-0040 |  |  | 1 | 954 | B0-UPSP-64702-P2008 | 0.6/1kV CU/XLPE/LSZH | 2C x 50sqmm + 1C X 25sqmm | PE-L1-3C50/25-01 | 3 | 230 | U | 480 | OIL METERING SYSTEM | B0-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-FM-4601 | OIL METERING PANEL PRIMARY | 21_DIESEL OIL PUMP STATION | L1, N, PE | B064-006FT0206 → B064-006FT0009 → B064-006FT0208 → B064-006FT0207 → B064-006FT0005 → B064-006AC0024 → M0501 → D0503-L35 → M0502 → D0504-L35 → M0503 → D0501-L35 → M0328 → D0324-L35 → M0329 → B114-997AT0021 → B114-017AT0020 → B114-017AT0025 → B025-017ET0032 → B025-017ET0031 → B025-017ET0030 → B025-017ET0020 → B025-017ET0019 → B025-017ET0018 → B025-017ET0017 → B025-017ET0016 → B025-997ET0003 → M0103 → B070-007AC0007 → END
B0-UPSP-64701 | -P20 | 07 |  | PE-L1-3C50/25-02 | PE-L1-3C50/25-02 | INC-0041 |  |  | 1 | 955 | B0-UPSP-64701-P2007 | 0.6/1kV CU/XLPE/LSZH | 2C x 50sqmm + 1C X 25sqmm | PE-L1-3C50/25-02 | 3 | 230 | U | 580 | OIL METERING SYSTEM | B0-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-FM-4601 | OIL METERING PANEL SECONDARY | 21_DIESEL OIL PUMP STATION | L1, N, PE | B164-006HT0205 → B164-006HT0004 → B164-006HT0005 → B064-006AC0011 → M0501 → D0503-L35 → M0502 → D0504-L35 → M0503 → D0501-L35 → M0328 → D0324-L35 → M0329 → B114-996AT0021 → B114-016AT0020 → B114-016AT0025 → B025-016FT0042 → B025-016FT0041 → B025-016FT0040 → B025-996FT0016 → B025-016FT0039 → B025-016FT0038 → B025-016FT0036 → B025-016FT0035 → B025-016FT0033 → B025-016FT0032 → B025-016FT0031 → B025-016FT0030 → B025-016FT0020 → B025-016FT0019 → B025-016FT0018 → B025-016FT0017 → B025-016FT0016 → B025-996FT0003 → M0103 → B070-007AC0008 → END
B0-DB-49602 | -P20 | 01 |  | PE-L1-3C16-01 | PE-L1-3C16-01 | INC-0042 |  |  | 1 | 956 | B0-DB-49602-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 16sqmm | PE-L1-3C16-01 | 1 | 230 | N | 400 | OIL METERING SYSTEM | B0-DB-49602 | 400V-230V DIST. BOARD FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, N, PE | B0-FM-4601 | OIL METERING PANEL NORMAL | 21_DIESEL OIL PUMP STATION | L1, N, PE | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L14 → M0207 → D0203-L21 → M0206 → D0205-L21 → M0205 → B025-996ET0004 → B025-016ET0022 → B025-016ET0021 → B025-016ET0020 → B025-016ET0019 → B025-016ET0018 → B025-016ET0017 → B025-016ET0016 → B025-996ET0003 → M0103 → B070-007AC0009 → END
B1-UPSP-64701 | -P20 | 07 |  | PE-L1-3C6-03 | PE-L1-3C6-03 | INC-0047 |  | DONE | 1 | 957 | B1-UPSP-64701-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-03 | 1.5 | 230 | U | 120 | VMS | B1-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-K-0011 | BLOCK #1 VMS (LER) PANEL PRIMARY | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B164-006GT0201 → B164-006GT0001 → B164-006GT0002 → B164-006GT0003 → B064-006AC0014 → M0501 → B064-996GT0020 → B064-016CT0033 → B064-016GT0229 → B064-016GT0230 → B064-016GT0047 → B064-016GT0048 → B064-016GT0239 → B064-996GT0013 → B064-996GT0053 → B064-996GT0073 → B064-037AT0214 → B064-037AT0039 → B064-037AT0040 → B064-037AT0041 → B064-037AT0228 → B064-037AT0227 → B064-037AT0226 → B064-037AT0027 → END
B1-UPSP-64702 | -P20 | 06 |  | PE-L1-3C6-01 | PE-L1-3C6-01 | INC-0048 |  | DONE | 1 | 958 | B1-UPSP-64702-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-01 | 1.5 | 230 | U | 110 | VMS | B1-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-K-0011 | BLOCK #1 VMS (LER) PANEL SECONDARY | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B164-006HT0202 → B164-006HT0201 → B164-006HT0001 → B164-006HT0002 → B164-006HT0003 → B064-006AC0015 → M0501 → B064-996AT0020 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0014 → B064-036AT0015 → B064-036AT0016 → B064-036AT0217 → B064-036AT0218 → B064-036AT0026 → B064-036AT0027 → END
B1-DB-64603 | -P20 | 04 | 재배정 | PE-L1-3C4-13 | PE-L1-3C4-16 | INC-0049 |  | DONE | 1 | 959 | B1-DB-64603-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-16 | 0.5 | 230 | N | 160 | VMS | B1-DB-64603 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-K-0011 | BLOCK #1 VMS (LER) PANEL NORMAL | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0095 → B064-016AT0094 → B064-016AT0278 → B064-016AT0277 → B064-016AT0067 → B064-016AT0068 → B064-016AT0290 → B064-016AT0240 → B064-016AT0049 → B064-016AT0048 → B064-016AT0234 → B064-016AT0233 → B064-016AT0232 → B064-016AT0013 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0014 → B064-036AT0015 → B064-036AT0016 → B064-036AT0217 → B064-036AT0218 → B064-036AT0026 → B064-036AT0027 → END
B1-UPSP-64702 | -P20 | 12 |  | PE-L1-3C6-05 | PE-L1-3C6-05 | INC-0049-001 |  | DONE | 1 | 960 | B1-UPSP-64702-P2012 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-05 | 1.5 | 230 | U | 110 | VMS | B1-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-K-0012 | BLOCK #1 VMS (LER) PANEL PRIMARY | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B164-006HT0202 → B164-006HT0201 → B164-006HT0001 → B164-006HT0002 → B164-006HT0003 → B064-006AC0015 → M0501 → B064-996AT0020 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0014 → B064-036AT0015 → B064-036AT0016 → B064-036AT0217 → B064-036AT0218 → B064-036AT0026 → B064-036AT0027 → END
B1-UPSP-64701 | -P20 | 13 |  | PE-L1-3C6-05 | PE-L1-3C6-05 | INC-0049-002 |  | DONE | 1 | 961 | B1-UPSP-64701-P2013 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-05 | 1.5 | 230 | U | 120 | VMS | B1-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-K-0012 | BLOCK #1 VMS (LER) PANEL SECONDARY | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B164-006GT0201 → B164-006GT0001 → B164-006GT0002 → B164-006GT0003 → B064-006AC0018 → M0501 → B064-996GT0020 → B064-016CT0033 → B064-016GT0229 → B064-016GT0230 → B064-016GT0047 → B064-016GT0048 → B064-016GT0239 → B064-996GT0013 → B064-996GT0053 → B064-996GT0073 → B064-037AT0214 → B064-037AT0039 → B064-037AT0040 → B064-037AT0041 → B064-037AT0228 → B064-037AT0227 → B064-037AT0226 → B064-037AT0027 → END
B1-DB-64603 | -P20 | 15 |  | PE-L1-3C6-05 | PE-L1-3C6-05 | INC-0049-003 |  | DONE | 1 | 962 | B1-DB-64603-P2015 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-05 | 0.5 | 230 | N | 160 | VMS | B1-DB-64603 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-K-0012 | BLOCK #1 VMS (LER) PANEL NORMAL | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0095 → B064-016AT0094 → B064-016AT0278 → B064-016AT0277 → B064-016AT0067 → B064-016AT0068 → B064-016AT0290 → B064-016AT0240 → B064-016AT0049 → B064-016AT0048 → B064-016AT0234 → B064-016AT0233 → B064-016AT0232 → B064-016AT0013 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0014 → B064-036AT0015 → B064-036AT0016 → B064-036AT0217 → B064-036AT0218 → B064-036AT0026 → B064-036AT0027 → END
B2-UPSP-64701 | -P20 | 07 |  | PE-L1-3C4-07 | PE-L1-3C4-07 | INC-0050 |  |  | 1 | 963 | B2-UPSP-64701-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-07 | 1.5 | 230 | U | 100 | VMS | B2-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-K-0021 | BLOCK #2 VMS (LER) PANEL PRIMARY | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016DT0061 → B264-016DT0248 → B264-016ET0062 → B264-006AC0008 → M0407 → B264-996AT0013 → B264-016AT0048 → B264-016AT0049 → B264-016AT0050 → B264-016AT0240 → B264-016AT0055 → B264-016AT0056 → B264-016AT0243 → END
B2-UPSP-64702 | -P20 | 06 |  | PE-L1-3C4-25 | PE-L1-3C4-25 | INC-0051 |  |  | 1 | 964 | B2-UPSP-64702-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-25 | 1.5 | 230 | U | 100 | VMS | B2-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-K-0021 | BLOCK #2 VMS (LER) PANEL SECONDARY | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016ET0061 → B264-016ET0248 → B264-016ET0062 → B264-006AC0006 → M0407 → B264-996BT0013 → B264-016BT0048 → B264-016BT0049 → B264-016BT0050 → B264-016BT0240 → B264-016BT0055 → B264-016BT0056 → B264-016BT0243 → END
B2-DB-64603 | -P20 | 03 |  | PE-L1-3C4-19 | PE-L1-3C4-19 | INC-0052 |  |  | 1 | 965 | B2-DB-64603-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-19 | 0.5 | 230 | N | 60 | VMS | B2-DB-64603 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-K-0021 | BLOCK #2 VMS (LER) PANEL NORMAL | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016AT0027 → B264-016AT0028 → B264-016AT0029 → B264-016AT0030 → B264-016AT0031 → B264-016AT0032 → B264-016AT0033 → B264-016AT0243 → END
B2-UPSP-64702 | -P20 | 13 |  | PE-L1-3C6-05 | PE-L1-3C6-05 | INC-0052-001 |  |  | 1 | 966 | B2-UPSP-64702-P2013 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-05 | 1.5 | 230 | U | 100 | VMS | B2-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-K-0022 | BLOCK #2 VMS (LER) PANEL PRIMARY | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016ET0061 → B264-016ET0248 → B264-016ET0062 → B264-006AC0006 → M0407 → B264-996BT0013 → B264-016BT0048 → B264-016BT0049 → B264-016BT0050 → B264-016BT0240 → B264-016BT0055 → B264-016BT0056 → B264-016BT0243 → END | 부하추가
B2-UPSP-64701 | -P20 | 14 |  | PE-L1-3C6-05 | PE-L1-3C6-05 | INC-0052-002 |  |  | 1 | 967 | B2-UPSP-64701-P2014 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-05 | 1.5 | 230 | U | 100 | VMS | B2-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-K-0022 | BLOCK #2 VMS (LER) PANEL SECONDARY | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016DT0061 → B264-016DT0248 → B264-016ET0062 → B264-006AC0008 → M0407 → B264-996AT0013 → B264-016AT0048 → B264-016AT0049 → B264-016AT0050 → B264-016AT0240 → B264-016AT0055 → B264-016AT0056 → B264-016AT0243 → END | 부하추가
B2-DB-64603 | -P20 | 16 |  | PE-L1-3C6-05 | PE-L1-3C6-05 | INC-0052-003 |  |  | 1 | 968 | B2-DB-64603-P2016 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-05 | 0.5 | 230 | N | 60 | VMS | B2-DB-64603 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-K-0022 | BLOCK #2 VMS (LER) PANEL NORMAL | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016AT0027 → B264-016AT0028 → B264-016AT0029 → B264-016AT0030 → B264-016AT0031 → B264-016AT0032 → B264-016AT0033 → B264-016AT0243 → END | 부하추가
B0-UPSP-69701 | -P20 | 03 |  | PE-L1-3C4-13 | PE-L1-3C4-13 | INC-0053 |  |  | 1 | 969 | B0-UPSP-69701-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-13 | 1 | 230 | U | 50 | VMS | B0-UPSP-69701 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ACC - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-K-0013 | BLOCK #1 VMS (ACC LER) PANEL PRIMARY | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-007AT0006 → B169-007AT0007 → B169-007AT0040 → B169-007AT0043 → END
B0-UPSP-69702 | -P20 | 03 |  | PE-L1-3C4-13 | PE-L1-3C4-13 | INC-0054 |  |  | 1 | 970 | B0-UPSP-69702-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-13 | 1 | 230 | U | 30 | VMS | B0-UPSP-69702 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ACC - B | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-K-0013 | BLOCK #1 VMS (ACC LER) PANEL SECONDARY | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0014 → B169-006AT0040 → END
B1-DB-69603 | -P20 | 14 |  | PE-L1-3C4-13 | PE-L1-3C4-13 | INC-0055 |  |  | 1 | 971 | B1-DB-69603-P2014 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-13 | 0.5 | 230 | N | 70 | VMS | B1-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-K-0013 | BLOCK #1 VMS (ACC LER) PANEL NORMAL | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0010 → B169-006AT0011 → B169-006AT0012 → B169-006AT0013 → B169-006AT0014 → B169-006AT0040 → END
B0-UPSP-69702 | -P20 | 04 |  | PE-L1-3C4-13 | PE-L1-3C4-13 | INC-0056 |  |  | 1 | 972 | B0-UPSP-69702-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-13 | 1 | 230 | U | 50 | VMS | B0-UPSP-69702 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ACC - B | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-K-0023 | BLOCK #2 VMS (ACC LER) PANEL PRIMARY | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-007AT0006 → B169-007AT0007 → B169-007AT0039 → B169-007AT0038 → B169-007AT0042 → END
B0-UPSP-69701 | -P20 | 04 |  | PE-L1-3C4-14 | PE-L1-3C4-14 | INC-0057 |  |  | 1 | 973 | B0-UPSP-69701-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-14 | 1 | 230 | U | 40 | VMS | B0-UPSP-69701 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ACC - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-K-0023 | BLOCK #2 VMS (ACC LER) PANEL SECONDARY | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0014 → B169-006AT0039 → B169-006AT0038 → END
B2-DB-69603 | -P20 | 14 |  | PE-L1-3C4-25 | PE-L1-3C4-25 | INC-0058 |  |  | 1 | 974 | B2-DB-69603-P2014 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-25 | 0.5 | 230 | N | 40 | VMS | B2-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-K-0023 | BLOCK #2 VMS (ACC LER) PANEL NORMAL | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0014 → B169-006AT0039 → B169-006AT0038 → END
B0-MCC-49601 | -P20 | 29 | 용량변경(200->108kW)에 따른 Cable 사양 변경(1C185x4line+1C95x1Line->5C95/50x1line) | PE-L1-1C185-03 | PE-L1-5C95/50-03 | INC-0059 |  |  | 1 | 975 | B0-MCC-49601-P2029 | 0.6/1kV CU/XLPE/LSZH | 4C x 95sqmm + 1C X 50sqmm | PE-L1-5C95/50-03 | 108 | 400 | N | 30 | EHT | B0-MCC-49601 | 400V MCC FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, N, PE | B0-HTP-00701 | EHT MAIN PDB PANEL (WWT BLD) | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, L2, L3, N, PE | B049-006CT0004 → B049-006CT0006 → B049-006CT0008 → END
B0-MCC-49601 | -P20 | 30 |  | PE-L1-1C185-03 | DEL |  |  |  | 1 | DEL | B0-MCC-49601-P2030 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | DEL |  | 400 | N |  | EHT | B0-MCC-49601 | 400V MCC FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L2 | B0-HTP-00701 | EHT MAIN PDB PANEL (WWT BLD) | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L2 | B049-006CT0004 → B049-006CT0006 → B049-006CT0008 → END
B0-MCC-49601 | -P20 | 31 |  | PE-L1-1C185-03 | DEL |  |  |  | 1 | DEL | B0-MCC-49601-P2031 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | DEL |  | 400 | N |  | EHT | B0-MCC-49601 | 400V MCC FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L3 | B0-HTP-00701 | EHT MAIN PDB PANEL (WWT BLD) | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L3 | B049-006CT0004 → B049-006CT0006 → B049-006CT0008 → END
B0-MCC-49601 | -P20 | 32 |  | PE-L1-1C185-04 | DEL |  |  |  | 1 | DEL | B0-MCC-49601-P2032 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | DEL |  | 400 | N |  | EHT | B0-MCC-49601 | 400V MCC FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | N | B0-HTP-00701 | EHT MAIN PDB PANEL (WWT BLD) | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | N | B049-006CT0004 → B049-006CT0006 → B049-006CT0008 → END
B0-MCC-49601 | -P20 | 33 |  | PE-L1-1C95-01 | DEL |  |  |  | 1 | DEL | B0-MCC-49601-P2033 | 0.6/1kV CU/XLPE/LSZH | 1C x 95sqmm | DEL |  | 400 | N |  | EHT | B0-MCC-49601 | 400V MCC FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | PE | B0-HTP-00701 | EHT MAIN PDB PANEL (WWT BLD) | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | PE | B049-006CT0004 → B049-006CT0006 → B049-006CT0008 → END
B0-MCC-49601 | -P20 | 34 | 용량변경(200->142kW) 'From변경 | PE-L1-1C300-01 | HOLD | INC-0059-001 | B0-MCC-49601-P2034 |  | 1 | 976 | B0-MCC-49602-P2044 | 0.6/1kV CU/XLPE/LSZH | 1C x 300sqmm | HOLD | 142 | 400 | N | 390 | EHT | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1 | B0-HTP-00704 | EHT MAIN PDB PANEL (DIST OIL P/P ST BLD) | 21_DIESEL OIL PUMP STATION | L1 | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L14 → M0207 → D0203-L15 → M0206 → D0205-L15 → M0205 → B025-996FT0005 → B025-016FT0029 → B025-016FT0028 → B025-016FT0020 → B025-016FT0019 → B025-016FT0018 → B025-016FT0017 → B025-016FT0016 → B025-996FT0003 → M0103 → B070-006AC0015 → END
B0-MCC-49601 | -P20 | 35 | From변경 | PE-L1-1C300-01 | HOLD |  | B0-MCC-49601-P2035 |  | 1 | 977 | B0-MCC-49602-P2045 | 0.6/1kV CU/XLPE/LSZH | 1C x 300sqmm | HOLD | 142 | 400 | N | 390 | EHT | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L2 | B0-HTP-00704 | EHT MAIN PDB PANEL (DIST OIL P/P ST BLD) | 21_DIESEL OIL PUMP STATION | L2 | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L14 → M0207 → D0203-L15 → M0206 → D0205-L15 → M0205 → B025-996FT0005 → B025-016FT0029 → B025-016FT0028 → B025-016FT0020 → B025-016FT0019 → B025-016FT0018 → B025-016FT0017 → B025-016FT0016 → B025-996FT0003 → M0103 → B070-006AC0015 → END
B0-MCC-49601 | -P20 | 36 | From변경 | PE-L1-1C300-02 | HOLD |  | B0-MCC-49601-P2036 |  | 1 | 978 | B0-MCC-49602-P2046 | 0.6/1kV CU/XLPE/LSZH | 1C x 300sqmm | HOLD | 142 | 400 | N | 390 | EHT | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L3 | B0-HTP-00704 | EHT MAIN PDB PANEL (DIST OIL P/P ST BLD) | 21_DIESEL OIL PUMP STATION | L3 | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L14 → M0207 → D0203-L15 → M0206 → D0205-L15 → M0205 → B025-996FT0005 → B025-016FT0029 → B025-016FT0028 → B025-016FT0020 → B025-016FT0019 → B025-016FT0018 → B025-016FT0017 → B025-016FT0016 → B025-996FT0003 → M0103 → B070-006AC0015 → END
B0-MCC-49601 | -P20 | 37 | From변경 | PE-L1-1C300-02 | HOLD |  | B0-MCC-49601-P2037 |  | 1 | 979 | B0-MCC-49602-P2047 | 0.6/1kV CU/XLPE/LSZH | 1C x 300sqmm | HOLD | 142 | 400 | N | 390 | EHT | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1 | B0-HTP-00704 | EHT MAIN PDB PANEL (DIST OIL P/P ST BLD) | 21_DIESEL OIL PUMP STATION | L1 | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L21 → M0207 → D0203-L21 → M0206 → D0205-L21 → M0205 → B025-996FT0005 → B025-016FT0029 → B025-016FT0028 → B025-016FT0020 → B025-016FT0019 → B025-016FT0018 → B025-016FT0017 → B025-016FT0016 → B025-996FT0003 → M0103 → B070-006AC0016 → END
B0-MCC-49601 | -P20 | 38 | From변경 | PE-L1-1C300-03 | HOLD |  | B0-MCC-49601-P2038 |  | 1 | 980 | B0-MCC-49602-P2038 | 0.6/1kV CU/XLPE/LSZH | 1C x 300sqmm | HOLD | 142 | 400 | N | 390 | EHT | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L2 | B0-HTP-00704 | EHT MAIN PDB PANEL (DIST OIL P/P ST BLD) | 21_DIESEL OIL PUMP STATION | L2 | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L21 → M0207 → D0203-L21 → M0206 → D0205-L21 → M0205 → B025-996FT0005 → B025-016FT0029 → B025-016FT0028 → B025-016FT0020 → B025-016FT0019 → B025-016FT0018 → B025-016FT0017 → B025-016FT0016 → B025-996FT0003 → M0103 → B070-006AC0016 → END
B0-MCC-49601 | -P20 | 39 | From변경 | PE-L1-1C300-03 | HOLD |  | B0-MCC-49601-P2039 |  | 1 | 981 | B0-MCC-49602-P2039 | 0.6/1kV CU/XLPE/LSZH | 1C x 300sqmm | HOLD | 142 | 400 | N | 390 | EHT | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L3 | B0-HTP-00704 | EHT MAIN PDB PANEL (DIST OIL P/P ST BLD) | 21_DIESEL OIL PUMP STATION | L3 | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L21 → M0207 → D0203-L21 → M0206 → D0205-L21 → M0205 → B025-996FT0005 → B025-016FT0029 → B025-016FT0028 → B025-016FT0020 → B025-016FT0019 → B025-016FT0018 → B025-016FT0017 → B025-016FT0016 → B025-996FT0003 → M0103 → B070-006AC0016 → END
B0-MCC-49601 | -P20 | 40 | From변경 | PE-L1-1C300-04 | HOLD |  | B0-MCC-49601-P2040 |  | 1 | 982 | B0-MCC-49602-P2040 | 0.6/1kV CU/XLPE/LSZH | 1C x 300sqmm | HOLD | 142 | 400 | N | 390 | EHT | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | N | B0-HTP-00704 | EHT MAIN PDB PANEL (DIST OIL P/P ST BLD) | 21_DIESEL OIL PUMP STATION | N | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L14 → M0207 → D0203-L15 → M0206 → D0205-L15 → M0205 → B025-996FT0005 → B025-016FT0029 → B025-016FT0028 → B025-016FT0020 → B025-016FT0019 → B025-016FT0018 → B025-016FT0017 → B025-016FT0016 → B025-996FT0003 → M0103 → B070-006AC0015 → END
B0-MCC-49601 | -P20 | 41 | From변경 | PE-L1-1C300-04 | HOLD |  | B0-MCC-49601-P2041 |  | 1 | 983 | B0-MCC-49602-P2041 | 0.6/1kV CU/XLPE/LSZH | 1C x 300sqmm | HOLD | 142 | 400 | N | 390 | EHT | B0-MCC-49602 | 400V MCC FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | PE | B0-HTP-00704 | EHT MAIN PDB PANEL (DIST OIL P/P ST BLD) | 21_DIESEL OIL PUMP STATION | PE | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0003 → B049-006BT0001 → D0204-L21 → M0207 → D0203-L21 → M0206 → D0205-L21 → M0205 → B025-996FT0005 → B025-016FT0029 → B025-016FT0028 → B025-016FT0020 → B025-016FT0019 → B025-016FT0018 → B025-016FT0017 → B025-016FT0016 → B025-996FT0003 → M0103 → B070-006AC0016 → END
B0-MCC-64601 | -P20 | 23 | 용량변경(200->172kW) | PE-L1-1C300-05 | HOLD | INC-0059-002 | 200->172kW |  | 1 | 984 | B0-MCC-64601-P2023 | 0.6/1kV CU/XLPE/LSZH | 1C x 300sqmm | HOLD | 172 | 400 | N | 370 | EHT | B0-MCC-64601 | 400V MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1 | B0-HTP-00703 | EHT MAIN PDB PANEL (AUX BOILER BLD) | 18_AUXILIARY BOILER / LER | L1 | B064-016BT0013 → B064-016BT0012 → B064-996BT0019 → M0501 → D0503-L41 → M0502 → D0504-L41 → M0503 → D0501-L41 → M0328 → D0324-L41 → M0329 → B114-996AT0021 → B114-016AT0020 → B114-016AT0025 → B025-016FT0042 → B025-016FT0041 → B025-016FT0040 → B025-016FT0043 → B025-016FT0044 → B025-016FT0045 → B025-016FT0046 → B025-016DT0047 → B025-996DT0008 → M0521 → D0528-L11 → B078-006AT0001 → END
B0-MCC-64601 | -P20 | 24 |  | PE-L1-1C300-05 | HOLD |  |  |  | 1 | 985 | B0-MCC-64601-P2024 | 0.6/1kV CU/XLPE/LSZH | 1C x 300sqmm | HOLD | 172 | 400 | N | 370 | EHT | B0-MCC-64601 | 400V MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L2 | B0-HTP-00703 | EHT MAIN PDB PANEL (AUX BOILER BLD) | 18_AUXILIARY BOILER / LER | L2 | B064-016BT0013 → B064-016BT0012 → B064-996BT0019 → M0501 → D0503-L41 → M0502 → D0504-L41 → M0503 → D0501-L41 → M0328 → D0324-L41 → M0329 → B114-996AT0021 → B114-016AT0020 → B114-016AT0025 → B025-016FT0042 → B025-016FT0041 → B025-016FT0040 → B025-016FT0043 → B025-016FT0044 → B025-016FT0045 → B025-016FT0046 → B025-016DT0047 → B025-996DT0008 → M0521 → D0528-L11 → B078-006AT0001 → END
B0-MCC-64601 | -P20 | 25 |  | PE-L1-1C300-06 | HOLD |  |  |  | 1 | 986 | B0-MCC-64601-P2025 | 0.6/1kV CU/XLPE/LSZH | 1C x 300sqmm | HOLD | 172 | 400 | N | 370 | EHT | B0-MCC-64601 | 400V MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L3 | B0-HTP-00703 | EHT MAIN PDB PANEL (AUX BOILER BLD) | 18_AUXILIARY BOILER / LER | L3 | B064-016BT0013 → B064-016BT0012 → B064-996BT0019 → M0501 → D0503-L41 → M0502 → D0504-L41 → M0503 → D0501-L41 → M0328 → D0324-L41 → M0329 → B114-996AT0021 → B114-016AT0020 → B114-016AT0025 → B025-016FT0042 → B025-016FT0041 → B025-016FT0040 → B025-016FT0043 → B025-016FT0044 → B025-016FT0045 → B025-016FT0046 → B025-016DT0047 → B025-996DT0008 → M0521 → D0528-L11 → B078-006AT0001 → END
B0-MCC-64601 | -P20 | 26 |  | PE-L1-1C300-06 | HOLD |  |  |  | 1 | 987 | B0-MCC-64601-P2026 | 0.6/1kV CU/XLPE/LSZH | 1C x 300sqmm | HOLD | 172 | 400 | N | 370 | EHT | B0-MCC-64601 | 400V MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1 | B0-HTP-00703 | EHT MAIN PDB PANEL (AUX BOILER BLD) | 18_AUXILIARY BOILER / LER | L1 | B064-016BT0013 → B064-016BT0012 → B064-996BT0019 → M0501 → D0503-L48 → M0502 → D0504-L48 → M0503 → D0501-L48 → M0328 → D0324-L48 → M0329 → B114-996AT0021 → B114-016AT0020 → B114-016AT0025 → B025-016FT0042 → B025-016FT0041 → B025-016FT0040 → B025-016FT0043 → B025-016FT0044 → B025-016FT0045 → B025-016FT0046 → B025-016DT0047 → B025-996DT0008 → M0521 → D0528-L12 → B078-006BT0001 → END
B0-MCC-64601 | -P20 | 27 |  | PE-L1-1C300-07 | HOLD |  |  |  | 1 | 988 | B0-MCC-64601-P2027 | 0.6/1kV CU/XLPE/LSZH | 1C x 300sqmm | HOLD | 172 | 400 | N | 370 | EHT | B0-MCC-64601 | 400V MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L2 | B0-HTP-00703 | EHT MAIN PDB PANEL (AUX BOILER BLD) | 18_AUXILIARY BOILER / LER | L2 | B064-016BT0013 → B064-016BT0012 → B064-996BT0019 → M0501 → D0503-L48 → M0502 → D0504-L48 → M0503 → D0501-L48 → M0328 → D0324-L48 → M0329 → B114-996AT0021 → B114-016AT0020 → B114-016AT0025 → B025-016FT0042 → B025-016FT0041 → B025-016FT0040 → B025-016FT0043 → B025-016FT0044 → B025-016FT0045 → B025-016FT0046 → B025-016DT0047 → B025-996DT0008 → M0521 → D0528-L12 → B078-006BT0001 → END
B0-MCC-64601 | -P20 | 28 |  | PE-L1-1C300-07 | HOLD |  |  |  | 1 | 989 | B0-MCC-64601-P2028 | 0.6/1kV CU/XLPE/LSZH | 1C x 300sqmm | HOLD | 172 | 400 | N | 370 | EHT | B0-MCC-64601 | 400V MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L3 | B0-HTP-00703 | EHT MAIN PDB PANEL (AUX BOILER BLD) | 18_AUXILIARY BOILER / LER | L3 | B064-016BT0013 → B064-016BT0012 → B064-996BT0019 → M0501 → D0503-L48 → M0502 → D0504-L48 → M0503 → D0501-L48 → M0328 → D0324-L48 → M0329 → B114-996AT0021 → B114-016AT0020 → B114-016AT0025 → B025-016FT0042 → B025-016FT0041 → B025-016FT0040 → B025-016FT0043 → B025-016FT0044 → B025-016FT0045 → B025-016FT0046 → B025-016DT0047 → B025-996DT0008 → M0521 → D0528-L12 → B078-006BT0001 → END
B0-MCC-64601 | -P20 | 29 |  | PE-L1-1C300-08 | HOLD |  |  |  | 1 | 990 | B0-MCC-64601-P2029 | 0.6/1kV CU/XLPE/LSZH | 1C x 300sqmm | HOLD | 172 | 400 | N | 370 | EHT | B0-MCC-64601 | 400V MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | N | B0-HTP-00703 | EHT MAIN PDB PANEL (AUX BOILER BLD) | 18_AUXILIARY BOILER / LER | N | B064-016BT0013 → B064-016BT0012 → B064-996BT0019 → M0501 → D0503-L41 → M0502 → D0504-L41 → M0503 → D0501-L41 → M0328 → D0324-L41 → M0329 → B114-996AT0021 → B114-016AT0020 → B114-016AT0025 → B025-016FT0042 → B025-016FT0041 → B025-016FT0040 → B025-016FT0043 → B025-016FT0044 → B025-016FT0045 → B025-016FT0046 → B025-016DT0047 → B025-996DT0008 → M0521 → D0528-L11 → B078-006AT0001 → END
B0-MCC-64601 | -P20 | 30 |  | PE-L1-1C300-08 | HOLD |  |  |  | 1 | 991 | B0-MCC-64601-P2030 | 0.6/1kV CU/XLPE/LSZH | 1C x 300sqmm | HOLD | 172 | 400 | N | 370 | EHT | B0-MCC-64601 | 400V MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | PE | B0-HTP-00703 | EHT MAIN PDB PANEL (AUX BOILER BLD) | 18_AUXILIARY BOILER / LER | PE | B064-016BT0013 → B064-016BT0012 → B064-996BT0019 → M0501 → D0503-L48 → M0502 → D0504-L48 → M0503 → D0501-L48 → M0328 → D0324-L48 → M0329 → B114-996AT0021 → B114-016AT0020 → B114-016AT0025 → B025-016FT0042 → B025-016FT0041 → B025-016FT0040 → B025-016FT0043 → B025-016FT0044 → B025-016FT0045 → B025-016FT0046 → B025-016DT0047 → B025-996DT0008 → M0521 → D0528-L12 → B078-006BT0001 → END
B0-MCC-64602 | -P20 | 23 | 용량변경(200->132kW) 'From변경 | PE-L1-1C185-04 | PE-L1-1C185-04 | INC-0060 | B0-MCC-64602-P2023 |  | 1 | 992 | B0-HTP-00716-P2023 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-04 | 132 | 400 | N | 160 | EHT | B0-HTP-00716 | LOCAL EHT CONTROL PANEL #6 | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1 | B0-HTP-00702 | EHT MAIN PDB PANEL (DIST POINT 10kV) | 19_DISTRIBUTION POINT 10KV WITH TP 10/0.4KV | L1 | B025-016FT0043 → B025-996FT0016 → B025-016FT0039 → B025-016FT0038 → B025-016FT0037 → B025-996FT0007 → PSP/INTEGRA TRAY
B0-MCC-64602 | -P20 | 24 | From변경 | PE-L1-1C185-04 | PE-L1-1C185-04 |  | B0-MCC-64602-P2024 |  | 1 | 993 | B0-HTP-00716-P2024 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-04 | 132 | 400 | N | 160 | EHT | B0-HTP-00716 | LOCAL EHT CONTROL PANEL #6 | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L2 | B0-HTP-00702 | EHT MAIN PDB PANEL (DIST POINT 10kV) | 19_DISTRIBUTION POINT 10KV WITH TP 10/0.4KV | L2 | B025-016FT0043 → B025-996FT0016 → B025-016FT0039 → B025-016FT0038 → B025-016FT0037 → B025-996FT0007 → PSP/INTEGRA TRAY
B0-MCC-64602 | -P20 | 25 | From변경 | PE-L1-1C185-04 | PE-L1-1C185-04 |  | B0-MCC-64602-P2025 |  | 1 | 994 | B0-HTP-00716-P2025 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-04 | 132 | 400 | N | 160 | EHT | B0-HTP-00716 | LOCAL EHT CONTROL PANEL #6 | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L3 | B0-HTP-00702 | EHT MAIN PDB PANEL (DIST POINT 10kV) | 19_DISTRIBUTION POINT 10KV WITH TP 10/0.4KV | L3 | B025-016FT0043 → B025-996FT0016 → B025-016FT0039 → B025-016FT0038 → B025-016FT0037 → B025-996FT0007 → PSP/INTEGRA TRAY
B0-MCC-64602 | -P20 | 26 | From변경 | PE-L1-1C185-04 | PE-L1-1C185-04 |  | B0-MCC-64602-P2026 |  | 1 | 995 | B0-HTP-00716-P2026 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-04 | 132 | 400 | N | 160 | EHT | B0-HTP-00716 | LOCAL EHT CONTROL PANEL #6 | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | N | B0-HTP-00702 | EHT MAIN PDB PANEL (DIST POINT 10kV) | 19_DISTRIBUTION POINT 10KV WITH TP 10/0.4KV | N | B025-016FT0043 → B025-996FT0016 → B025-016FT0039 → B025-016FT0038 → B025-016FT0037 → B025-996FT0007 → PSP/INTEGRA TRAY
B0-MCC-64602 | -P20 | 27 | From변경 | PE-L1-1C95-01 | PE-L1-1C95-01 |  | B0-MCC-64602-P2027 |  | 1 | 996 | B0-HTP-00716-P2027 | 0.6/1kV CU/XLPE/LSZH | 1C x 95sqmm | PE-L1-1C95-01 | 132 | 400 | N | 160 | EHT | B0-HTP-00716 | LOCAL EHT CONTROL PANEL #6 | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | PE | B0-HTP-00702 | EHT MAIN PDB PANEL (DIST POINT 10kV) | 19_DISTRIBUTION POINT 10KV WITH TP 10/0.4KV | PE | B025-016FT0043 → B025-996FT0016 → B025-016FT0039 → B025-016FT0038 → B025-016FT0037 → B025-996FT0007 → PSP/INTEGRA TRAY
B0-MCC-64602 | -P20 | 28 | DEL |  |  |  | B0-MCC-64602-P2028 |  | 1 | DEL | B0-MCC-64602-P2028 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm |  | 200 | 400 | N |  | EHT | B0-MCC-64602 | 400V MCC FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L3 | B0-HTP-00702 | EHT MAIN PDB PANEL (DIST POINT 10kV) | 19_DISTRIBUTION POINT 10KV WITH TP 10/0.4KV | L3 | B064-016BT0032 → B064-996BT0020 → M0501 → D0503-L45 → M0502 → D0504-L45 → M0503 → D0501-L45 → M0328 → D0324-L45 → M0329 → B114-996AT0021 → B114-016AT0020 → B114-016AT0025 → B025-016FT0042 → B025-016FT0041 → B025-016FT0040 → B025-996FT0016 → B025-016FT0039 → B025-016FT0038 → B025-016FT0037 → B025-996FT0007 → PSP/INTEGRA TRAY | DEL
B0-MCC-64602 | -P20 | 29 | DEL |  |  |  | B0-MCC-64602-P2029 |  | 1 | DEL | B0-MCC-64602-P2029 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm |  | 200 | 400 | N |  | EHT | B0-MCC-64602 | 400V MCC FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | N | B0-HTP-00702 | EHT MAIN PDB PANEL (DIST POINT 10kV) | 19_DISTRIBUTION POINT 10KV WITH TP 10/0.4KV | N | B064-016BT0032 → B064-996BT0020 → M0501 → D0503-L36 → M0502 → D0504-L36 → M0503 → D0501-L36 → M0328 → D0324-L36 → M0329 → B114-996AT0021 → B114-016AT0020 → B114-016AT0025 → B025-016FT0042 → B025-016FT0041 → B025-016FT0040 → B025-996FT0016 → B025-016FT0039 → B025-016FT0038 → B025-016FT0037 → B025-996FT0007 → PSP/INTEGRA TRAY | DEL
B0-MCC-64602 | -P20 | 30 | DEL |  |  |  | B0-MCC-64602-P2030 |  | 1 | DEL | B0-MCC-64602-P2030 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm |  | 200 | 400 | N |  | EHT | B0-MCC-64602 | 400V MCC FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | PE | B0-HTP-00702 | EHT MAIN PDB PANEL (DIST POINT 10kV) | 19_DISTRIBUTION POINT 10KV WITH TP 10/0.4KV | PE | B064-016BT0032 → B064-996BT0020 → M0501 → D0503-L45 → M0502 → D0504-L45 → M0503 → D0501-L45 → M0328 → D0324-L45 → M0329 → B114-996AT0021 → B114-016AT0020 → B114-016AT0025 → B025-016FT0042 → B025-016FT0041 → B025-016FT0040 → B025-996FT0016 → B025-016FT0039 → B025-016FT0038 → B025-016FT0037 → B025-996FT0007 → PSP/INTEGRA TRAY | DEL
B2-MCC-64603 | -P20 | 01 |  | PE-L1-5C95/50-04 | PE-L1-5C95/50-04 | INC-0075 | B2-MCC-64603-P2001 |  | 1 | 997 | B2-MCC-64603-P2030 | 0.6/1kV CU/XLPE/LSZH | 4C x 95sqmm + 1C X 50sqmm | PE-L1-5C95/50-04 | 66 | 400 | N | 150 | EHT | B2-MCC-64603 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, N, PE | B0-HTP-00721 | LOCAL EHT CONTROL PANEL #11 | 8.2 CCW PUMP/HEAT EXCHANGER BUILDING/PIPE-RACK | L1, L2, L3, N, PE | B264-016BT0026 → B264-016BT0025 → B264-016BT0206 → B264-996BT0001 → M0401 → D0403-L11 → M0402 → D0402-L11 → M0424 → B232-006AC0063 → END
B1-MCC-59601 | -P20 | 01 | From변경 | PE-L1-5C95/50-04 | PE-L1-5C95/50-04 | INC-0076 | B1-SWG-59601-P2001 | Cable no. 중복해소 | 1 | 998 | B1-MCC-59601-P2022 | 0.6/1kV CU/XLPE/LSZH | 4C x 95sqmm + 1C X 50sqmm | PE-L1-5C95/50-04 | 55 | 400 | N | 180 | EHT | B1-MCC-59601 | 400V MCC FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, L2, L3, N, PE | B0-HTP-00725 | LOCAL EHT CONTROL PANEL #15 | 4.2 STG GENERATOR STEP UP TR/PIPE-RACK | L1, L2, L3, N, PE | B159-006BT0003 → B159-006BT0019 → B159-006BT0006 → B159-006BT0018 → B159-006BT0010 → B159-006BT0022 → B159-006BT0023 → B159-006BT0024 → B159-006BT0013 → D0314-L21 → M0315 → D0313-L11 → M0312 → D0312-L11 → M0330 → D0404-L11 → M0408 → B213-006CC0023 → END
B0-MCC-72602 | -P20 | 08 | 용량변경(50->10.2kW)에 따른 Cable 사양 변경(5C25/16->5C16) 'From변경 | PE-L1-5C25/16-05 | PE-L1-5C16-03 | INC-0077 | B0-MCC-72602-P2008 |  | 1 | 999 | B0-MCC-72601-P2008 | 0.6/1kV CU/XLPE/LSZH | 5C x 16sqmm | PE-L1-5C16-03 | 10.2 | 400 | N | 160 | EHT | B0-MCC-72601 | 400V MCC FOR WORKSHOP - A | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, L2, L3, N, PE | B0-HTP-00729 | LOCAL EHT CONTROL PANEL #19 | 33.1_OIL STORAGE DYKE (nearby, field area) | L1, L2, L3, N, PE | B071-006AT0001 → D0101-L11 → M0102 → B025-996AT0001 → B025-016AT0004 → B025-016AT0005 → B025-016AT0006 → B025-016AT0009 → FIELD RUN
B0-MCC-72601 | -P20 | 07 | 재배정 (10/6) | PE-L1-5C120/70-08 | PE-L1-5C120/70-01 | INC-0078-001 | B0-MCC-72601-P2007 |  | 1 | 1000 | B0-MCC-72602-P2008 | 0.6/1kV CU/XLPE/LSZH | 4C x 120sqmm + 1C X 70sqmm | PE-L1-5C120/70-01 | 113 | 400 | N | 120 | EHT | B0-MCC-72602 | 400V MCC FOR WORKSHOP - B | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, L2, L3, N, PE | B0-HTP-00705 | EHT MAIN PDB PANEL (WORKSHOP BLD) | 24_WORKSHOP AND STORAGE RADIATION SHELTER (nearby, field area) | L1, L2, L3, N, PE | B071-006AT0001 → D0101-L12 → M0102 → B025-016AT0003 → B025-016AT0002 → FIELD RUN
B0-MCC-72601 | -P20 | 07 | 용량변경(16.2kW)에 따른 Cable 사양 변경(5C25/16->5C16)' ADD | PE-L1-5C25/16-05 | PE-L1-5C16-03 | INC-0078-002 | ADD | Cable no. 중복해소 | 1 | 1001 | B2-MCC-64603-P2031 | 0.6/1kV CU/XLPE/LSZH | 5C x 16sqmm | PE-L1-5C16-03 | 16.2 | 400 | N | 130 | EHT | B2-MCC-64603 | 400V MCC FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, N, PE | B0-HTP-00730 | LOCAL EHT CONTROL PANEL #20 | 53.2_IGNITION GAS CONTAINER | L1, L2, L3, N, PE | B264-016AT0027 → B264-016AT0225 → B264-996AT0011 → M0405 → D0421-L26 → M0406 → FIELD RUN
B2-MCC-69603 | -P20 | 09 | 용량변경(200->157kW) | PE-L1-1C185-02 | PE-L1-1C185-02 | INC-0060-003 |  |  | 1 | 1002 | B2-MCC-69603-P2009 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-02 | 157 | 400 | N | 60 | EHT | B2-MCC-69603 | 400V MCC FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1 | B0-HTP-00706 | EHT MAIN PDB PANEL (CEP BLD W/ACC LER) | 16_CEP BUILDING W/ACC LER | L1 | B169-006AT0013 → B169-006AT0012 → B169-006AT0011 → B169-006AT0010 → B169-006AT0009 → B169-006AT0008 → END
B2-MCC-69603 | -P20 | 10 |  | PE-L1-1C185-02 | PE-L1-1C185-02 |  |  |  | 1 | 1003 | B2-MCC-69603-P2010 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-02 | 157 | 400 | N | 60 | EHT | B2-MCC-69603 | 400V MCC FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L2 | B0-HTP-00706 | EHT MAIN PDB PANEL (CEP BLD W/ACC LER) | 16_CEP BUILDING W/ACC LER | L2 | B169-006AT0013 → B169-006AT0012 → B169-006AT0011 → B169-006AT0010 → B169-006AT0009 → B169-006AT0008 → END
B2-MCC-69603 | -P20 | 11 |  | PE-L1-1C185-02 | PE-L1-1C185-02 |  |  |  | 1 | 1004 | B2-MCC-69603-P2011 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-02 | 157 | 400 | N | 60 | EHT | B2-MCC-69603 | 400V MCC FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L3 | B0-HTP-00706 | EHT MAIN PDB PANEL (CEP BLD W/ACC LER) | 16_CEP BUILDING W/ACC LER | L3 | B169-006AT0013 → B169-006AT0012 → B169-006AT0011 → B169-006AT0010 → B169-006AT0009 → B169-006AT0008 → END
B2-MCC-69603 | -P20 | 12 |  | PE-L1-1C185-02 | PE-L1-1C185-02 |  |  |  | 1 | 1005 | B2-MCC-69603-P2012 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-02 | 157 | 400 | N | 60 | EHT | B2-MCC-69603 | 400V MCC FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | N | B0-HTP-00706 | EHT MAIN PDB PANEL (CEP BLD W/ACC LER) | 16_CEP BUILDING W/ACC LER | N | B169-006AT0013 → B169-006AT0012 → B169-006AT0011 → B169-006AT0010 → B169-006AT0009 → B169-006AT0008 → END
B2-MCC-69603 | -P20 | 13 |  | PE-L1-1C95-01 | PE-L1-1C95-01 |  |  |  | 1 | 1006 | B2-MCC-69603-P2013 | 0.6/1kV CU/XLPE/LSZH | 1C x 95sqmm | PE-L1-1C95-01 | 157 | 400 | N | 60 | EHT | B2-MCC-69603 | 400V MCC FOR ACC#2 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | PE | B0-HTP-00706 | EHT MAIN PDB PANEL (CEP BLD W/ACC LER) | 16_CEP BUILDING W/ACC LER | PE | B169-006AT0013 → B169-006AT0012 → B169-006AT0011 → B169-006AT0010 → B169-006AT0009 → B169-006AT0008 → END
B1-DB-59601 | -P20 | 12 |  | PE-L1-3C4-08 | PE-L1-3C4-08 | INC-0061 |  |  | 1 | 1007 | B1-DB-59601-P2012 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-08 | 0.35 | 230 | N | 230 | INST | B1-DB-59601 | 400V-230V DIST. BOARD FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-M-2601 | INSTRUMENT BOX 1 | 1.1_MAIN BUILDING COMPLEX (STG #1) | L1, N, PE | B159-006AT0003 → B159-006AT0014 → B159-006AT0005 → B159-006AT0018 → B159-006AT0017 → D0314-L24 → M0315 → D0315-L24 → M0318 → D0331-L14 → M0317 → B114-016BT0102 → B114-016BT0101 → B114-016BT0039 → B114-016BT0038 → B215-016BT0023 → B025-016BT0123 → END
B1-DB-59601 | -P20 | 13 |  | PE-L1-3C4-09 | PE-L1-3C4-09 | INC-0062 |  |  | 1 | 1008 | B1-DB-59601-P2013 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-09 | 0.35 | 230 | N | 230 | INST | B1-DB-59601 | 400V-230V DIST. BOARD FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-M-2602 | INSTRUMENT BOX 2 | 1.1_MAIN BUILDING COMPLEX (STG #1) | L1, N, PE | B159-006AT0003 → B159-006AT0014 → B159-006AT0005 → B159-006AT0018 → B159-006AT0017 → D0314-L24 → M0315 → D0315-L24 → M0318 → D0331-L14 → M0317 → B114-016BT0102 → B114-016BT0101 → B114-016BT0039 → B114-016BT0038 → B215-016BT0023 → B025-016BT0123 → END
B1-DB-59601 | -P20 | 14 |  | PE-L1-3C4-14 | PE-L1-3C4-14 | INC-0063 |  |  | 1 | 1009 | B1-DB-59601-P2014 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-14 | 0.35 | 230 | N | 250 | INST | B1-DB-59601 | 400V-230V DIST. BOARD FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-M-2701 | INSTRUMENT BOX 3 | 1.1_MAIN BUILDING COMPLEX (STG #1) | L1, N, PE | B159-006AT0003 → B159-006AT0014 → B159-006AT0005 → B159-006AT0018 → B159-006AT0017 → D0314-L24 → M0315 → D0315-L24 → M0318 → D0331-L14 → M0317 → B114-016BT0102 → B114-016BT0101 → B114-016BT0039 → B114-016BT0038 → B215-016BT0023 → B025-016BT0123 → B025-016BT0124 → END
B1-DB-59601 | -P20 | 15 |  | PE-L1-3C4-14 | PE-L1-3C4-14 | INC-0064 |  |  | 1 | 1010 | B1-DB-59601-P2015 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-14 | 0.35 | 230 | N | 250 | INST | B1-DB-59601 | 400V-230V DIST. BOARD FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-M-2702 | INSTRUMENT BOX 4 | 1.1_MAIN BUILDING COMPLEX (STG #1) | L1, N, PE | B159-006AT0003 → B159-006AT0014 → B159-006AT0005 → B159-006AT0018 → B159-006AT0017 → D0314-L24 → M0315 → D0315-L24 → M0318 → D0331-L14 → M0317 → B114-016BT0102 → B114-016BT0101 → B114-016BT0039 → B114-016BT0038 → B215-016BT0023 → B025-016BT0123 → B025-016BT0124 → END
B1-DB-64602 | -P20 | 02 |  | PE-L1-3C4-28 | PE-L1-3C4-28 | INC-0065 | DONE(10/12) | DONE | 1 | 1011 | B1-DB-64602-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-28 | 0.35 | 230 | N | 190 | INST | B1-DB-64602 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-M-3201 | INSTRUMENT BOX 5 | 7.1_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, N, PE | B164-016AT0115 → B164-996AT0023 → M0504 → D0531-L41 → M0510 → D0517-L16 → M0501 → D0503-L48 → M0502 → D0504-L48 → M0503 → B132-006AC0005 → B182-017AT0001 → B182-037AT0002 → B182-037AT0003 → B182-037AT0004 → B182-037AT0005 → B132-007AC0001 → END
B1-DB-64602 | -P20 | 03 |  | PE-L1-3C4-28 | PE-L1-3C4-28 | INC-0066 | DONE(10/6) | DONE | 1 | 1012 | B1-DB-64602-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-28 | 0.35 | 230 | N | 180 | INST | B1-DB-64602 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-M-3202 | INSTRUMENT BOX 6 | 8.1_CCW PUMP/HEAT EXCHANGER BUILDING | L1, N, PE | B164-016AT0115 → B164-996AT0023 → M0504 → D0531-L41 → M0510 → D0517-L16 → M0501 → D0503-L48 → M0502 → D0504-L48 → M0503 → B132-006AC0005 → B182-017AT0001 → B182-037AT0002 → B182-037AT0003 → B182-037AT0004 → B182-037AT0005 → B132-007AC0002 → END
B2-DB-59601 | -P20 | 11 |  | PE-L1-3C4-28 | PE-L1-3C4-28 | INC-0067 |  |  | 1 | 1013 | B2-DB-59601-P2011 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-28 | 0.35 | 230 | N | 190 | INST | B2-DB-59601 | 400V-230V DIST. BOARD FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B2-M-2601 | INSTRUMENT BOX 7 | 1.1_MAIN BUILDING COMPLEX (STG #2) | L1, N, PE | B259-006AT0003 → B259-006AT0014 → B259-006AT0015 → B259-006AT0016 → B259-006AT0017 → D0310-L25 → M0311 → D0311-L15 → M0312 → D0330-L14 → M0314 → B215-016BT0104 → B215-016BT0103 → B215-016BT0037 → B215-016BT0023 → B025-016BT0123 → END
B2-DB-59601 | -P20 | 12 |  | PE-L1-3C4-19 | PE-L1-3C4-19 | INC-0068 |  |  | 1 | 1014 | B2-DB-59601-P2012 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-19 | 0.35 | 230 | N | 190 | INST | B2-DB-59601 | 400V-230V DIST. BOARD FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B2-M-2602 | INSTRUMENT BOX 8 | 1.1_MAIN BUILDING COMPLEX (STG #2) | L1, N, PE | B259-006AT0003 → B259-006AT0014 → B259-006AT0015 → B259-006AT0016 → B259-006AT0017 → D0310-L25 → M0311 → D0311-L15 → M0312 → D0330-L14 → M0314 → B215-016BT0104 → B215-016BT0103 → B215-016BT0037 → B215-016BT0023 → B025-016BT0123 → END
B2-DB-59601 | -P20 | 13 |  | PE-L1-3C4-19 | PE-L1-3C4-19 | INC-0069 |  |  | 1 | 1015 | B2-DB-59601-P2013 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-19 | 0.35 | 230 | N | 210 | INST | B2-DB-59601 | 400V-230V DIST. BOARD FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B2-M-2701 | INSTRUMENT BOX 9 | 1.1_MAIN BUILDING COMPLEX (STG #2) | L1, N, PE | B259-006AT0003 → B259-006AT0014 → B259-006AT0015 → B259-006AT0016 → B259-006AT0017 → D0310-L26 → M0311 → D0311-L16 → M0312 → D0330-L15 → M0314 → B215-016BT0104 → B215-016BT0103 → B215-016BT0037 → B215-016BT0023 → B025-016BT0123 → B025-016BT0124 → END
B2-DB-59601 | -P20 | 14 |  | PE-L1-3C4-19 | PE-L1-3C4-19 | INC-0070 |  |  | 1 | 1016 | B2-DB-59601-P2014 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-19 | 0.35 | 230 | N | 210 | INST | B2-DB-59601 | 400V-230V DIST. BOARD FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B2-M-2702 | INSTRUMENT BOX 10 | 1.1_MAIN BUILDING COMPLEX (STG #2) | L1, N, PE | B259-006AT0003 → B259-006AT0014 → B259-006AT0015 → B259-006AT0016 → B259-006AT0017 → D0310-L26 → M0311 → D0311-L16 → M0312 → D0330-L15 → M0314 → B215-016BT0104 → B215-016BT0103 → B215-016BT0037 → B215-016BT0023 → B025-016BT0123 → B025-016BT0124 → END
B2-DB-64603 | -P20 | 04 |  | PE-L1-3C4-28 | PE-L1-3C4-28 | INC-0071 |  |  | 1 | 1017 | B2-DB-64603-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-28 | 0.35 | 230 | N | 220 | INST | B2-DB-64603 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-M-3201 | INSTRUMENT BOX 11 | 7.2_FIN FAN COOLER FOR CLOSED COOLING WATER(CCW) CLOSED TYPE | L1, N, PE | B264-016AT0027 → B264-016AT0026 → B264-016AT0025 → B264-016AT0206 → B264-996AT0001 → M0401 → D0403-L15 → M0402 → D0402-L15 → M0424 → D0422-L11 → M0403 → B232-006AC0005 → B282-017AT0001 → B282-037AT0002 → B282-037AT0003 → B282-037AT0004 → B282-037AT0005 → B232-007AC0001 → END
B2-DB-64603 | -P20 | 05 |  | PE-L1-3C4-28 | PE-L1-3C4-28 | INC-0072 |  |  | 1 | 1018 | B2-DB-64603-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-28 | 0.35 | 230 | N | 210 | INST | B2-DB-64603 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-M-3202 | INSTRUMENT BOX 12 | 8.2_CCW PUMP/HEAT EXCHANGER BUILDING | L1, N, PE | B264-016AT0027 → B264-016AT0026 → B264-016AT0025 → B264-016AT0206 → B264-996AT0001 → M0401 → D0403-L15 → M0402 → D0402-L15 → M0424 → D0422-L11 → M0403 → B232-006AC0005 → B282-017AT0001 → B282-037AT0002 → B282-037AT0003 → B282-037AT0004 → B282-037AT0005 → B232-007AC0002 → END
B1-DCP-64701 | -P20 | 01 |  | PE-L1-2C10-01 | PE-L1-2C10-01 | ELE-GCB-1001 |  | DONE | 1 | 1019 | B1-DCP-64701-P2001 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-01 | 1.7 | 220 | D | 130 | ELE - GCB | B1-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-CB-11301 | BLOCK #1 GENERATOR CIRCUIT BREAKER FOR GT#1 | 1.1_MAIN BUILDING COMPLEX | L+, L- | B164-006GT0203 → B164-006GT0002 → B164-006GT0003 → B064-006AC0009 → M0501 → D0517-L16 → M0510 → D0502-L41 → M0326 → D0320-L41 → M0325 → B161-007BC0017 → B161-017BC0004 → END
B1-DCP-64702 | -P20 | 01 |  | PE-L1-2C10-02 | PE-L1-2C10-02 | ELE-GCB-1002 |  | DONE | 1 | 1020 | B1-DCP-64702-P2001 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-02 | 1.7 | 220 | D | 140 | ELE - GCB | B1-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-CB-11301 | BLOCK #1 GENERATOR CIRCUIT BREAKER FOR GT#1 | 1.1_MAIN BUILDING COMPLEX | L+, L- | B164-006HT0204 → B164-006HT0008 → B164-006HT0009 → B164-006HT0010 → B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0009 → M0501 → D0517-L16 → M0510 → D0502-L41 → M0326 → D0320-L41 → M0325 → B161-007BC0017 → B161-017BC0004 → END
B1-DB-64602 | -P20 | 04 |  | PE-L1-3C6-02 | PE-L1-3C6-02 | ELE-GCB-1003 |  | DONE | 1 | 1021 | B1-DB-64602-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-02 | 1.71 | 230 | N | 110 | ELE - GCB | B1-DB-64602 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-CB-11301 | BLOCK #1 GENERATOR CIRCUIT BREAKER FOR GT#1 - AUX. POWER | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B164-016AT0115 → B164-996AT0023 → M0504 → D0531-L31 → M0510 → D0502-L41 → M0326 → D0320-L41 → M0325 → B161-007BC0018 → B161-017BC0005 → END
B1-DB-64602 | -P20 | 05 |  | PE-L1-3C10-01 | PE-L1-3C10-01 | ELE-GCB-1004 |  | DONE | 1 | 1022 | B1-DB-64602-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 10sqmm | PE-L1-3C10-01 | 2.3 | 230 | N | 110 | ELE - GCB | B1-DB-64602 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-CB-11301 | BLOCK #1 GENERATOR CIRCUIT BREAKER FOR GT#1 - MOTOR | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B164-016AT0115 → B164-996AT0023 → M0504 → D0531-L31 → M0510 → D0502-L41 → M0326 → D0320-L41 → M0325 → B161-007BC0018 → B161-017BC0005 → END
B1-DCP-64701 | -P20 | 02 |  | PE-L1-2C10-01 | PE-L1-2C10-01 | ELE-GCB-2001 |  | DONE | 1 | 1023 | B1-DCP-64701-P2002 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-01 | 1.7 | 220 | D | 190 | ELE - GCB | B1-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-CB-12301 | BLOCK #1 GENERATOR CIRCUIT BREAKER FOR GT#2 | 1.1_MAIN BUILDING COMPLEX | L+, L- | B164-006GT0203 → B164-006GT0002 → B164-006GT0003 → B064-006AC0008 → M0501 → D0517-L22 → M0510 → D0502-L31 → M0326 → D0320-L27 → M0325 → D0319-L23 → M0324 → D0327-L23 → M0327 → B161-007DC0017 → B161-017DC0004 → END
B1-DCP-64702 | -P20 | 02 |  | PE-L1-2C10-01 | PE-L1-2C10-01 | ELE-GCB-2002 |  | DONE | 1 | 1024 | B1-DCP-64702-P2002 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-01 | 1.7 | 220 | D | 200 | ELE - GCB | B1-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-CB-12301 | BLOCK #1 GENERATOR CIRCUIT BREAKER FOR GT#2 | 1.1_MAIN BUILDING COMPLEX | L+, L- | B164-006HT0204 → B164-006HT0008 → B164-006HT0009 → B164-006HT0010 → B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0008 → M0501 → D0517-L22 → M0510 → D0502-L31 → M0326 → D0320-L27 → M0325 → D0319-L23 → M0324 → D0327-L23 → M0327 → B161-007DC0017 → B161-017DC0004 → END
B1-DB-64604 | -P20 | 03 |  | PE-L1-3C10-01 | PE-L1-3C10-01 | ELE-GCB-2003 |  | DONE | 1 | 1025 | B1-DB-64604-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 10sqmm | PE-L1-3C10-01 | 1.71 | 230 | N | 180 | ELE - GCB | B1-DB-64604 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-CB-12301 | BLOCK #1 GENERATOR CIRCUIT BREAKER FOR GT#2 - AUX. POWER | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B164-016AT0118 → B164-016AT0117 → B164-016AT0116 → B164-996AT0023 → M0504 → D0531-L31 → M0510 → D0502-L31 → M0326 → D0320-L27 → M0325 → D0319-L23 → M0324 → D0327-L23 → M0321 → B161-007DC0018 → B161-017DC0005 → END
B1-DB-64603 | -P20 | 05 |  | PE-L1-3C16-01 | PE-L1-3C16-01 | ELE-GCB-2004 |  | DONE | 1 | 1026 | B1-DB-64603-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 16sqmm | PE-L1-3C16-01 | 2.3 | 230 | N | 190 | ELE - GCB | B1-DB-64603 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-CB-12301 | BLOCK #1 GENERATOR CIRCUIT BREAKER FOR GT#2 - MOTOR | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B164-016AT0094 → B164-016AT0093 → B164-016AT0092 → B164-996AT0022 → M0504 → D0531-L31 → M0510 → D0502-L31 → M0326 → D0320-L31 → M0325 → D0319-L23 → M0324 → D0327-L23 → M0321 → B161-007DC0018 → B161-017DC0005 → END
B2-DCP-64701 | -P20 | 01 |  | PE-L1-2C10-02 | PE-L1-2C10-02 | ELE-GCB-3001 |  |  | 1 | 1027 | B2-DCP-64701-P2001 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-02 | 1.7 | 220 | D | 160 | ELE - GCB | B2-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-CB-11301 | BLOCK #2 GENERATOR CIRCUIT BREAKER FOR GT#1 | 1.1_MAIN BUILDING COMPLEX | L+, L- | B264-016FT0063 → B264-016FT0062 → B264-006AC0006 → M0407 → D0302-L41 → M0302 → D0303-L41 → M0303 → D0305-L31 → M0306 → D0321-L31 → M0307 → B261-007DC0017 → B261-017DC0004 → END
B2-DCP-64702 | -P20 | 01 |  | PE-L1-2C10-02 | PE-L1-2C10-02 | ELE-GCB-3002 |  |  | 1 | 1028 | B2-DCP-64702-P2001 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-02 | 1.7 | 220 | D | 160 | ELE - GCB | B2-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-CB-11301 | BLOCK #2 GENERATOR CIRCUIT BREAKER FOR GT#1 | 1.1_MAIN BUILDING COMPLEX | L+, L- | B264-016ET0063 → B264-016ET0062 → B264-006AC0008 → M0407 → D0302-L41 → M0302 → D0303-L41 → M0303 → D0305-L31 → M0306 → D0321-L31 → M0307 → B261-007DC0017 → B261-017DC0004 → END
B2-DB-64601 | -P20 | 03 | From변경 | PE-L1-3C10-02 | PE-L1-3C10-02 | ELE-GCB-3003 | B2-DB-64601-P2003 |  | 1 | 1029 | B2-DB-64602-P2010 | 0.6/1kV CU/XLPE/LSZH | 3C x 10sqmm | PE-L1-3C10-02 | 1.71 | 230 | N | 170 | ELE - GCB | B2-DB-64602 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-CB-11301 | BLOCK #2 GENERATOR CIRCUIT BREAKER FOR GT#1 - AUX. POWER | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B264-016AT0045 → B264-016AT0046 → B264-016AT0047 → B264-996AT0013 → M0407 → D0302-L41 → M0302 → D0303-L41 → M0303 → D0305-L31 → M0306 → D0321-L31 → M0307 → B261-007DC0018 → B261-017DC0005 → END → END
B2-DB-64601 | -P20 | 04 |  | PE-L1-3C16-01 | PE-L1-3C16-01 | ELE-GCB-3004 |  |  | 1 | 1030 | B2-DB-64601-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 16sqmm | PE-L1-3C16-01 | 2.3 | 230 | N | 160 | ELE - GCB | B2-DB-64601 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-CB-11301 | BLOCK #2 GENERATOR CIRCUIT BREAKER FOR GT#1 - MOTOR | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B264-016AT0025 → B264-016AT0026 → B264-016AT0027 → B264-016AT0028 → B264-996AT0012 → M0407 → D0302-L41 → M0302 → D0303-L41 → M0303 → D0305-L31 → M0306 → D0321-L31 → M0307 → B261-007DC0018 → B261-017DC0005 → END
B2-DCP-64701 | -P20 | 02 |  | PE-L1-2C10-02 | PE-L1-2C10-02 | ELE-GCB-4001 |  |  | 1 | 1031 | B2-DCP-64701-P2002 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-02 | 1.7 | 220 | D | 110 | ELE - GCB | B2-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-CB-12301 | BLOCK #2 GENERATOR CIRCUIT BREAKER FOR GT#2 | 1.1_MAIN BUILDING COMPLEX | L+, L- | B264-016FT0063 → B264-016FT0062 → B264-006AC0011 → M0407 → D0302-L31 → M0302 → D0303-L31 → M0303 → B261-007BC0017 → B261-017BC0004 → END
B2-DCP-64702 | -P20 | 02 |  | PE-L1-2C6-02 | PE-L1-2C6-02 | ELE-GCB-4002 |  |  | 1 | 1032 | B2-DCP-64702-P2002 | 0.6/1kV CU/XLPE/LSZH | 2C x 6sqmm | PE-L1-2C6-02 | 1.74 | 220 | D | 110 | ELE - GCB | B2-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-CB-12301 | BLOCK #2 GENERATOR CIRCUIT BREAKER FOR GT#2 | 1.1_MAIN BUILDING COMPLEX | L+, L- | B264-016ET0063 → B264-016ET0062 → B264-006AC0011 → M0407 → D0302-L31 → M0302 → D0303-L31 → M0303 → B261-007BC0017 → B261-017BC0004 → END
B2-DB-64604 | -P20 | 04 |  | PE-L1-3C6-05 | PE-L1-3C6-05 | ELE-GCB-4003 |  |  | 1 | 1033 | B2-DB-64604-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-05 | 1.71 | 230 | N | 90 | ELE - GCB | B2-DB-64604 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-CB-12301 | BLOCK #2 GENERATOR CIRCUIT BREAKER FOR GT#2 - AUX. POWER | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B264-016CT0047 → B264-996CT0017 → M0407 → D0302-L31 → M0302 → D0303-L31 → M0303 → B261-007BC0018 → B261-017BC0005 → END
B2-DB-64603 | -P20 | 06 |  | PE-L1-3C10-02 | PE-L1-3C10-02 | ELE-GCB-4004 |  |  | 1 | 1034 | B2-DB-64603-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 10sqmm | PE-L1-3C10-02 | 2.3 | 230 | N | 90 | ELE - GCB | B2-DB-64603 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-CB-12301 | BLOCK #2 GENERATOR CIRCUIT BREAKER FOR GT#2 - MOTOR | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B264-016BT0027 → B264-016BT0028 → B264-996BT0012 → M0407 → D0302-L31 → M0302 → D0303-L31 → M0303 → B261-007BC0018 → B261-017BC0005 → END
B1-DCP-59702 | -P20 | 08 | From변경 | PE-L1-2C6-01 | PE-L1-2C6-01 | ELE-GCB-5001 | B1-DCP-59702-P2008 |  | 1 | 1035 | B1-DCP-59701-P2008 | 0.6/1kV CU/XLPE/LSZH | 2C x 6sqmm | PE-L1-2C6-01 | 1.74 | 220 | D | 100 | ELE - GCB | B1-DCP-59701 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L+, L- | B1-CB-13301 | BLOCK #1 GENERATOR CIRCUIT BREAKER FOR ST | 1.1_MAIN BUILDING COMPLEX | L+, L- | B159-006AT0005 → B159-006AT0018 → B159-006AT0017 → D0314-L23 → M0315 → D0315-L23 → M0318 → B113-007CC0004 → B113-017CC0001 → END
B1-DCP-59701 | -P20 | 08 | From변경 | PE-L1-2C6-01 | PE-L1-2C6-01 | ELE-GCB-5002 | B1-DCP-59701-P2008 |  | 1 | 1036 | B1-DCP-59702-P2008 | 0.6/1kV CU/XLPE/LSZH | 2C x 6sqmm | PE-L1-2C6-01 | 1.74 | 220 | D | 110 | ELE - GCB | B1-DCP-59702 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L+, L- | B1-CB-13301 | BLOCK #1 GENERATOR CIRCUIT BREAKER FOR ST | 1.1_MAIN BUILDING COMPLEX | L+, L- | B159-006BT0005 → B159-006BT0018 → B159-006BT0010 → B159-006BT0022 → B159-006BT0023 → B159-006BT0024 → B159-006BT0013 → D0314-L23 → M0315 → D0315-L23 → M0318 → B113-007CC0004 → B113-017CC0001 → END
B1-DB-59601 | -P20 | 16 |  | PE-L1-3C6-01 | PE-L1-3C6-01 | ELE-GCB-5003 |  |  | 1 | 1037 | B1-DB-59601-P2016 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-01 | 1.71 | 230 | N | 120 | ELE - GCB | B1-DB-59601 | 400V-230V DIST. BOARD FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-CB-13301 | BLOCK #1 GENERATOR CIRCUIT BREAKER FOR ST - AUX. POWER | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B159-006AT0003 → B159-006AT0019 → B159-006AT0006 → B159-006AT0018 → B159-006AT0017 → D0314-L23 → M0315 → D0315-L23 → M0318 → B113-006CC0016 → B113-016CC0001 → END
B1-DB-59602 | -P20 | 05 |  | PE-L1-3C6-02 | PE-L1-3C6-02 | ELE-GCB-5004 |  |  | 1 | 1038 | B1-DB-59602-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-02 | 2.3 | 230 | N | 100 | ELE - GCB | B1-DB-59602 | 400V-230V DIST. BOARD FOR ST #1 FOR BLOCK #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-CB-13301 | BLOCK #1 GENERATOR CIRCUIT BREAKER FOR ST - MOTOR | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B159-006AT0006 → B159-006AT0018 → B159-006AT0017 → D0314-L23 → M0315 → D0315-L23 → M0318 → B113-006CC0016 → B113-016CC0001 → END
B2-DCP-59702 | -P20 | 08 | From변경 | PE-L1-2C6-02 | PE-L1-2C6-02 | ELE-GCB-6001 | B2-DCP-59702-P2008 |  | 1 | 1039 | B2-DCP-59701-P2008 | 0.6/1kV CU/XLPE/LSZH | 2C x 6sqmm | PE-L1-2C6-02 | 1.74 | 220 | D | 90 | ELE - GCB | B2-DCP-59701 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L+, L- | B2-CB-13301 | BLOCK #2 GENERATOR CIRCUIT BREAKER FOR ST | 1.1_MAIN BUILDING COMPLEX | L+, L- | B259-006AT0014 → B259-006AT0015 → B259-006AT0016 → B259-006AT0017 → D0310-L26 → M0311 → D0311-L16 → M0312 → B213-007CC0004 → B213-017CC0001 → END
B2-DCP-59701 | -P20 | 08 |  | PE-L1-2C6-02 | PE-L1-2C6-02 | ELE-GCB-6002 | B2-DCP-59701-P2008 | Cable no. 중복해소 | 1 | 1040 | B2-DCP-59702-P2011 | 0.6/1kV CU/XLPE/LSZH | 2C x 6sqmm | PE-L1-2C6-02 | 1.74 | 220 | D | 110 | ELE - GCB | B2-DCP-59702 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L+, L- | B2-CB-13301 | BLOCK #2 GENERATOR CIRCUIT BREAKER FOR ST | 1.1_MAIN BUILDING COMPLEX | L+, L- | B259-006BT0005 → B259-006BT0018 → B259-006BT0010 → B259-006BT0022 → B259-006BT0023 → B259-006BT0024 → B259-006BT0013 → D0310-L26 → M0311 → D0311-L16 → M0312 → B213-007CC0004 → B213-017CC0001 → END
B2-DB-59601 | -P20 | 15 |  | PE-L1-3C6-07 | PE-L1-3C6-07 | ELE-GCB-6003 |  |  | 1 | 1041 | B2-DB-59601-P2015 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-07 | 1.71 | 230 | N | 110 | ELE - GCB | B2-DB-59601 | 400V-230V DIST. BOARD FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B2-CB-13301 | BLOCK #2 GENERATOR CIRCUIT BREAKER FOR ST - AUX. POWER | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B259-006AT0003 → B259-006AT0019 → B259-006AT0006 → B259-006AT0005 → B259-006AT0015 → B259-006AT0016 → B259-006AT0017 → D0310-L26 → M0311 → D0311-L16 → M0312 → B213-006CC0016 → B213-016CC0001 → END
B2-DB-59601 | -P20 | 16 |  | PE-L1-3C10-02 | PE-L1-3C10-02 | ELE-GCB-6004 |  |  | 1 | 1042 | B2-DB-59601-P2016 | 0.6/1kV CU/XLPE/LSZH | 3C x 10sqmm | PE-L1-3C10-02 | 2.3 | 230 | N | 100 | ELE - GCB | B2-DB-59601 | 400V-230V DIST. BOARD FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B2-CB-13301 | BLOCK #2 GENERATOR CIRCUIT BREAKER FOR ST - MOTOR | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B259-006AT0006 → B259-006AT0005 → B259-006AT0015 → B259-006AT0016 → B259-006AT0017 → D0310-L26 → M0311 → D0311-L16 → M0312 → B213-006CC0016 → B213-016CC0001 → END
B1-DB-64601 | -P20 | 03 |  | PE-L1-3C4-14 | PE-L1-3C4-14 | ELE-IPB-1003 |  | DONE | 1 | 1043 | B1-DB-64601-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-14 | 0.2 | 230 | N | 120 | ELE - IPB | B1-DB-64601 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-BD-11301 | PRESSURIZATION CABINET FOR BLOCK #1 GTG #1 | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B164-016AT0090 → B164-016AT0091 → B164-996AT0022 → M0504 → D0531-L37 → M0510 → D0502-L41 → M0326 → D0320-L41 → M0325 → B161-007BC0018 → B161-017BC0005 → END
B1-DB-64604 | -P20 | 04 |  | PE-L1-3C4-14 | PE-L1-3C4-14 | ELE-IPB-2003 |  | DONE | 1 | 1044 | B1-DB-64604-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-14 | 0.2 | 230 | N | 180 | ELE - IPB | B1-DB-64604 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-BD-12301 | PRESSURIZATION CABINET FOR BLOCK #1 GTG #2 | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B164-016AT0118 → B164-016AT0117 → B164-016AT0116 → B164-996AT0023 → M0504 → D0531-L31 → M0510 → D0502-L31 → M0326 → D0320-L31 → M0325 → D0319-L23 → M0324 → D0327-L23 → M0321 → B161-007DC0018 → B161-017DC0005 → END
B2-DB-64601 | -P20 | 05 |  | PE-L1-3C4-21 | PE-L1-3C4-21 | ELE-IPB-3003 |  |  | 1 | 1045 | B2-DB-64601-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-21 | 0.2 | 230 | N | 160 | ELE - IPB | B2-DB-64601 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-BD-11301 | PRESSURIZATION CABINET FOR BLOCK #2 GTG #1 | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B264-016AT0025 → B264-016AT0026 → B264-016AT0027 → B264-016AT0028 → B264-996AT0012 → M0407 → D0302-L41 → M0302 → D0303-L41 → M0303 → D0305-L31 → M0306 → D0321-L31 → M0307 → B261-007DC0018 → B261-017DC0005 → END
B2-DB-64604 | -P20 | 05 |  | PE-L1-3C4-21 | PE-L1-3C4-21 | ELE-IPB-4003 |  |  | 1 | 1046 | B2-DB-64604-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-21 | 0.2 | 230 | N | 90 | ELE - IPB | B2-DB-64604 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-BD-12301 | PRESSURIZATION CABINET FOR BLOCK #2 GTG #2 | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B264-016CT0047 → B264-996CT0017 → M0407 → D0302-L31 → M0302 → D0303-L31 → M0303 → B261-007BC0018 → B261-017BC0005 → END
B1-DB-59601 | -P20 | 17 |  | PE-L1-3C4-14 | PE-L1-3C4-14 | ELE-IPB-5003 |  |  | 1 | 1047 | B1-DB-59601-P2017 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-14 | 0.2 | 230 | N | 110 | ELE - IPB | B1-DB-59601 | 400V-230V DIST. BOARD FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-BD-13301 | PRESSURIZATION CABINET FOR BLOCK #1 STG #1 | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B159-006AT0003 → B159-006AT0014 → B159-006AT0005 → B159-006AT0018 → B159-006AT0017 → D0314-L23 → M0315 → D0315-L23 → M0318 → B113-007CC0005 → END
B2-DB-59601 | -P20 | 17 |  | PE-L1-3C4-28 | PE-L1-3C4-28 | ELE-IPB-6003 |  |  | 1 | 1048 | B2-DB-59601-P2017 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-28 | 0.2 | 230 | N | 100 | ELE - IPB | B2-DB-59601 | 400V-230V DIST. BOARD FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B2-BD-12301 | PRESSURIZATION CABINET FOR BLOCK #2 STG #1 | 1.1_MAIN BUILDING COMPLEX | L1, N, PE | B259-006AT0003 → B259-006AT0014 → B259-006AT0015 → B259-006AT0016 → B259-006AT0017 → D0310-L26 → M0311 → D0311-L16 → M0312 → B213-007CC0005 → END
B1-DCP-64701 | -P20 | 03 |  | PE-L1-2C10-02 | PE-L1-2C10-02 | ELE-SWG-1001 |  | DONE | 1 | 1049 | B1-DCP-64701-P2003 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-02 | 3.36 | 220 | D | 100 | SWGR & MCC | B1-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #1 (DC CONTROL-1) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006GT0203 → B164-006GT0002 → B164-006GT0003 → B064-006AC0016 → M0501 → B064-996GT0020 → B064-016GT0033 → B064-016GT0229 → B064-016GT0230 → B064-016GT0047 → B064-016GT0048 → B064-016GT0239 → B064-016GT0053 → B064-016GT0275 → B064-016GT0276 → B064-016GT0277 → B064-016GT0066 → END
B1-DCP-64702 | -P20 | 03 |  | PE-L1-2C10-01 | PE-L1-2C10-01 | ELE-SWG-1002 |  | DONE | 1 | 1050 | B1-DCP-64702-P2003 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-01 | 3.36 | 220 | D | 110 | SWGR & MCC | B1-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #1 (DC CONTROL-2) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0204 → B164-006HT0008 → B164-006HT0009 → B164-006HT0010 → B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0016 → M0501 → B064-996AT0020 → B064-016AT0012 → B064-016AT0011 → B064-016AT0212 → B064-016AT0213 → B064-016AT0214 → B064-016AT0063 → B064-016AT0064 → B064-016AT0065 → END
B1-DB-64602 | -P20 | 06 | 재배정 | PE-L1-3C4-14 | PE-L1-3C4-06 | ELE-SWG-1003 |  | DONE | 1 | 1051 | B1-DB-64602-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-06 | 3.34 | 230 | N | 50 | SWGR & MCC | B1-DB-64602 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #1 (AUX. POWER) | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0217 → B064-016AT0090 → B064-016AT0216 → B064-016AT0215 → B064-016AT0063 → B064-016AT0064 → B064-016AT0065 → END
B1-DCP-64701 | -P20 | 04 |  | PE-L1-2C4-03 | PE-L1-2C4-03 | ELE-SWG-1003-001 |  | DONE | 1 | 1052 | B1-DCP-64701-P2004 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-03 | 0.17 | 220 | D | 140 | SWGR & MCC | B1-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-ATS-64701 | HSBT - 10KV SWGR #1 FOR BLOCK #1 (DC CONTROL-1) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006GT0203 → B164-006GT0002 → B164-006GT0003 → B064-006AC0014 → M0501 → B064-996BT0020 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B164-016AT0094 → B164-016AT0093 → B164-016AT0092 → B164-016AT0091 → B164-016AT0216 → B164-016AT0215 → END
B1-DCP-64702 | -P20 | 04 |  | PE-L1-2C4-03 | PE-L1-2C4-03 | ELE-SWG-1003-002 |  | DONE | 1 | 1053 | B1-DCP-64702-P2004 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-03 | 0.17 | 220 | D | 100 | SWGR & MCC | B1-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-ATS-64701 | HSBT - 10KV SWGR #1 FOR BLOCK #1 (DC CONTROL-2) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0204 → B164-006HT0008 → B164-006HT0009 → B164-006HT0010 → B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0015 → M0501 → B064-996AT0020 → B064-016AT0012 → B064-016AT0011 → B064-016AT0212 → B064-016AT0213 → B064-016AT0214 → B064-016AT0215 → END
B1-DB-64602 | -P20 | 15 | 재배정 | PE-L1-3C4-14 | PE-L1-3C4-06 | ELE-SWG-1003-003 |  | DONE | 1 | 1054 | B1-DB-64602-P2015 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-06 | 0.1 | 230 | N | 40 | SWGR & MCC | B1-DB-64602 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-ATS-64701 | HSBT - 10KV SWGR #1 FOR BLOCK #1 (AUX. POWER) | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0106 → B164-016AT0217 → B164-016AT0090 → B164-016AT0216 → END
B1-DCP-64701 | -P20 | 05 |  | PE-L1-2C6-01 | PE-L1-2C6-01 | ELE-SWG-1004 |  | DONE | 1 | 1055 | B1-DCP-64701-P2005 | 0.6/1kV CU/XLPE/LSZH | 2C x 6sqmm | PE-L1-2C6-01 | 1.3 | 220 | D | 120 | SWGR & MCC | B1-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-SWG-64601 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #1 - A (DC CONTROL-1) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006GT0203 → B164-006GT0002 → B164-006GT0003 → B064-006AC0014 → M0501 → B064-996BT0020 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B164-016AT0094 → B164-016AT0093 → B164-016AT0092 → END
B1-DCP-64702 | -P20 | 05 |  | PE-L1-2C4-03 | PE-L1-2C4-03 | ELE-SWG-1005 |  | DONE | 1 | 1056 | B1-DCP-64702-P2005 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-03 | 1.3 | 220 | D | 100 | SWGR & MCC | B1-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-SWG-64601 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #1 - A (DC CONTROL-2) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0204 → B164-006HT0008 → B164-006HT0009 → B164-006HT0010 → B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0015 → M0501 → B064-996AT0120 → B064-016AT0032 → B064-016AT0213 → B064-016AT0214 → B064-016AT0215 → B064-016AT0216 → B064-016AT0091 → END
B1-DB-64602 | -P20 | 07 | 재배정 | PE-L1-3C4-14 | PE-L1-3C4-06 | ELE-SWG-1006 |  | DONE | 1 | 1057 | B1-DB-64602-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-06 | 2.1 | 230 | N | 40 | SWGR & MCC | B1-DB-64602 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-SWG-64601 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #1 - A (AC AUX. POWER) | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0106 → B064-016AT0217 → B064-016AT0090 → B064-016AT0091 → END
B1-DB-64602 | -P20 | 08 | 재배정 | PE-L1-3C4-14 | PE-L1-3C4-06 | ELE-SWG-1006-1 |  | DONE | 1 | 1058 | B1-DB-64602-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-06 | 0.87 | 230 | N | 40 | SWGR & MCC | B1-DB-64602 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-SWG-64601 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #1 - A (MOTOR SPACE HEATER) | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0106 → B064-016AT0217 → B064-016AT0090 → B064-016AT0091 → END
B1-DCP-64701 | -P20 | 06 |  | PE-L1-2C4-03 | PE-L1-2C4-03 | ELE-SWG-1007 |  | DONE | 1 | 1059 | B1-DCP-64701-P2006 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-03 | 0.67 | 220 | D | 140 | SWGR & MCC | B1-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-SWG-64602 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #1 - B (DC CONTROL-1) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006GT0203 → B164-006GT0002 → B164-006GT0003 → B064-006AC0016 → M0501 → B064-996BT0020 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B164-016AT0094 → B164-016AT0093 → B164-016AT0092 → B164-016AT0091 → B164-016AT0090 → B164-016AT0217 → B164-016AT0114 → END
B1-DCP-64702 | -P20 | 06 |  | PE-L1-2C4-03 | PE-L1-2C4-03 | ELE-SWG-1008 |  | DONE | 1 | 1060 | B1-DCP-64702-P2006 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-03 | 0.67 | 220 | D | 120 | SWGR & MCC | B1-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-SWG-64602 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #1 - B (DC CONTROL-2) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0204 → B164-006HT0008 → B164-006HT0009 → B164-006HT0010 → B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0017 → M0501 → B064-996AT0120 → B064-016AT0032 → B064-016AT0213 → B064-016AT0214 → B064-016AT0215 → B064-016AT0216 → B064-016AT0090 → B064-016AT0217 → B064-016AT0106 → B064-016AT0107 → END
B1-DB-64601 | -P20 | 04 | 재배정 | PE-L1-3C4-14 | PE-L1-3C4-06 | ELE-SWG-1009 |  | DONE | 1 | 1061 | B1-DB-64601-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-06 | 2.37 | 230 | N | 40 | SWGR & MCC | B1-DB-64601 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-SWG-64602 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #1 - B (AC AUX. POWER) | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0217 → B064-016AT0106 → B064-016AT0107 → END
B1-DB-64601 | -P20 | 05 | 재배정 | PE-L1-3C4-14 | PE-L1-3C4-06 | ELE-SWG-1009-1 |  | DONE | 1 | 1062 | B1-DB-64601-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-06 | 0.87 | 230 | N | 40 | SWGR & MCC | B1-DB-64601 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-SWG-64602 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #1 - B (MOTOR SPACE HEATER) | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0217 → B064-016AT0106 → B064-016AT0107 → END
B1-DCP-64701 | -P20 | 07 |  | PE-L1-2C10-02 | PE-L1-2C10-02 | ELE-SWG-1010 |  | DONE | 1 | 1063 | B1-DCP-64701-P2007 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-02 | 3.7 | 220 | D | 100 | SWGR & MCC | B1-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #1 (DC CONTROL-1) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006GT0203 → B164-006GT0002 → B164-006GT0003 → B064-006AC0017 → M0501 → B064-996GT0020 → B064-016GT0033 → B064-016GT0229 → B064-016GT0230 → B064-016GT0047 → B064-016GT0048 → B064-016GT0239 → B064-016GT0053 → B064-016GT0275 → B064-016GT0276 → B064-016GT0277 → B064-016GT0067 → END
B1-DCP-64702 | -P20 | 07 |  | PE-L1-2C10-01 | PE-L1-2C10-01 | ELE-SWG-1011 |  | DONE | 1 | 1064 | B1-DCP-64702-P2007 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-01 | 3.7 | 220 | D | 120 | SWGR & MCC | B1-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #1 (DC CONTROL-2) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0204 → B164-006HT0008 → B164-006HT0009 → B164-006HT0010 → B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0017 → M0501 → B064-996AT0020 → B064-016AT0012 → B064-016AT0011 → B064-016AT0212 → B064-016AT0213 → B064-016AT0214 → B064-016AT0063 → B064-016AT0064 → B064-016AT0065 → B064-016AT0066 → B064-016AT0067 → B064-016AT0068 → END
B1-DB-64604 | -P20 | 05 |  | PE-L1-3C6-01 | PE-L1-3C6-01 | ELE-SWG-1012 |  | DONE | 1 | 1065 | B1-DB-64604-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-01 | 3.32 | 230 | N | 60 | SWGR & MCC | B1-DB-64604 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #1 (AUX. POWER) | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0111 → B064-016AT0296 → B064-016AT0094 → B064-016AT0278 → B064-016AT0277 → B064-016AT0067 → B064-016AT0068 → END
B1-DCP-64701 | -P20 | 08 |  | PE-L1-2C4-02 | PE-L1-2C4-02 | ELE-SWG-1013 |  | DONE | 1 | 1066 | B1-DCP-64701-P2008 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-02 | 0.17 | 220 | D | 140 | SWGR & MCC | B1-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-ATS-64703 | HSBT - 10KV SWGR #3 FOR BLOCK #1 (DC CONTROL-1) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006GT0203 → B164-006GT0002 → B164-006GT0003 → B064-006AC0016 → M0501 → B064-996BT0020 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B164-016AT0094 → B164-016AT0093 → B164-016AT0092 → B164-016AT0091 → B164-016AT0216 → B164-016AT0215 → END
B1-DCP-64702 | -P20 | 08 |  | PE-L1-2C4-02 | PE-L1-2C4-02 | ELE-SWG-1014 |  | DONE | 1 | 1067 | B1-DCP-64702-P2008 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-02 | 0.17 | 220 | D | 100 | SWGR & MCC | B1-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-ATS-64703 | HSBT - 10KV SWGR #3 FOR BLOCK #1 (DC CONTROL-2) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0204 → B164-006HT0008 → B164-006HT0009 → B164-006HT0010 → B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0017 → M0501 → B064-996AT0020 → B064-016AT0012 → B064-016AT0011 → B064-016AT0212 → B064-016AT0213 → B064-016AT0214 → B064-016AT0215 → END
B1-DB-64602 | -P20 | 09 | 재배정 | PE-L1-3C4-14 | PE-L1-3C4-06 | ELE-SWG-1015 |  | DONE | 1 | 1068 | B1-DB-64602-P2009 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-06 | 0.1 | 230 | N | 40 | SWGR & MCC | B1-DB-64602 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-ATS-64703 | HSBT - 10KV SWGR #3 FOR BLOCK #1 (AUX. POWER) | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0106 → B064-016AT0217 → B064-016AT0090 → B064-016AT0216 → END
B1-DCP-64701 | -P20 | 09 |  | PE-L1-2C10-01 | PE-L1-2C10-01 | ELE-SWG-2001 |  | DONE | 1 | 1069 | B1-DCP-64701-P2009 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-01 | 3.36 | 220 | D | 100 | SWGR & MCC | B1-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #1 (DC CONTROL-1) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006GT0203 → B164-006GT0002 → B164-006GT0003 → B064-006AC0018 → M0501 → B064-996GT0020 → B064-016CT0033 → B064-016GT0229 → B064-016GT0230 → B064-016GT0047 → B064-016GT0048 → B064-016GT0239 → B064-016GT0053 → B064-016GT0275 → B064-016GT0276 → B064-016GT0277 → B064-016GT0076 → END
B1-DCP-64702 | -P20 | 09 |  | PE-L1-2C10-01 | PE-L1-2C10-01 | ELE-SWG-2002 |  | DONE | 1 | 1070 | B1-DCP-64702-P2009 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-01 | 3.36 | 220 | D | 110 | SWGR & MCC | B1-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #1 (DC CONTROL-2) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0204 → B164-006HT0008 → B164-006HT0009 → B164-006HT0010 → B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0018 → M0501 → B064-996AT0020 → B064-016AT0012 → B064-016AT0011 → B064-016AT0212 → B064-016AT0213 → B064-016AT0214 → B064-016AT0215 → B064-016AT0073 → B064-016AT0074 → B064-016AT0075 → END
B1-DB-64601 | -P20 | 06 |  | PE-L1-3C6-01 | PE-L1-3C6-01 | ELE-SWG-2003 |  | DONE | 1 | 1071 | B1-DB-64601-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-01 | 3.34 | 230 | N | 50 | SWGR & MCC | B1-DB-64601 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #1 (AUX. POWER) | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0217 → B064-016AT0090 → B064-016AT0216 → B064-016AT0073 → B064-016AT0074 → B064-016AT0075 → END
B1-DCP-64701 | -P20 | 10 |  | PE-L1-2C4-02 | PE-L1-2C4-02 | ELE-SWG-2003-001 |  | DONE | 1 | 1072 | B1-DCP-64701-P2010 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-02 | 0.17 | 220 | D | 140 | SWGR & MCC | B1-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-ATS-64702 | HSBT - 10KV SWGR #2 FOR BLOCK #1 (DC CONTROL-1) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006GT0203 → B164-006GT0002 → B164-006GT0003 → B064-006AC0001 → M0501 → B064-996BT0020 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B164-016AT0094 → B164-016AT0093 → B164-016AT0092 → B164-016AT0091 → B164-016AT0216 → B164-016AT0215 → END
B1-DCP-64702 | -P20 | 10 |  | PE-L1-2C4-02 | PE-L1-2C4-02 | ELE-SWG-2003-002 |  | DONE | 1 | 1073 | B1-DCP-64702-P2010 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-02 | 0.17 | 220 | D | 100 | SWGR & MCC | B1-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-ATS-64702 | HSBT - 10KV SWGR #2 FOR BLOCK #1 (DC CONTROL-2) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0204 → B164-006HT0008 → B164-006HT0009 → B164-006HT0010 → B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0016 → M0501 → B064-996AT0020 → B064-016AT0012 → B064-016AT0011 → B064-016AT0212 → B064-016AT0213 → B064-016AT0214 → B064-016AT0215 → END
B1-DB-64603 | -P20 | 06 | 재배정 | PE-L1-3C4-14 | PE-L1-3C4-06 | ELE-SWG-2003-003 |  | DONE | 1 | 1074 | B1-DB-64603-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-06 | 0.1 | 230 | N | 60 | SWGR & MCC | B1-DB-64603 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-ATS-64702 | HSBT - 10KV SWGR #2 FOR BLOCK #1 (AUX. POWER) | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0095 → B064-016AT0094 → B064-016AT0278 → B064-016AT0076 → B064-016AT0075 → B064-016AT0074 → B064-016AT0073 → END
B1-DCP-64701 | -P20 | 11 |  | PE-L1-2C6-01 | PE-L1-2C6-01 | ELE-SWG-2004 |  | DONE | 1 | 1075 | B1-DCP-64701-P2011 | 0.6/1kV CU/XLPE/LSZH | 2C x 6sqmm | PE-L1-2C6-01 | 1.59 | 220 | D | 110 | SWGR & MCC | B1-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-SWG-64603 | 400V SWITCHGEAR FOR GT/HRSG #2 FOR BLOCK #1 - A (DC CONTROL-1) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006GT0203 → B164-006GT0002 → B164-006GT0003 → B064-006AC0022 → M0501 → B064-996BT0020 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B164-016AT0094 → B164-016AT0093 → END
B1-DCP-64702 | -P20 | 11 |  | PE-L1-2C6-01 | PE-L1-2C6-01 | ELE-SWG-2005 |  | DONE | 1 | 1076 | B1-DCP-64702-P2011 | 0.6/1kV CU/XLPE/LSZH | 2C x 6sqmm | PE-L1-2C6-01 | 1.59 | 220 | D | 120 | SWGR & MCC | B1-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-SWG-64603 | 400V SWITCHGEAR FOR GT/HRSG #2 FOR BLOCK #1 - A (DC CONTROL-2) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0204 → B164-006HT0008 → B164-006HT0009 → B164-006HT0010 → B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0006 → M0501 → B064-996AT0120 → B064-016AT0032 → B064-016AT0213 → B064-016AT0214 → B064-016AT0215 → B064-016AT0216 → B064-016AT0091 → B064-016AT0092 → B064-016AT0093 → B064-016AT0094 → END
B1-DB-64604 | -P20 | 06 | 재배정 | PE-L1-3C4-14 | PE-L1-3C4-06 | ELE-SWG-2006 |  | DONE | 1 | 1077 | B1-DB-64604-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-06 | 2.24 | 230 | N | 40 | SWGR & MCC | B1-DB-64604 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-SWG-64603 | 400V SWITCHGEAR FOR GT/HRSG #2 FOR BLOCK #1 - A (AUX. POWER) | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0111 → B064-016AT0296 → B064-016AT0094 → END
B1-DB-64604 | -P20 | 07 | 재배정 | PE-L1-3C4-14 | PE-L1-3C4-06 | ELE-SWG-2006-1 |  | DONE | 1 | 1078 | B1-DB-64604-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-06 | 0.4 | 230 | N | 40 | SWGR & MCC | B1-DB-64604 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-SWG-64603 | 400V SWITCHGEAR FOR GT/HRSG #2 FOR BLOCK #1 - A (MOTOR SPACE HEATER) | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0111 → B064-016AT0296 → B064-016AT0094 → END
B1-DCP-64701 | -P20 | 12 |  | PE-L1-2C10-02 | PE-L1-2C10-02 | ELE-SWG-2007 |  | DONE | 1 | 1079 | B1-DCP-64701-P2012 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-02 | 1.54 | 220 | D | 160 | SWGR & MCC | B1-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-SWG-64604 | 400V SWITCHGEAR FOR GT/HRSG #2 FOR BLOCK #1 - B (DC CONTROL-1) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006GT0203 → B164-006GT0002 → B164-006GT0003 → B064-006AC0006 → M0501 → B064-996BT0020 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B164-016AT0094 → B164-016AT0093 → B164-016AT0092 → B164-016AT0091 → B164-016AT0090 → B164-016AT0217 → B164-016AT0114 → B164-016AT0115 → B164-016AT0116 → B164-016AT0117 → END
B1-DCP-64702 | -P20 | 12 |  | PE-L1-2C6-01 | PE-L1-2C6-01 | ELE-SWG-2008 |  | DONE | 1 | 1080 | B1-DCP-64702-P2012 | 0.6/1kV CU/XLPE/LSZH | 2C x 6sqmm | PE-L1-2C6-01 | 1.54 | 220 | D | 130 | SWGR & MCC | B1-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-SWG-64604 | 400V SWITCHGEAR FOR GT/HRSG #2 FOR BLOCK #1 - B (DC CONTROL-2) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0204 → B164-006HT0008 → B164-006HT0009 → B164-006HT0010 → B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0021 → M0501 → B064-996AT0120 → B064-016AT0032 → B064-016AT0213 → B064-016AT0214 → B064-016AT0215 → B064-016AT0216 → B064-016AT0091 → B064-016AT0092 → B064-016AT0093 → B064-016AT0094 → B064-016AT0296 → B064-016AT0110 → END
B1-DB-64603 | -P20 | 07 | 재배정 | PE-L1-3C4-15 | PE-L1-3C4-06 | ELE-SWG-2009 |  | DONE | 1 | 1081 | B1-DB-64603-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-06 | 2.5 | 230 | N | 30 | SWGR & MCC | B1-DB-64603 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-SWG-64604 | 400V SWITCHGEAR FOR GT/HRSG #2 FOR BLOCK #1 - B (AUX. POWER) | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0095 → B064-016AT0296 → B064-016AT0110 → B064-016AT0109 → END
B1-DB-64603 | -P20 | 08 | 재배정 | PE-L1-3C4-15 | PE-L1-3C4-06 | ELE-SWG-2009-1 |  | DONE | 1 | 1082 | B1-DB-64603-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-06 | 0.3 | 230 | N | 30 | SWGR & MCC | B1-DB-64603 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-SWG-64604 | 400V SWITCHGEAR FOR GT/HRSG #2 FOR BLOCK #1 - B (MOTOR SPACE HEATER) | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0095 → B064-016AT0296 → B064-016AT0110 → B064-016AT0109 → END
B1-DCP-64701 | -P20 | 13 |  | PE-L1-2C10-01 | PE-L1-2C10-01 | ELE-SWG-2009-004 |  | DONE | 1 | 1083 | B1-DCP-64701-P2013 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-01 | 3.36 | 220 | D | 100 | SWGR & MCC | B1-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #1 (DC CONTROL-1) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006GT0203 → B164-006GT0002 → B164-006GT0003 → B064-006AC0019 → M0501 → B064-996GT0020 → B064-016GT0033 → B064-016GT0229 → B064-016GT0230 → B064-016GT0047 → B064-016GT0048 → B064-016GT0239 → B064-016GT0053 → B064-016GT0275 → B064-016GT0276 → B064-016GT0277 → B064-016GT0077 → END
B1-DCP-64702 | -P20 | 13 |  | PE-L1-2C10-01 | PE-L1-2C10-01 | ELE-SWG-2009-005 |  | DONE | 1 | 1084 | B1-DCP-64702-P2013 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-01 | 3.36 | 220 | D | 120 | SWGR & MCC | B1-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #1 (DC CONTROL-2) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0204 → B164-006HT0008 → B164-006HT0009 → B164-006HT0010 → B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0019 → M0501 → B064-996AT0020 → B064-016AT0012 → B064-016AT0011 → B064-016AT0212 → B064-016AT0213 → B064-016AT0214 → B064-016AT0215 → B064-016AT0073 → B064-016AT0074 → B064-016AT0075 → B064-016AT0076 → B064-016AT0077 → B064-016AT0078 → B064-016AT0079 → END
B1-DB-64604 | -P20 | 08 |  | PE-L1-3C10-01 | PE-L1-3C10-01 | ELE-SWG-2009-006 |  | DONE | 1 | 1085 | B1-DB-64604-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 10sqmm | PE-L1-3C10-01 | 4.33 | 230 | N | 60 | SWGR & MCC | B1-DB-64604 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #1 (AUX. POWER) | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0111 → B064-016AT0296 → B064-016AT0094 → B064-016AT0278 → B064-016AT0077 → B064-016AT0078 → B064-016AT0079 → END
B1-DCP-64701 | -P20 | 14 |  | PE-L1-2C4-02 | PE-L1-2C4-02 | ELE-SWG-2010 |  | DONE | 1 | 1086 | B1-DCP-64701-P2014 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-02 | 0.17 | 220 | D | 140 | SWGR & MCC | B1-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-ATS-64704 | HSBT - 10KV SWGR #4 FOR BLOCK #1 (DC CONTROL-1) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006GT0203 → B164-006GT0002 → B164-006GT0003 → B064-006AC0009 → M0501 → B064-996BT0020 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → B064-016BT0242 → B064-016BT0243 → B064-016BT0244 → B064-016BT0292 → B064-016BT0293 → B164-016AT0094 → B164-016AT0093 → B164-016AT0092 → B164-016AT0091 → B164-016AT0216 → B164-016AT0215 → END
B1-DCP-64702 | -P20 | 14 |  | PE-L1-2C4-02 | PE-L1-2C4-02 | ELE-SWG-2011 |  | DONE | 1 | 1087 | B1-DCP-64702-P2014 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-02 | 0.17 | 220 | D | 100 | SWGR & MCC | B1-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-ATS-64704 | HSBT - 10KV SWGR #4 FOR BLOCK #1 (DC CONTROL-2) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0204 → B164-006HT0008 → B164-006HT0009 → B164-006HT0010 → B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0009 → M0501 → B064-996AT0020 → B064-016AT0012 → B064-016AT0011 → B064-016AT0212 → B064-016AT0213 → B064-016AT0214 → B064-016AT0215 → END
B1-DB-64603 | -P20 | 09 | 재배정 | PE-L1-3C4-15 | PE-L1-3C4-06 | ELE-SWG-2012 |  | DONE | 1 | 1088 | B1-DB-64603-P2009 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-06 | 0.1 | 230 | N | 60 | SWGR & MCC | B1-DB-64603 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-ATS-64704 | HSBT - 10KV SWGR #4 FOR BLOCK #1 (AUX. POWER) | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0095 → B064-016AT0094 → B064-016AT0278 → B064-016AT0076 → B064-016AT0075 → B064-016AT0074 → B064-016AT0073 → END
B2-DCP-64701 | -P20 | 03 |  | PE-L1-2C10-02 | PE-L1-2C10-02 | ELE-SWG-3001 |  |  | 1 | 1089 | B2-DCP-64701-P2003 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-02 | 3.36 | 220 | D | 80 | SWGR & MCC | B2-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #2 (DC CONTROL-1) | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-017ET0063 → B264-017ET0248 → B264-017ET0060 → B264-006AC0001 → M0405 → B264-996AT0011 → B264-016AT0014 → B264-016AT0211 → B264-016AT0008 → END
B2-DCP-64702 | -P20 | 03 |  | PE-L1-2C10-02 | PE-L1-2C10-02 | ELE-SWG-3002 |  |  | 1 | 1090 | B2-DCP-64702-P2003 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-02 | 3.36 | 220 | D | 80 | SWGR & MCC | B2-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #2 (DC CONTROL-2) | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-016ET0063 → B264-016ET0248 → B264-016ET0060 → B264-006AC0001 → M0405 → B264-996CT0009 → B264-016BT0014 → B264-016BT0211 → B264-016BT0008 → END
B2-DB-64602 | -P20 | 02 |  | PE-L1-3C6-05 | PE-L1-3C6-05 | ELE-SWG-3003 |  |  | 1 | 1091 | B2-DB-64602-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-05 | 3.34 | 230 | N | 60 | SWGR & MCC | B2-DB-64602 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #2 (AUX. POWER) | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016AT0045 → B264-016AT0205 → B264-016AT0204 → B264-016AT0203 → B264-016AT0007 → B264-016AT0008 → END
B2-DCP-64701 | -P20 | 04 |  | PE-L1-2C4-06 | PE-L1-2C4-06 | ELE-SWG-3003-001 |  |  | 1 | 1092 | B2-DCP-64701-P2004 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-06 | 0.17 | 220 | D | 80 | SWGR & MCC | B2-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-ATS-64701 | HSBT - 10KV SWGR #1 FOR BLOCK #2 (DC CONTROL-1) | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-017ET0063 → B264-017ET0248 → B264-017ET0060 → B264-006AC0001 → M0405 → B264-996AT0011 → B264-016AT0014 → B264-016AT0013 → END
B2-DCP-64702 | -P20 | 04 |  | PE-L1-2C4-09 | PE-L1-2C4-09 | ELE-SWG-3003-002 |  |  | 1 | 1093 | B2-DCP-64702-P2004 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-09 | 0.17 | 220 | D | 80 | SWGR & MCC | B2-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-ATS-64701 | HSBT - 10KV SWGR #1 FOR BLOCK #2 (DC CONTROL-2) | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-016ET0063 → B264-016ET0248 → B264-016ET0060 → B264-006AC0001 → M0405 → B264-996CT0009 → B264-016BT0014 → B264-016BT0013 → END
B2-DB-64601 | -P20 | 06 |  | PE-L1-3C4-25 | PE-L1-3C4-25 | ELE-SWG-3003-003 |  |  | 1 | 1094 | B2-DB-64601-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-25 | 0.1 | 230 | N | 30 | SWGR & MCC | B2-DB-64601 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-ATS-64701 | HSBT - 10KV SWGR #1 FOR BLOCK #2 (AUX. POWER) | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016AT0024 → B264-016AT0204 → END
B2-DCP-64701 | -P20 | 05 |  | PE-L1-2C4-09 | PE-L1-2C4-09 | ELE-SWG-3004 |  |  | 1 | 1095 | B2-DCP-64701-P2005 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-09 | 1.3 | 220 | D | 80 | SWGR & MCC | B2-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-SWG-64601 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #2 - A (DC CONTROL-1) | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-017ET0063 → B264-017ET0062 → B264-006AC0008 → M0407 → B264-996AT0012 → B264-016AT0028 → B264-016AT0027 → B264-016AT0026 → B264-016AT0025 → END
B2-DCP-64702 | -P20 | 05 |  | PE-L1-2C4-09 | PE-L1-2C4-09 | ELE-SWG-3005 |  |  | 1 | 1096 | B2-DCP-64702-P2005 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-09 | 1.3 | 220 | D | 80 | SWGR & MCC | B2-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-SWG-64601 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #2 - A (DC CONTROL-2) | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-016ET0063 → B264-016ET0062 → B264-006AC0009 → M0407 → B264-996BT0012 → B264-016BT0028 → B264-016BT0027 → B264-016BT0026 → B264-016BT0025 → END
B2-DB-64602 | -P20 | 03 |  | PE-L1-3C4-25 | PE-L1-3C4-25 | ELE-SWG-3006 |  |  | 1 | 1097 | B2-DB-64602-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-25 | 2.12 | 230 | N | 40 | SWGR & MCC | B2-DB-64602 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-SWG-64601 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #2 - A (AC AUX. POWER) | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016AT0045 → B264-016AT0205 → B264-016AT0024 → B264-016AT0025 → END
B2-DB-64602 | -P20 | 04 |  | PE-L1-3C4-25 | PE-L1-3C4-25 | ELE-SWG-3006-1 |  |  | 1 | 1098 | B2-DB-64602-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-25 | 1.07 | 230 | N | 40 | SWGR & MCC | B2-DB-64602 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-SWG-64601 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #2 - A (MOTOR SPACE HEATER) | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016AT0045 → B264-016AT0205 → B264-016AT0024 → B264-016AT0025 → END
B2-DCP-64701 | -P20 | 06 |  | PE-L1-2C4-09 | PE-L1-2C4-09 | ELE-SWG-3007 |  |  | 1 | 1099 | B2-DCP-64701-P2006 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-09 | 0.67 | 220 | D | 80 | SWGR & MCC | B2-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-SWG-64602 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #2 - B (DC CONTROL-1) | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-016DT0063 → B264-016DT0062 → B264-006AC0008 → M0407 → B264-996AT0013 → B264-016AT0047 → B264-016BT0046 → END
B2-DCP-64702 | -P20 | 06 |  | PE-L1-2C4-09 | PE-L1-2C4-09 | ELE-SWG-3008 |  |  | 1 | 1100 | B2-DCP-64702-P2006 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-09 | 0.67 | 220 | D | 80 | SWGR & MCC | B2-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-SWG-64602 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #2 - B (DC CONTROL-2) | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-016ET0063 → B264-016ET0062 → B264-006AC0009 → M0407 → B264-996BT0013 → B264-016BT0047 → B264-016BT0046 → END
B2-DB-64601 | -P20 | 07 |  | PE-L1-3C4-11 | PE-L1-3C4-11 | ELE-SWG-3009 |  |  | 1 | 1101 | B2-DB-64601-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-11 | 2.38 | 230 | N | 50 | SWGR & MCC | B2-DB-64601 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-SWG-64602 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #2 - B (AC AUX. POWER) | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016AT0024 → B264-016AT0025 → B264-016AT0209 → B264-016AT0046 → END
B2-DB-64601 | -P20 | 08 |  | PE-L1-3C4-11 | PE-L1-3C4-11 | ELE-SWG-3009-1 |  |  | 1 | 1102 | B2-DB-64601-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-11 | 0.96 | 230 | N | 50 | SWGR & MCC | B2-DB-64601 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-SWG-64602 | 400V SWITCHGEAR FOR GT/HRSG #1 FOR BLOCK #2 - B (MOTOR SPACE HEATER) | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016AT0024 → B264-016AT0025 → B264-016AT0209 → B264-016AT0046 → END
B2-DCP-64701 | -P20 | 07 |  | PE-L1-2C10-02 | PE-L1-2C10-02 | ELE-SWG-3010 |  |  | 1 | 1103 | B2-DCP-64701-P2007 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-02 | 3.7 | 220 | D | 80 | SWGR & MCC | B2-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #2 (DC CONTROL-1) | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-016FT0063 → B264-016FT0248 → B264-016FT0060 → B264-006AC0001 → M0405 → B264-996AT0011 → B264-016AT0014 → B264-016AT0211 → B264-016AT0009 → END
B2-DCP-64702 | -P20 | 07 |  | PE-L1-2C10-02 | PE-L1-2C10-02 | ELE-SWG-3011 |  |  | 1 | 1104 | B2-DCP-64702-P2007 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-02 | 3.7 | 220 | D | 80 | SWGR & MCC | B2-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #2 (DC CONTROL-1) | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-016ET0063 → B264-016ET0248 → B264-016ET0060 → B264-006AC0002 → M0405 → B264-996CT0009 → B264-016BT0014 → B264-016BT0211 → B264-016BT0009 → END
B2-DB-64604 | -P20 | 06 |  | PE-L1-3C10-02 | PE-L1-3C10-02 | ELE-SWG-3012 |  |  | 1 | 1105 | B2-DB-64604-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 10sqmm | PE-L1-3C10-02 | 5.06 | 230 | N | 60 | SWGR & MCC | B2-DB-64604 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #2 (AUX. POWER) | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016BT0047 → B264-016BT0209 → B264-016BT0026 → B264-016BT0212 → B264-016BT0211 → B264-016BT0009 → END
B2-DCP-64701 | -P20 | 08 |  | PE-L1-2C4-09 | PE-L1-2C4-09 | ELE-SWG-3013 |  |  | 1 | 1106 | B2-DCP-64701-P2008 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-09 | 0.17 | 220 | D | 90 | SWGR & MCC | B2-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-ATS-64703 | HSBT - 10KV SWGR #3 FOR BLOCK #2 (DC CONTROL-1) | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-017ET0063 → B264-017ET0247 → B264-017ET0061 → B264-017ET0060 → B264-006AC0001 → M0405 → B264-996AT0011 → B264-016AT0014 → B264-016AT0013 → END
B2-DCP-64702 | -P20 | 08 |  | PE-L1-2C4-09 | PE-L1-2C4-09 | ELE-SWG-3014 |  |  | 1 | 1107 | B2-DCP-64702-P2008 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-09 | 0.17 | 220 | D | 80 | SWGR & MCC | B2-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-ATS-64703 | HSBT - 10KV SWGR #3 FOR BLOCK #2 (DC CONTROL-2) | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-016ET0063 → B264-016ET0248 → B264-016ET0060 → B264-006AC0001 → M0405 → B264-996CT0009 → B264-016BT0014 → B264-016BT0013 → END
B2-DB-64601 | -P20 | 09 |  | PE-L1-3C4-11 | PE-L1-3C4-11 | ELE-SWG-3015 |  |  | 1 | 1108 | B2-DB-64601-P2009 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-11 | 0.1 | 230 | N | 30 | SWGR & MCC | B2-DB-64601 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-ATS-64703 | HSBT - 10KV SWGR #3 FOR BLOCK #2 (AUX. POWER) | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016AT0024 → B264-016AT0204 → END
B2-DCP-64701 | -P20 | 09 |  | PE-L1-2C10-02 | PE-L1-2C10-02 | ELE-SWG-4001 |  |  | 1 | 1109 | B2-DCP-64701-P2009 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-02 | 3.36 | 220 | D | 70 | SWGR & MCC | B2-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #2 (DC CONTROL-1) | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-017ET0063 → B264-017ET0248 → B264-017ET0060 → B264-006AC0001 → M0405 → B264-996AT0011 → B264-016AT0014 → END
B2-DCP-64702 | -P20 | 09 |  | PE-L1-2C10-02 | PE-L1-2C10-02 | ELE-SWG-4002 |  |  | 1 | 1110 | B2-DCP-64702-P2009 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-02 | 3.36 | 220 | D | 80 | SWGR & MCC | B2-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #2 (DC CONTROL-1) | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-016ET0063 → B264-016ET0248 → B264-016ET0060 → B264-006AC0002 → M0405 → B264-996CT0009 → B264-016BT0014 → B264-016BT0013 → END
B2-DB-64601 | -P20 | 10 |  | PE-L1-3C4-11 | PE-L1-3C4-11 | ELE-SWG-4003 |  |  | 1 | 1111 | B2-DB-64601-P2010 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-11 | 3.34 | 230 | N | 40 | SWGR & MCC | B2-DB-64601 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #2 (AUX. POWER) | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016AT0024 → B264-016AT0204 → B264-016AT0013 → END
B2-DCP-64701 | -P20 | 10 |  | PE-L1-2C4-09 | PE-L1-2C4-09 | ELE-SWG-4003-001 |  |  | 1 | 1112 | B2-DCP-64701-P2010 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-09 | 0.17 | 220 | D | 80 | SWGR & MCC | B2-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-ATS-64702 | HSBT - 10KV SWGR #2 FOR BLOCK #2 (DC CONTROL-1) | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-017ET0063 → B264-017ET0248 → B264-017ET0060 → B264-006AC0003 → M0405 → B264-996AT0011 → B264-016AT0014 → B264-016AT0013 → END
B2-DCP-64702 | -P20 | 10 |  | PE-L1-2C4-09 | PE-L1-2C4-09 | ELE-SWG-4003-002 |  |  | 1 | 1113 | B2-DCP-64702-P2010 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-09 | 0.17 | 220 | D | 80 | SWGR & MCC | B2-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-ATS-64702 | HSBT - 10KV SWGR #2 FOR BLOCK #2 (DC CONTROL-2) | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-016ET0063 → B264-016ET0248 → B264-016ET0060 → B264-006AC0001 → M0405 → B264-996CT0009 → B264-016BT0014 → B264-016BT0013 → END
B2-DB-64603 | -P20 | 07 |  | PE-L1-3C4-07 | PE-L1-3C4-07 | ELE-SWG-4003-003 |  |  | 1 | 1114 | B2-DB-64603-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-07 | 0.1 | 230 | N | 50 | SWGR & MCC | B2-DB-64603 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-ATS-64702 | HSBT - 10KV SWGR #2 FOR BLOCK #2 (AUX. POWER) | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016BT0027 → B264-016BT0026 → B264-016BT0025 → B264-016BT0024 → B264-016BT0204 → END
B2-DCP-64701 | -P20 | 11 |  | PE-L1-2C4-10 | PE-L1-2C4-10 | ELE-SWG-4004 |  |  | 1 | 1115 | B2-DCP-64701-P2011 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-10 | 1.59 | 220 | D | 70 | SWGR & MCC | B2-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-SWG-64603 | 400V SWITCHGEAR FOR GT/HRSG #2 FOR BLOCK #2 - A (DC CONTROL-1) | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-016DT0063 → B264-016DT0062 → B264-006AC0015 → M0407 → B264-996AT0012 → B264-016AT0028 → B264-016AT0027 → B264-016AT0026 → END
B2-DCP-64702 | -P20 | 11 |  | PE-L1-2C4-10 | PE-L1-2C4-10 | ELE-SWG-4005 |  |  | 1 | 1116 | B2-DCP-64702-P2011 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-10 | 1.59 | 220 | D | 70 | SWGR & MCC | B2-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-SWG-64603 | 400V SWITCHGEAR FOR GT/HRSG #2 FOR BLOCK #2 - A (DC CONTROL-2) | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-016ET0063 → B264-016ET0062 → B264-006AC0016 → M0407 → B264-996BT0012 → B264-016BT0028 → B264-016BT0027 → B264-016BT0026 → END
B2-DB-64604 | -P20 | 07 |  | PE-L1-3C4-07 | PE-L1-3C4-07 | ELE-SWG-4006 |  |  | 1 | 1117 | B2-DB-64604-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-07 | 2.24 | 230 | N | 40 | SWGR & MCC | B2-DB-64604 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-SWG-64603 | 400V SWITCHGEAR FOR GT/HRSG #2 FOR BLOCK #2 - A (AUX. POWER) | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016AT0047 → B264-016AT0209 → B264-016AT0026 → END
B2-DB-64604 | -P20 | 08 |  | PE-L1-3C4-07 | PE-L1-3C4-07 | ELE-SWG-4006-1 |  |  | 1 | 1118 | B2-DB-64604-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-07 | 0.4 | 230 | N | 40 | SWGR & MCC | B2-DB-64604 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-SWG-64603 | 400V SWITCHGEAR FOR GT/HRSG #2 FOR BLOCK #2 - A (MOTOR SPACE HEATER) | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016AT0047 → B264-016AT0209 → B264-016AT0026 → END
B2-DCP-64701 | -P20 | 12 |  | PE-L1-2C4-10 | PE-L1-2C4-10 | ELE-SWG-4007 |  |  | 1 | 1119 | B2-DCP-64701-P2012 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-10 | 1.54 | 220 | D | 60 | SWGR & MCC | B2-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-SWG-64604 | 400V SWITCHGEAR FOR GT/HRSG #2 FOR BLOCK #2 - B (DC CONTROL-1) | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-017ET0063 → B264-017ET0062 → B264-006AC0010 → M0407 → B264-996AT0013 → B264-016AT0047 → END
B2-DCP-64702 | -P20 | 12 |  | PE-L1-2C4-10 | PE-L1-2C4-10 | ELE-SWG-4008 |  |  | 1 | 1120 | B2-DCP-64702-P2012 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-10 | 1.54 | 220 | D | 60 | SWGR & MCC | B2-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-SWG-64604 | 400V SWITCHGEAR FOR GT/HRSG #2 FOR BLOCK #2 - B (DC CONTROL-2) | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-016ET0063 → B264-016ET0062 → B264-006AC0011 → M0407 → B264-996BT0013 → B264-016BT0047 → END
B2-DB-64603 | -P20 | 08 |  | PE-L1-3C4-07 | PE-L1-3C4-07 | ELE-SWG-4009 |  |  | 1 | 1121 | B2-DB-64603-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-07 | 2.5 | 230 | N | 40 | SWGR & MCC | B2-DB-64603 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-SWG-64604 | 400V SWITCHGEAR FOR GT/HRSG #2 FOR BLOCK #2 - B (AUX. POWER) | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016BT0027 → B264-016BT0026 → B264-016BT0209 → B264-016BT0047 → END
B2-DB-64603 | -P20 | 09 | 재배정 | PE-L1-3C4-05 | PE-L1-3C4-17 | ELE-SWG-4009-1 |  |  | 1 | 1122 | B2-DB-64603-P2009 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-17 | 0.5 | 230 | N | 40 | SWGR & MCC | B2-DB-64603 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-SWG-64604 | 400V SWITCHGEAR FOR GT/HRSG #2 FOR BLOCK #2 - B (MOTOR SPACE HEATER) | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016BT0027 → B264-016BT0026 → B264-016BT0209 → B264-016BT0047 → END
B2-DCP-64701 | -P20 | 13 |  | PE-L1-2C10-02 | PE-L1-2C10-02 | ELE-SWG-4009-004 |  |  | 1 | 1123 | B2-DCP-64701-P2013 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-02 | 3.36 | 220 | D | 70 | SWGR & MCC | B2-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #2 (DC CONTROL-1) | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-017ET0063 → B264-017ET0248 → B264-017ET0060 → B264-006AC0001 → M0405 → B264-996AT0011 → B264-016AT0014 → END
B2-DCP-64702 | -P20 | 13 |  | PE-L1-2C6-02 | PE-L1-2C6-02 | ELE-SWG-4009-005 |  |  | 1 | 1124 | B2-DCP-64702-P2013 | 0.6/1kV CU/XLPE/LSZH | 2C x 6sqmm | PE-L1-2C6-02 | 3.36 | 220 | D | 60 | SWGR & MCC | B2-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #2 (DC CONTROL-1) | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-016ET0063 → B264-016ET0248 → B264-016ET0060 → B264-006AC0002 → M0405 → B264-996CT0009 → B264-016BT0014 → END
B2-DB-64603 | -P20 | 10 |  | PE-L1-3C6-05 | PE-L1-3C6-05 | ELE-SWG-4009-006 |  |  | 1 | 1125 | B2-DB-64603-P2010 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-05 | 4.34 | 230 | N | 40 | SWGR & MCC | B2-DB-64603 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #2 (AUX. POWER) | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016BT0027 → B264-016BT0212 → B264-016BT0014 → END
B2-DCP-64701 | -P20 | 14 |  | PE-L1-2C4-10 | PE-L1-2C4-10 | ELE-SWG-4010 |  |  | 1 | 1126 | B2-DCP-64701-P2014 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-10 | 0.17 | 220 | D | 80 | SWGR & MCC | B2-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-ATS-64704 | HSBT - 10KV SWGR #4 FOR BLOCK #2 (DC CONTROL-1) | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-017ET0063 → B264-017ET0248 → B264-017ET0060 → B264-006AC0003 → M0405 → B264-996AT0011 → B264-016AT0014 → B264-016AT0013 → END
B2-DCP-64702 | -P20 | 14 |  | PE-L1-2C4-10 | PE-L1-2C4-10 | ELE-SWG-4011 |  |  | 1 | 1127 | B2-DCP-64702-P2014 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-10 | 0.17 | 220 | D | 80 | SWGR & MCC | B2-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-ATS-64704 | HSBT - 10KV SWGR #4 FOR BLOCK #2 (DC CONTROL-2) | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-016ET0063 → B264-016ET0248 → B264-016ET0060 → B264-006AC0001 → M0405 → B264-996CT0009 → B264-016BT0014 → B264-016BT0013 → END
B2-DB-64603 | -P20 | 11 | 재배정 | PE-L1-3C4-05 | PE-L1-3C4-17 | ELE-SWG-4012 |  |  | 1 | 1128 | B2-DB-64603-P2011 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-17 | 0.1 | 230 | N | 50 | SWGR & MCC | B2-DB-64603 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-ATS-64704 | HSBT - 10KV SWGR #4 FOR BLOCK #2 (AUX. POWER) | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016BT0027 → B264-016BT0026 → B264-016BT0025 → B264-016BT0024 → B264-016BT0204 → END
B1-DCP-59702 | -P20 | 09 |  | PE-L1-2C4-02 | PE-L1-2C4-02 | ELE-SWG-6001 |  |  | 1 | 1129 | B1-DCP-59702-P2009 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-02 | 1.01 | 220 | D | 40 | SWGR & MCC | B1-DCP-59702 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L+, L- | B1-SWG-59601 | 400V SWITCHGEAR FOR ST #1 FOR BLOCK #1 - A (DC CONTROL-1) | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L+, L- | B159-006AT0005 → B159-006AT0006 → B159-006AT0019 → B159-006AT0003 → END
B1-DCP-59701 | -P20 | 09 |  | PE-L1-2C4-02 | PE-L1-2C4-02 | ELE-SWG-6002 |  |  | 1 | 1130 | B1-DCP-59701-P2009 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-02 | 1.01 | 220 | D | 40 | SWGR & MCC | B1-DCP-59701 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L+, L- | B1-SWG-59601 | 400V SWITCHGEAR FOR ST #1 FOR BLOCK #1 - A (DC CONTROL-2) | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L+, L- | B159-006BT0005 → B159-006BT0006 → B159-006BT0019 → B159-006BT0003 → END
B1-DB-59602 | -P20 | 06 |  | PE-L1-3C4-15 | PE-L1-3C4-15 | ELE-SWG-6003 |  |  | 1 | 1131 | B1-DB-59602-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 1.83 | 230 | N | 40 | SWGR & MCC | B1-DB-59602 | 400V-230V DIST. BOARD FOR ST #1 FOR BLOCK #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-SWG-59601 | 400V SWITCHGEAR FOR ST #1 FOR BLOCK #1 - A (AUX. POWER) | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B159-006AT0005 → B159-006AT0014 → B159-006AT0003 → END
B1-DCP-59702 | -P20 | 10 |  | PE-L1-2C4-02 | PE-L1-2C4-02 | ELE-SWG-6004 |  |  | 1 | 1132 | B1-DCP-59702-P2010 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-02 | 0.67 | 220 | D | 30 | SWGR & MCC | B1-DCP-59702 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L+, L- | B1-SWG-59602 | 400V SWITCHGEAR FOR ST #1 FOR BLOCK #1 - B (DC CONTROL-1) | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L+, L- | B159-006AT0005 → B159-006AT0006 → END
B1-DCP-59701 | -P20 | 10 |  | PE-L1-2C4-02 | PE-L1-2C4-02 | ELE-SWG-6005 |  |  | 1 | 1133 | B1-DCP-59701-P2010 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-02 | 0.67 | 220 | D | 30 | SWGR & MCC | B1-DCP-59701 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L+, L- | B1-SWG-59602 | 400V SWITCHGEAR FOR ST #1 FOR BLOCK #1 - B (DC CONTROL-2) | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L+, L- | B159-006BT0005 → B159-006BT0006 → END
B1-DB-59601 | -P20 | 18 |  | PE-L1-3C4-15 | PE-L1-3C4-15 | ELE-SWG-6006 |  |  | 1 | 1134 | B1-DB-59601-P2018 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 2.13 | 230 | N | 40 | SWGR & MCC | B1-DB-59601 | 400V-230V DIST. BOARD FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-SWG-59602 | 400V SWITCHGEAR FOR ST #1 FOR BLOCK #1 - B (AUX. POWER) | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B159-006AT0003 → B159-006AT0019 → B159-006AT0006 → END
B0-DCP-69701 | -P20 | 01 |  | PE-L1-2C10-02 | PE-L1-2C10-02 | ELE-SWG-6007 |  |  | 1 | 1135 | B0-DCP-69701-P2001 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-02 | 5.07 | 220 | D | 50 | SWGR & MCC | B0-DCP-69701 | 220V DC LOCAL DISTRIBUTION PANEL FOR FOR ACC - A | 16_CEP BUILDING W/ACC LER | L+, L- | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A (DC CONTROL-1) | 16_CEP BUILDING W/ACC LER | L+, L- | B169-006BT0054 → B169-006BT0018 → B169-006BT0017 → B169-006BT0016 → END
B0-DCP-69702 | -P20 | 01 |  | PE-L1-2C10-02 | PE-L1-2C10-02 | ELE-SWG-6008 |  |  | 1 | 1136 | B0-DCP-69702-P2001 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-02 | 5.07 | 220 | D | 50 | SWGR & MCC | B0-DCP-69702 | 220V DC LOCAL DISTRIBUTION PANEL FOR FOR ACC - B | 16_CEP BUILDING W/ACC LER | L+, L- | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A (DC CONTROL-2) | 16_CEP BUILDING W/ACC LER | L+, L- | B169-006AT0033 → B169-006AT0018 → B169-006AT0017 → B169-006AT0016 → B169-006AT0015 → END
B1-DB-69603 | -P20 | 15 |  | PE-L1-3C4-15 | PE-L1-3C4-15 | ELE-SWG-6009 |  |  | 1 | 1137 | B1-DB-69603-P2015 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 2.01 | 230 | N | 50 | SWGR & MCC | B1-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A (AUX. POWER) | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0011 → B169-006AT0010 → B169-006AT0009 → B169-006AT0053 → B169-006AT0015 → END
B1-DB-69603 | -P20 | 16 |  | PE-L1-3C4-15 | PE-L1-3C4-15 | ELE-SWG-6009-1 |  |  | 1 | 1138 | B1-DB-69603-P2016 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 2.6 | 230 | N | 50 | SWGR & MCC | B1-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-SWG-69601 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - A (MOTOR SPACE HEATER) | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0011 → B169-006AT0010 → B169-006AT0009 → B169-006AT0053 → B169-006AT0015 → END
B0-DCP-69702 | -P20 | 02 |  | PE-L1-2C4-02 | PE-L1-2C4-02 | ELE-SWG-6010 |  |  | 1 | 1139 | B0-DCP-69702-P2002 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-02 | 1.01 | 220 | D | 30 | SWGR & MCC | B0-DCP-69702 | 220V DC LOCAL DISTRIBUTION PANEL FOR FOR ACC - B | 16_CEP BUILDING W/ACC LER | L+, L- | B1-SWG-69602 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - B (DC CONTROL-1) | 16_CEP BUILDING W/ACC LER | L+, L- | B169-006BT0054 → B169-006BT0018 → END
B0-DCP-69701 | -P20 | 02 |  | PE-L1-2C4-02 | PE-L1-2C4-02 | ELE-SWG-6011 |  |  | 1 | 1140 | B0-DCP-69701-P2002 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-02 | 1.01 | 220 | D | 80 | SWGR & MCC | B0-DCP-69701 | 220V DC LOCAL DISTRIBUTION PANEL FOR FOR ACC - A | 16_CEP BUILDING W/ACC LER | L+, L- | B1-SWG-69602 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - B (DC CONTROL-2) | 16_CEP BUILDING W/ACC LER | L+, L- | B169-006AT0012 → B169-006AT0011 → B169-006AT0010 → B169-006AT0009 → B169-006AT0053 → B169-006AT0016 → B169-006AT0017 → B169-006AT0018 → END
B1-DB-69601 | -P20 | 16 |  | PE-L1-3C4-15 | PE-L1-3C4-15 | ELE-SWG-6012 |  |  | 1 | 1141 | B1-DB-69601-P2016 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 0.74 | 230 | N | 50 | SWGR & MCC | B1-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-SWG-69602 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - B (AUX. POWER) | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0015 → B169-006AT0016 → B169-006AT0017 → B169-006AT0018 → END
B0-DCP-69701 | -P20 | 03 |  | PE-L1-2C10-02 | PE-L1-2C10-02 | ELE-SWG-6013 |  |  | 1 | 1142 | B0-DCP-69701-P2003 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-02 | 5.02 | 220 | D | 70 | SWGR & MCC | B0-DCP-69701 | 220V DC LOCAL DISTRIBUTION PANEL FOR FOR ACC - A | 16_CEP BUILDING W/ACC LER | L+, L- | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C (DC CONTROL-1) | 16_CEP BUILDING W/ACC LER | L+, L- | B169-006BT0054 → B169-006BT0018 → B169-006BT0017 → B169-006BT0016 → B169-006BT0031 → B169-006BT0009 → B169-006BT0010 → END
B0-DCP-69702 | -P20 | 03 |  | PE-L1-2C10-02 | PE-L1-2C10-02 | ELE-SWG-6014 |  |  | 1 | 1143 | B0-DCP-69702-P2003 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-02 | 5.02 | 220 | D | 40 | SWGR & MCC | B0-DCP-69702 | 220V DC LOCAL DISTRIBUTION PANEL FOR FOR ACC - B | 16_CEP BUILDING W/ACC LER | L+, L- | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C (DC CONTROL-2) | 16_CEP BUILDING W/ACC LER | L+, L- | B169-006AT0033 → B169-006AT0012 → B169-006AT0011 → END
B1-DB-69601 | -P20 | 17 |  | PE-L1-3C4-15 | PE-L1-3C4-15 | ELE-SWG-6015 |  |  | 1 | 1144 | B1-DB-69601-P2017 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 2.38 | 230 | N | 50 | SWGR & MCC | B1-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C (AUX. POWER) | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0015 → B169-006AT0053 → B169-006AT0009 → B169-006AT0010 → B169-006AT0011 → END
B1-DB-69601 | -P20 | 18 |  | PE-L1-3C4-15 | PE-L1-3C4-15 | ELE-SWG-6015-1 |  |  | 1 | 1145 | B1-DB-69601-P2018 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 2.8 | 230 | N | 50 | SWGR & MCC | B1-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-SWG-69603 | 400V SWITCHGEAR FOR ACC#1 FOR BLOCK #1 - C (MOTOR SPACE HEATER) | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0015 → B169-006AT0053 → B169-006AT0009 → B169-006AT0010 → B169-006AT0011 → END
B1-DCP-64701 | -P20 | 15 |  | PE-L1-2C6-01 | PE-L1-2C6-01 | ELE-SWG-6016 |  | DONE | 1 | 1146 | B1-DCP-64701-P2015 | 0.6/1kV CU/XLPE/LSZH | 2C x 6sqmm | PE-L1-2C6-01 | 1.59 | 220 | D | 120 | SWGR & MCC | B1-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #1 - A (DC CONTROL-1) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006GT0203 → B164-006GT0002 → B164-006GT0003 → B064-006AC0004 → M0501 → B064-996BT0020 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → B064-016BT0037 → B064-016BT0038 → B064-016BT0249 → B064-016BT0250 → B064-016BT0061 → B064-016BT0062 → B064-016BT0305 → B064-016BT0306 → B064-016BT0307 → B064-016BT0105 → END
B1-DCP-64702 | -P20 | 15 |  | PE-L1-2C10-02 | PE-L1-2C10-02 | ELE-SWG-6017 |  | DONE | 1 | 1147 | B1-DCP-64702-P2015 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-02 | 1.59 | 220 | D | 140 | SWGR & MCC | B1-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #1 - A (DC CONTROL-2) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0204 → B164-006HT0008 → B164-006HT0009 → B164-006HT0010 → B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0004 → M0501 → B064-996AT0020 → B064-016AT0013 → B064-016AT0014 → B064-016AT0015 → B064-016AT0016 → B064-016AT0309 → B064-016AT0245 → B064-016AT0051 → B064-016AT0312 → B064-016AT0072 → B064-016AT0306 → B064-016AT0307 → B064-016AT0097 → END
B1-EDB-64602 | -P20 | 01 | 재배정 | PE-L1-3C4-15 | PE-L1-3C4-06 | ELE-SWG-6018 |  | DONE | 1 | 1148 | B1-EDB-64602-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-06 | 1.83 | 230 | E | 40 | SWGR & MCC | B1-EDB-64602 | 400V-230V EMERGENCY.DIST. BOARD FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #1 - A (AUX. POWER) | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0113 → B064-016AT0308 → B064-016AT0097 → B064-016AT0096 → END
B1-EDB-64602 | -P20 | 02 | 재배정 | PE-L1-3C4-15 | PE-L1-3C4-06 | ELE-SWG-6018-1 |  | DONE | 1 | 1149 | B1-EDB-64602-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-06 | 0.6 | 230 | E | 40 | SWGR & MCC | B1-EDB-64602 | 400V-230V EMERGENCY.DIST. BOARD FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #1 - A (MOTOR SPACE HEATER) | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0113 → B064-016AT0308 → B064-016AT0097 → B064-016AT0096 → END
B1-DCP-64701 | -P20 | 16 | Route 검토중 | PE-L1-2C6-01 | PE-L1-2C6-01 | ELE-SWG-6019 |  | DONE | 1 | 1150 | B1-DCP-64701-P2016 | 0.6/1kV CU/XLPE/LSZH | 2C x 6sqmm | PE-L1-2C6-01 | 1.25 | 220 | D | 130 | SWGR & MCC | B1-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #1 - B (DC CONTROL-1) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006GT0203 → B164-006GT0002 → B164-006GT0003 → B064-006AC0022 → M0501 → B064-996AT0020 → B064-016AT0033 → B064-016AT0034 → B064-016AT0233 → B064-016AT0234 → B064-016AT0048 → B064-016AT0049 → B064-016AT0240 → B064-016AT0290 → B064-016AT0068 → B064-016AT0067 → B064-016AT0277 → B064-016AT0278 → B064-016AT0094 → B064-016AT0296 → B064-016AT0111 → B064-016AT0112 → END | B164-006GT0203 → B164-006GT0002 → B164-006GT0003 → B064-006AC0022 → M0501 → B064-996BT0020 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → B064-016BT0037 → B064-016BT0038 → B064-016BT0249 → B064-016BT0250 → B064-016BT0061 → B064-016BT0062 → B064-016BT0305 → B064-016BT0306 → B064-016BT0307 → B064-016BT0105 → END
B1-DCP-64702 | -P20 | 16 |  | PE-L1-2C6-01 | PE-L1-2C6-01 | ELE-SWG-6020 |  | DONE | 1 | 1151 | B1-DCP-64702-P2016 | 0.6/1kV CU/XLPE/LSZH | 2C x 6sqmm | PE-L1-2C6-01 | 1.25 | 220 | D | 140 | SWGR & MCC | B1-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #1 - B (DC CONTROL-2) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0204 → B164-006HT0008 → B164-006HT0009 → B164-006HT0010 → B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0004 → M0501 → B064-996AT0020 → B064-016AT0013 → B064-016AT0014 → B064-016AT0015 → B064-016AT0016 → B064-016AT0309 → B064-016AT0245 → B064-016AT0051 → B064-016AT0312 → B064-016AT0072 → B064-016AT0306 → B064-016AT0307 → B064-016AT0308 → B064-016AT0113 → END
B1-EDB-64601 | -P20 | 01 | 재배정 | PE-L1-3C4-15 | PE-L1-3C4-06 | ELE-SWG-6021 |  | DONE | 1 | 1152 | B1-EDB-64601-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-06 | 2.13 | 230 | E | 40 | SWGR & MCC | B1-EDB-64601 | 400V-230V EMERGENCY.DIST. BOARD FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #1 - B (AUX. POWER) | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0097 → B064-016AT0308 → B064-016AT0113 → END
B1-EDB-64601 | -P20 | 02 | 재배정 | PE-L1-3C4-15 | PE-L1-3C4-06 | ELE-SWG-6021-1 |  | DONE | 1 | 1153 | B1-EDB-64601-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-06 | 0.6 | 230 | E | 40 | SWGR & MCC | B1-EDB-64601 | 400V-230V EMERGENCY.DIST. BOARD FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #1 - B (MOTOR SPACE HEATER) | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0097 → B064-016AT0308 → B064-016AT0113 → END
B2-DCP-59702 | -P20 | 09 |  | PE-L1-2C4-10 | PE-L1-2C4-10 | ELE-SWG-7001 |  |  | 1 | 1154 | B2-DCP-59702-P2009 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-10 | 1.01 | 220 | D | 40 | SWGR & MCC | B2-DCP-59702 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L+, L- | B2-SWG-59601 | 400V SWITCHGEAR FOR ST #2 FOR BLOCK #2 - A (DC CONTROL-1) | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L+, L- | B259-006AT0005 → B259-006AT0006 → B259-006AT0019 → B259-006AT0003 → END
B2-DCP-59701 | -P20 | 09 |  | PE-L1-2C4-10 | PE-L1-2C4-10 | ELE-SWG-7002 |  |  | 1 | 1155 | B2-DCP-59701-P2009 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-10 | 1.01 | 220 | D | 40 | SWGR & MCC | B2-DCP-59701 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L+, L- | B2-SWG-59601 | 400V SWITCHGEAR FOR ST #2 FOR BLOCK #2 - A (DC CONTROL-2) | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L+, L- | B259-006BT0005 → B259-006BT0006 → B259-006BT0019 → B259-006BT0003 → END
B2-DB-59602 | -P20 | 06 | 재배정 | PE-L1-3C4-05 | PE-L1-3C4-17 | ELE-SWG-7003 |  |  | 1 | 1156 | B2-DB-59602-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-17 | 1.83 | 230 | N | 40 | SWGR & MCC | B2-DB-59602 | 400V-230V DIST. BOARD FOR ST #2 FOR BLOCK #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B2-SWG-59601 | 400V SWITCHGEAR FOR ST #2 FOR BLOCK #2 - A (AUX. POWER) | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B259-006AT0005 → B259-006AT0006 → B259-006AT0019 → B259-006AT0003 → END
B2-DCP-59702 | -P20 | 10 |  | PE-L1-2C4-02 | PE-L1-2C4-02 | ELE-SWG-7004 |  |  | 1 | 1157 | B2-DCP-59702-P2010 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-02 | 0.67 | 220 | D | 20 | SWGR & MCC | B2-DCP-59702 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L+, L- | B2-SWG-59602 | 400V SWITCHGEAR FOR ST #2 FOR BLOCK #2 - B (DC CONTROL-1) | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L+, L- | B259-006AT0005 → B259-006AT0006 → END
B2-DCP-59701 | -P20 | 10 |  | PE-L1-2C4-06 | PE-L1-2C4-06 | ELE-SWG-7005 |  |  | 1 | 1158 | B2-DCP-59701-P2010 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-06 | 0.67 | 220 | D | 20 | SWGR & MCC | B2-DCP-59701 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L+, L- | B2-SWG-59602 | 400V SWITCHGEAR FOR ST #2 FOR BLOCK #2 - B (DC CONTROL-2) | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L+, L- | B259-006BT0005 → B259-006BT0006 → END
B2-DB-59601 | -P20 | 18 | 재배정 | PE-L1-3C4-05 | PE-L1-3C4-17 | ELE-SWG-7006 |  |  | 1 | 1159 | B2-DB-59601-P2018 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-17 | 2.13 | 230 | N | 30 | SWGR & MCC | B2-DB-59601 | 400V-230V DIST. BOARD FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B2-SWG-59602 | 400V SWITCHGEAR FOR ST #2 FOR BLOCK #2 - B (AUX. POWER) | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B259-006AT0003 → B259-006AT0019 → END
B0-DCP-69702 | -P20 | 04 |  | PE-L1-2C10-02 | PE-L1-2C10-02 | ELE-SWG-7007 |  |  | 1 | 1160 | B0-DCP-69702-P2004 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-02 | 5.07 | 220 | D | 70 | SWGR & MCC | B0-DCP-69702 | 220V DC LOCAL DISTRIBUTION PANEL FOR FOR ACC - B | 16_CEP BUILDING W/ACC LER | L+, L- | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A (DC CONTROL-1) | 16_CEP BUILDING W/ACC LER | L+, L- | B169-007AT0005 → B169-007AT0006 → B169-007AT0007 → B169-007AT0039 → B169-007AT0028 → B169-007AT0027 → END
B0-DCP-69701 | -P20 | 04 |  | PE-L1-2C10-02 | PE-L1-2C10-02 | ELE-SWG-7008 |  |  | 1 | 1161 | B0-DCP-69701-P2004 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-02 | 5.07 | 220 | D | 30 | SWGR & MCC | B0-DCP-69701 | 220V DC LOCAL DISTRIBUTION PANEL FOR FOR ACC - A | 16_CEP BUILDING W/ACC LER | L+, L- | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A (DC CONTROL-2) | 16_CEP BUILDING W/ACC LER | L+, L- | B169-006AT0033 → B169-006AT0020 → END
B2-DB-69603 | -P20 | 15 | 재배정 | PE-L1-3C4-05 | PE-L1-3C4-17 | ELE-SWG-7009 |  |  | 1 | 1162 | B2-DB-69603-P2015 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-17 | 2.01 | 230 | N | 50 | SWGR & MCC | B2-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A (AUX. POWER) | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0014 → B169-006AT0013 → B169-006AT0033 → B169-006AT0019 → END
B2-DB-69603 | -P20 | 16 | 재배정 | PE-L1-3C4-05 | PE-L1-3C4-17 | ELE-SWG-7009-1 |  |  | 1 | 1163 | B2-DB-69603-P2016 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-17 | 2.6 | 230 | N | 50 | SWGR & MCC | B2-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-SWG-69601 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - A (MOTOR SPACE HEATER) | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0014 → B169-006AT0013 → B169-006AT0033 → B169-006AT0019 → END
B0-DCP-69701 | -P20 | 05 |  | PE-L1-2C4-02 | PE-L1-2C4-02 | ELE-SWG-7010 |  |  | 1 | 1164 | B0-DCP-69701-P2005 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-02 | 1.01 | 220 | D | 60 | SWGR & MCC | B0-DCP-69701 | 220V DC LOCAL DISTRIBUTION PANEL FOR FOR ACC - A | 16_CEP BUILDING W/ACC LER | L+, L- | B2-SWG-69602 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - B (DC CONTROL-1) | 16_CEP BUILDING W/ACC LER | L+, L- | B169-007AT0005 → B169-007AT0006 → B169-007AT0007 → B169-007AT0039 → B169-007AT0028 → END
B0-DCP-69702 | -P20 | 05 |  | PE-L1-2C4-02 | PE-L1-2C4-02 | ELE-SWG-7011 |  |  | 1 | 1165 | B0-DCP-69702-P2005 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-02 | 1.01 | 220 | D | 80 | SWGR & MCC | B0-DCP-69702 | 220V DC LOCAL DISTRIBUTION PANEL FOR FOR ACC - B | 16_CEP BUILDING W/ACC LER | L+, L- | B2-SWG-69602 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - B (DC CONTROL-2) | 16_CEP BUILDING W/ACC LER | L+, L- | B169-006AT0018 → B169-006AT0017 → B169-006AT0016 → B169-006AT0053 → B169-006AT0009 → B169-006AT0010 → B169-006AT0011 → B169-006AT0012 → END
B2-DB-69601 | -P20 | 16 | 재배정 | PE-L1-3C4-10 | PE-L1-3C4-15 | ELE-SWG-7012 |  |  | 1 | 1166 | B2-DB-69601-P2016 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 0.74 | 230 | N | 40 | SWGR & MCC | B2-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-SWG-69602 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - B (AUX. POWER) | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0019 → B169-006AT0020 → B169-006AT0021 → END
B0-DCP-69702 | -P20 | 06 |  | PE-L1-2C10-02 | PE-L1-2C10-02 | ELE-SWG-7013 |  |  | 1 | 1167 | B0-DCP-69702-P2006 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-02 | 5.02 | 220 | D | 40 | SWGR & MCC | B0-DCP-69702 | 220V DC LOCAL DISTRIBUTION PANEL FOR FOR ACC - B | 16_CEP BUILDING W/ACC LER | L+, L- | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C (DC CONTROL-1) | 16_CEP BUILDING W/ACC LER | L+, L- | B169-007AT0005 → B169-007AT0006 → B169-007AT0007 → END
B0-DCP-69701 | -P20 | 06 |  | PE-L1-2C10-02 | PE-L1-2C10-02 | ELE-SWG-7014 |  |  | 1 | 1168 | B0-DCP-69701-P2006 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-02 | 5.02 | 220 | D | 40 | SWGR & MCC | B0-DCP-69701 | 220V DC LOCAL DISTRIBUTION PANEL FOR FOR ACC - A | 16_CEP BUILDING W/ACC LER | L+, L- | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C (DC CONTROL-2) | 16_CEP BUILDING W/ACC LER | L+, L- | B169-006AT0033 → B169-006AT0013 → B169-006AT0014 → END
B2-DB-69601 | -P20 | 17 |  | PE-L1-3C4-10 | PE-L1-3C4-10 | ELE-SWG-7015 |  |  | 1 | 1169 | B2-DB-69601-P2017 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-10 | 2.38 | 230 | N | 50 | SWGR & MCC | B2-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C (AUX. POWER) | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0019 → B169-006AT0033 → B169-006AT0013 → B169-006AT0014 → END
B2-DB-69601 | -P20 | 18 |  | PE-L1-3C4-10 | PE-L1-3C4-10 | ELE-SWG-7015-1 |  |  | 1 | 1170 | B2-DB-69601-P2018 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-10 | 2.8 | 230 | N | 50 | SWGR & MCC | B2-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-SWG-69603 | 400V SWITCHGEAR FOR ACC#2 FOR BLOCK #2 - C (MOTOR SPACE HEATER) | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0019 → B169-006AT0033 → B169-006AT0013 → B169-006AT0014 → END
B2-DCP-64701 | -P20 | 15 |  | PE-L1-2C4-10 | PE-L1-2C4-10 | ELE-SWG-7016 |  |  | 1 | 1171 | B2-DCP-64701-P2015 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-10 | 1.59 | 220 | D | 80 | SWGR & MCC | B2-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #2 - A (DC CONTROL-1) | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-017ET0063 → B264-017ET0248 → B264-017ET0060 → B264-006AC0001 → M0405 → B264-996AT0011 → B264-016AT0015 → B264-016AT0234 → B264-016AT0030 → END
B2-DCP-64702 | -P20 | 15 |  | PE-L1-2C4-10 | PE-L1-2C4-10 | ELE-SWG-7017 |  |  | 1 | 1172 | B2-DCP-64702-P2015 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-10 | 1.59 | 220 | D | 90 | SWGR & MCC | B2-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #2 - A (DC CONTROL-2) | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-016ET0063 → B264-016ET0248 → B264-016ET0060 → B264-006AC0003 → M0405 → B264-996CT0009 → B264-016BT0014 → B264-016BT0015 → B264-013BT0234 → B264-016BT0030 → END
B2-EDB-64602 | -P20 | 01 |  | PE-L1-3C4-25 | PE-L1-3C4-25 | ELE-SWG-7018 |  |  | 1 | 1173 | B2-EDB-64602-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-25 | 1.72 | 230 | E | 40 | SWGR & MCC | B2-EDB-64602 | 400V-230V EMERGENCY.DIST. BOARD FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #2 - A (AUX. POWER) | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016CT0049 → B264-016CT0238 → B264-016CT0030 → END
B2-EDB-64602 | -P20 | 02 |  | PE-L1-3C4-25 | PE-L1-3C4-25 | ELE-SWG-7018-1 |  |  | 1 | 1174 | B2-EDB-64602-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-25 | 0.4 | 230 | E | 40 | SWGR & MCC | B2-EDB-64602 | 400V-230V EMERGENCY.DIST. BOARD FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #2 - A (MOTOR SPACE HEATER) | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016CT0049 → B264-016CT0238 → B264-016CT0030 → END
B2-DCP-64701 | -P20 | 16 |  | PE-L1-2C4-05 | PE-L1-2C4-05 | ELE-SWG-7019 |  |  | 1 | 1175 | B2-DCP-64701-P2016 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-05 | 1.25 | 220 | D | 80 | SWGR & MCC | B2-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #2 - B (DC CONTROL-1) | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-017ET0063 → B264-017ET0248 → B264-017ET0060 → B264-006AC0001 → M0405 → B264-996AT0011 → B264-016AT0015 → B264-016AT0234 → B264-016AT0235 → B264-016AT0049 → END
B2-DCP-64702 | -P20 | 16 |  | PE-L1-2C4-10 | PE-L1-2C4-10 | ELE-SWG-7020 |  |  | 1 | 1176 | B2-DCP-64702-P2016 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-10 | 1.25 | 220 | D | 90 | SWGR & MCC | B2-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #2 - B (DC CONTROL-2) | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-016ET0063 → B264-016ET0248 → B264-016ET0060 → B264-006AC0003 → M0405 → B264-996CT0009 → B264-016BT0014 → B264-016BT0015 → B264-013BT0234 → B264-013BT0235 → B264-016BT0049 → END
B2-EDB-64601 | -P20 | 01 |  | PE-L1-3C4-25 | PE-L1-3C4-25 | ELE-SWG-7021 |  |  | 1 | 1177 | B2-EDB-64601-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-25 | 2.02 | 230 | E | 40 | SWGR & MCC | B2-EDB-64601 | 400V-230V EMERGENCY.DIST. BOARD FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #2 - B (AUX. POWER) | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016CT0030 → B264-016CT0238 → B264-016CT0049 → END
B2-EDB-64601 | -P20 | 02 |  | PE-L1-3C4-25 | PE-L1-3C4-25 | ELE-SWG-7021-1 |  |  | 1 | 1178 | B2-EDB-64601-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-25 | 0.4 | 230 | E | 40 | SWGR & MCC | B2-EDB-64601 | 400V-230V EMERGENCY.DIST. BOARD FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #2 - B (MOTOR SPACE HEATER) | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016CT0030 → B264-016CT0238 → B264-016CT0049 → END
B0-DCP-64701 | -P20 | 02 |  | PE-L1-2C10-01 | PE-L1-2C10-01 | ELE-SWG-0001 |  | DONE | 1 | 1179 | B0-DCP-64701-P2002 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-01 | 4.082 | 220 | D | 70 | SWGR & MCC | B0-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B0-SWG-64301 | 10KV SWITCHGEAR FOR COMMON - A (DC CONTROL-1) | 1.2_LEB FOR BLOCK #1 | L+, L- | B064-006FT0207 → B064-006FT0005 → B064-006AC0020 → M0501 → B064-996AT0020 → B064-016AT0032 → B064-016AT0213 → B064-016AT0045 → B064-016AT0046 → END
B0-DCP-64702 | -P20 | 02 |  | PE-L1-2C10-01 | PE-L1-2C10-01 | ELE-SWG-0002 |  | DONE | 1 | 1180 | B0-DCP-64702-P2002 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-01 | 4.082 | 220 | D | 80 | SWGR & MCC | B0-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B0-SWG-64301 | 10KV SWITCHGEAR FOR COMMON - A (DC CONTROL-2) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0020 → M0501 → B064-996AT0020 → B064-016AT0013 → B064-016AT0232 → B064-016AT0233 → B064-016AT0234 → B064-016AT0047 → B064-016AT0046 → END | B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0020 → M0501 → B064-996GT0020 → B064-016GT0033 → B064-016GT0229 → B064-016GT0230 → END → B064-016AT0046 → END
B0-DB-64602 | -P20 | 03 |  | PE-L1-3C4-15 | PE-L1-3C4-15 | ELE-SWG-0003 |  | DONE | 1 | 1181 | B0-DB-64602-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 3.58 | 230 | N | 40 | SWGR & MCC | B0-DB-64602 | 400V-230V DIST. BOARD FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-SWG-64301 | 10KV SWITCHGEAR FOR COMMON - A (AUX. POWER) | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0032 → B064-016AT0213 → B064-016AT0045 → B064-016AT0046 → END
B0-DCP-64701 | -P20 | 03 |  | PE-L1-2C10-01 | PE-L1-2C10-01 | ELE-SWG-0004 |  | DONE | 1 | 1182 | B0-DCP-64701-P2003 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-01 | 4.082 | 220 | D | 90 | SWGR & MCC | B0-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B0-SWG-64302 | 10KV SWITCHGEAR FOR COMMON - B (DC CONTROL-1) | 1.2_LEB FOR BLOCK #1 | L+, L- | B064-006FT0207 → B064-006FT0005 → B064-006AC0021 → M0501 → B064-996AT0020 → B064-016AT0032 → B064-016AT0213 → B064-016AT0045 → B064-016AT0046 → B064-016AT0047 → B064-016AT0048 → B064-016AT0049 → B064-016AT0050 → END | B064-006FT0207 → B064-006FT0005 → B064-006AC0021 → M0501 → B064-996GT0020 → B064-016GT0033 → B064-016GT0229 → B064-016GT0230 → B064-016GT0047 → B064-016GT0048 → END
B0-DCP-64702 | -P20 | 03 |  | PE-L1-2C10-01 | PE-L1-2C10-01 | ELE-SWG-0005 |  | DONE | 1 | 1183 | B0-DCP-64702-P2003 | 0.6/1kV CU/XLPE/LSZH | 2C x 10sqmm | PE-L1-2C10-01 | 4.082 | 220 | D | 70 | SWGR & MCC | B0-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B0-SWG-64302 | 10KV SWITCHGEAR FOR COMMON - B (DC CONTROL-2) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0021 → M0501 → B064-996AT0020 → B064-016AT0013 → B064-016AT0232 → B064-016AT0233 → B064-016AT0234 → B064-016AT0048 → B064-016AT0049 → END
B0-DB-64601 | -P20 | 02 |  | PE-L1-3C6-01 | PE-L1-3C6-01 | ELE-SWG-0006 |  | DONE | 1 | 1184 | B0-DB-64601-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 6sqmm | PE-L1-3C6-01 | 3.28 | 230 | N | 50 | SWGR & MCC | B0-DB-64601 | 400V-230V DIST. BOARD FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-SWG-64302 | 10KV SWITCHGEAR FOR COMMON - B (AUX. POWER) | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0012 → B064-016AT0013 → B064-016AT0232 → B064-016AT0233 → B064-016AT0234 → B064-016AT0048 → B064-016AT0049 → END
B0-DCP-64701 | -P20 | 04 |  | PE-L1-2C6-01 | PE-L1-2C6-01 | ELE-SWG-0006-001 |  | DONE | 1 | 1185 | B0-DCP-64701-P2004 | 0.6/1kV CU/XLPE/LSZH | 2C x 6sqmm | PE-L1-2C6-01 | 1.61 | 220 | D | 100 | SWGR & MCC | B0-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B0-SWG-64303 | 10KV SWITCHGEAR FOR BACK UP - A (DC CONTROL-1) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006JT0209 → B164-006JT0006 → B064-006AC0021 → M0501 → B064-996BT0019 → B064-016BT0013 → B064-016BT0014 → B064-016BT0015 → B064-016BT0016 → B064-016BT0309 → B064-016BT0038 → B064-016BT0249 → B064-016BT0250 → B064-016BT0061 → B064-016BT0062 → B064-016BT0305 → END
B0-DCP-64702 | -P20 | 04 |  | PE-L1-2C6-01 | PE-L1-2C6-01 | ELE-SWG-0006-002 |  | DONE | 1 | 1186 | B0-DCP-64702-P2004 | 0.6/1kV CU/XLPE/LSZH | 2C x 6sqmm | PE-L1-2C6-01 | 1.61 | 220 | D | 100 | SWGR & MCC | B0-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B0-SWG-64303 | 10KV SWITCHGEAR FOR BACK UP - A (DC CONTROL-2) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0022 → M0501 → B064-996AT0020 → B064-016AT0013 → B064-016AT0232 → B064-016AT0233 → B064-016AT0234 → B064-016AT0048 → B064-016AT0049 → B064-016AT0050 → B064-016AT0051 → B064-016AT0312 → B064-016AT0072 → END
B0-DB-64602 | -P20 | 04 |  | PE-L1-3C4-15 | PE-L1-3C4-15 | ELE-SWG-0006-003 |  | DONE | 1 | 1187 | B0-DB-64602-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 1.23 | 230 | N | 90 | SWGR & MCC | B0-DB-64602 | 400V-230V DIST. BOARD FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-SWG-64303 | 10KV SWITCHGEAR FOR BACK UP - A (AUX. POWER) | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0032 → B064-016AT0213 → B064-016AT0214 → B064-016AT0063 → B064-016AT0064 → B064-016AT0065 → B064-016AT0066 → B064-016AT0067 → B064-016AT0068 → B064-016AT0069 → B064-016AT0070 → B064-016AT0071 → B064-016AT0072 → END
B0-DCP-64701 | -P20 | 05 |  | PE-L1-2C6-01 | PE-L1-2C6-01 | ELE-SWG-0006-004 |  | DONE | 1 | 1188 | B0-DCP-64701-P2005 | 0.6/1kV CU/XLPE/LSZH | 2C x 6sqmm | PE-L1-2C6-01 | 1.61 | 220 | D | 100 | SWGR & MCC | B0-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B0-SWG-64304 | 10KV SWITCHGEAR FOR BACK UP - B (DC CONTROL-1) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006JT0209 → B164-006JT0006 → B064-006AC0021 → M0501 → B064-996BT0019 → B064-016BT0013 → B064-016BT0014 → B064-016BT0015 → B064-016BT0016 → B064-016BT0309 → B064-016BT0038 → B064-016BT0249 → B064-016BT0250 → B064-016BT0061 → B064-016BT0062 → B064-016BT0305 → B064-016BT0306 → END
B0-DCP-64702 | -P20 | 05 |  | PE-L1-2C6-01 | PE-L1-2C6-01 | ELE-SWG-0006-005 |  | DONE | 1 | 1189 | B0-DCP-64702-P2005 | 0.6/1kV CU/XLPE/LSZH | 2C x 6sqmm | PE-L1-2C6-01 | 1.61 | 220 | D | 120 | SWGR & MCC | B0-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B0-SWG-64304 | 10KV SWITCHGEAR FOR BACK UP - B (DC CONTROL-2) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0022 → M0501 → B064-996AT0020 → B064-016AT0013 → B064-016AT0232 → B064-016AT0233 → B064-016AT0234 → B064-016AT0048 → B064-016AT0049 → B064-016AT0050 → B064-016AT0051 → B064-016AT0312 → B064-016AT0072 → B064-016AT0306 → B064-016AT0082 → B064-016AT0081 → END
B0-DB-64601 | -P20 | 03 |  | PE-L1-3C4-15 | PE-L1-3C4-15 | ELE-SWG-0006-006 |  | DONE | 1 | 1190 | B0-DB-64601-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 1.23 | 230 | N | 100 | SWGR & MCC | B0-DB-64601 | 400V-230V DIST. BOARD FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-SWG-64304 | 10KV SWITCHGEAR FOR BACK UP - B (AUX. POWER) | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0012 → B064-016AT0013 → B064-016AT0232 → B064-016AT0233 → B064-016AT0234 → B064-016AT0048 → B064-016AT0049 → B064-016AT0050 → B064-016AT0051 → B064-016AT0312 → B064-016AT0072 → B064-016AT0306 → B064-016AT0082 → B064-016AT0081 → END
B0-DCP-64701 | -P20 | 06 |  | PE-L1-2C4-03 | PE-L1-2C4-03 | ELE-SWG-0007 |  | DONE | 1 | 1191 | B0-DCP-64701-P2006 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-03 | 0.17 | 220 | D | 50 | SWGR & MCC | B0-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B0-ATS-64701 | HSBT - 10KV SWGR FOR COMMON - A (DC CONTROL-1) | 1.2_LEB FOR BLOCK #1 | L+, L- | B064-006FT0207 → B064-006FT0005 → B064-006AC0018 → M0501 → B064-996AT0020 → B064-016AT0033 → B064-016AT0034 → B064-016AT0233 → END | B064-006FT0207 → B064-006FT0005 → B064-006AC0018 → M0501 → B064-996GT0020 → B064-016GT0033 → B064-016GT0229 → B064-016GT0230 → B064-016GT0047 → END
B0-DCP-64702 | -P20 | 06 |  | PE-L1-2C4-03 | PE-L1-2C4-03 | ELE-SWG-0008 |  | DONE | 1 | 1192 | B0-DCP-64702-P2006 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-03 | 0.17 | 220 | D | 60 | SWGR & MCC | B0-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B0-ATS-64701 | HSBT - 10KV SWGR FOR COMMON - A (DC CONTROL-2) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0009 → M0501 → B064-996AT0020 → B064-016AT0013 → B064-016AT0232 → B064-016AT0233 → END
B0-DB-64601 | -P20 | 04 |  | PE-L1-3C4-15 | PE-L1-3C4-15 | ELE-SWG-0009 |  | DONE | 1 | 1193 | B0-DB-64601-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 0.1 | 230 | N | 40 | SWGR & MCC | B0-DB-64601 | 400V-230V DIST. BOARD FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-ATS-64701 | HSBT - 10KV SWGR FOR COMMON - A (AUX. POWER) | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0012 → B064-016AT0013 → B064-016AT0232 → B064-016AT0233 → END
B0-DCP-64701 | -P20 | 07 |  | PE-L1-2C4-03 | PE-L1-2C4-03 | ELE-SWG-00009-001 |  | DONE | 1 | 1194 | B0-DCP-64701-P2007 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-03 | 0.17 | 220 | D | 50 | SWGR & MCC | B0-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B0-ATS-64702 | HSBT - 10KV SWGR FOR COMMON - B (DC CONTROL-1) | 1.2_LEB FOR BLOCK #1 | L+, L- | B064-006FT0207 → B064-006FT0005 → B064-006AC0019 → M0501 → B064-996AT0020 → B064-016AT0033 → B064-016AT0034 → B064-016AT0233 → END | B064-006FT0207 → B064-006FT0005 → B064-006AC0019 → M0501 → B064-996GT0020 → B064-016GT0033 → B064-016GT0229 → B064-016GT0230 → B064-016GT0047 → END
B0-DCP-64702 | -P20 | 07 |  | PE-L1-2C4-03 | PE-L1-2C4-03 | ELE-SWG-00009-002 |  | DONE | 1 | 1195 | B0-DCP-64702-P2007 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-03 | 0.17 | 220 | D | 60 | SWGR & MCC | B0-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B0-ATS-64702 | HSBT - 10KV SWGR FOR COMMON - B (DC CONTROL-2) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0009 → M0501 → B064-996AT0020 → B064-016AT0013 → B064-016AT0232 → B064-016AT0233 → END
B0-DB-64602 | -P20 | 05 |  | PE-L1-3C4-15 | PE-L1-3C4-15 | ELE-SWG-00009-003 |  | DONE | 1 | 1196 | B0-DB-64602-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 0.1 | 230 | N | 40 | SWGR & MCC | B0-DB-64602 | 400V-230V DIST. BOARD FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-ATS-64702 | HSBT - 10KV SWGR FOR COMMON - B (AUX. POWER) | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0032 → B064-016AT0033 → B064-016AT0034 → B064-016AT0233 → END
B0-DCP-64701 | -P20 | 08 |  | PE-L1-2C4-03 | PE-L1-2C4-03 | ELE-SWG-0010 |  | DONE | 1 | 1197 | B0-DCP-64701-P2008 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-03 | 1.3 | 220 | D | 40 | SWGR & MCC | B0-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B0-SWG-64601 | 400V SWITCHGEAR FOR COMMON - A (DC CONTROL-1) | 1.2_LEB FOR BLOCK #1 | L+, L- | B064-006FT0207 → B064-006FT0005 → B064-006AC0018 → M0501 → B064-996BT0019 → B064-016BT0013 → END
B0-DCP-64702 | -P20 | 08 |  | PE-L1-2C4-03 | PE-L1-2C4-03 | ELE-SWG-0011 |  | DONE | 1 | 1198 | B0-DCP-64702-P2008 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-03 | 1.3 | 220 | D | 50 | SWGR & MCC | B0-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B0-SWG-64601 | 400V SWITCHGEAR FOR COMMON - A (DC CONTROL-2) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0022 → M0501 → B064-996AT0020 → B064-016AT0013 → END
B0-DB-64602 | -P20 | 06 |  | PE-L1-3C4-15 | PE-L1-3C4-15 | ELE-SWG-0012 |  | DONE | 1 | 1199 | B0-DB-64602-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 2.12 | 230 | N | 50 | SWGR & MCC | B0-DB-64602 | 400V-230V DIST. BOARD FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-SWG-64601 | 400V SWITCHGEAR FOR COMMON - A (AUX. POWER) | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0032 → B064-016AT0212 → B064-016AT0011 → B064-016AT0012 → B064-016AT0013 → END
B0-DB-64602 | -P20 | 07 |  | PE-L1-3C4-15 | PE-L1-3C4-15 | ELE-SWG-0012-2 |  | DONE | 1 | 1200 | B0-DB-64602-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 0.4 | 230 | N | 50 | SWGR & MCC | B0-DB-64602 | 400V-230V DIST. BOARD FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-SWG-64601 | 400V SWITCHGEAR FOR COMMON - A (MOTOR SPACE HEATER) | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0032 → B064-016AT0212 → B064-016AT0011 → B064-016AT0012 → B064-016AT0013 → END
B0-DCP-64701 | -P20 | 09 |  | PE-L1-2C4-03 | PE-L1-2C4-03 | ELE-SWG-0013 |  | DONE | 1 | 1201 | B0-DCP-64701-P2009 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-03 | 0.96 | 220 | D | 40 | SWGR & MCC | B0-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B0-SWG-64602 | 400V SWITCHGEAR FOR COMMON - B (DC CONTROL-1) | 1.2_LEB FOR BLOCK #1 | L+, L- | B064-006FT0207 → B064-006FT0005 → B064-006AC0019 → M0501 → B064-996BT0020 → B064-016BT0033 → END
B0-DCP-64702 | -P20 | 09 |  | PE-L1-2C4-03 | PE-L1-2C4-03 | ELE-SWG-0014 |  | DONE | 1 | 1202 | B0-DCP-64702-P2009 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-03 | 0.96 | 220 | D | 60 | SWGR & MCC | B0-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B0-SWG-64602 | 400V SWITCHGEAR FOR COMMON - B (DC CONTROL-2) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0022 → M0501 → B064-996AT0020 → B064-016AT0012 → B064-016AT0011 → B064-016AT0212 → B064-016AT0032 → END
B0-DB-64601 | -P20 | 05 |  | PE-L1-3C4-15 | PE-L1-3C4-15 | ELE-SWG-0015 |  | DONE | 1 | 1203 | B0-DB-64601-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 2.38 | 230 | N | 40 | SWGR & MCC | B0-DB-64601 | 400V-230V DIST. BOARD FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-SWG-64602 | 400V SWITCHGEAR FOR COMMON - B (AUX. POWER) | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0012 → B064-016AT0013 → B064-016AT0232 → B064-016AT0034 → END
B0-DB-64601 | -P20 | 06 |  | PE-L1-3C4-15 | PE-L1-3C4-15 | ELE-SWG-0015-2 |  | DONE | 1 | 1204 | B0-DB-64601-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 0.4 | 230 | N | 40 | SWGR & MCC | B0-DB-64601 | 400V-230V DIST. BOARD FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-SWG-64602 | 400V SWITCHGEAR FOR COMMON - B (MOTOR SPACE HEATER) | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0012 → B064-016AT0013 → B064-016AT0232 → B064-016AT0034 → END
B0-DCP-64701 | -P20 | 10 |  | PE-L1-2C4-03 | PE-L1-2C4-03 | ELE-SWG-0016 |  | DONE | 1 | 1205 | B0-DCP-64701-P2010 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-03 | 1.3 | 220 | D | 50 | SWGR & MCC | B0-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B0-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR COMMON - A (DC CONTROL-1) | 1.2_LEB FOR BLOCK #1 | L+, L- | B064-006FT0207 → B064-006FT0005 → B064-006AC0018 → M0501 → B064-996BT0019 → B064-016BT0013 → B064-016BT0014 → END
B0-DCP-64702 | -P20 | 10 |  | PE-L1-2C4-03 | PE-L1-2C4-03 | ELE-SWG-0017 |  | DONE | 1 | 1206 | B0-DCP-64702-P2010 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-03 | 1.3 | 220 | D | 60 | SWGR & MCC | B0-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B0-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR COMMON - A (DC CONTROL-2) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0004 → M0501 → B064-996AT0020 → B064-016AT0013 → B064-016AT0014 → B064-016AT0015 → END
B0-EDB-64602 | -P20 | 01 |  | PE-L1-3C4-15 | PE-L1-3C4-15 | ELE-SWG-0018 |  | DONE | 1 | 1207 | B0-EDB-64602-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 1.72 | 230 | E | 40 | SWGR & MCC | B0-EDB-64602 | 400V-230V EMERGENCY.DIST. BOARD FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR COMMON - A (AUX. POWER) | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0037 → B064-016AT0309 → B064-016AT0016 → B064-016AT0015 → END
B0-DCP-64701 | -P20 | 11 |  | PE-L1-2C4-03 | PE-L1-2C4-03 | ELE-SWG-0019 |  | DONE | 1 | 1208 | B0-DCP-64701-P2011 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-03 | 0.96 | 220 | D | 60 | SWGR & MCC | B0-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B0-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR COMMON - B (DC CONTROL-1) | 1.2_LEB FOR BLOCK #1 | L+, L- | B064-006FT0207 → B064-006FT0005 → B064-006AC0019 → M0501 → B064-996BT0020 → B064-016BT0033 → B064-016BT0034 → B064-016BT0035 → B064-016BT0036 → END
B0-DCP-64702 | -P20 | 11 |  | PE-L1-2C4-03 | PE-L1-2C4-03 | ELE-SWG-0020 |  | DONE | 1 | 1209 | B0-DCP-64702-P2011 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-03 | 0.96 | 220 | D | 70 | SWGR & MCC | B0-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B0-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR COMMON - B (DC CONTROL-2) | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0004 → M0501 → B064-996AT0020 → B064-016AT0013 → B064-016AT0232 → B064-016AT0035 → B064-016AT0036 → END
B0-EDB-64601 | -P20 | 01 |  | PE-L1-3C4-15 | PE-L1-3C4-15 | ELE-SWG-0021 |  | DONE | 1 | 1210 | B0-EDB-64601-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 1.98 | 230 | E | 40 | SWGR & MCC | B0-EDB-64601 | 400V-230V EMERGENCY.DIST. BOARD FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR COMMON - B (AUX. POWER) | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0016 → B064-016AT0309 → B064-016AT0037 → B064-016AT0036 → B064-016AT0035 → END
B0-DCP-64701 | -P20 | 12 |  | PE-L1-2C16-01 | PE-L1-2C16-01 | ELE-SWG-0022 |  |  | 1 | 1211 | B0-DCP-64701-P2012 | 0.6/1kV CU/XLPE/LSZH | 2C x 16sqmm | PE-L1-2C16-01 | 1.3 | 220 | D | 530 | SWGR & MCC | B0-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B0-SWG-49601 | 400V SWITCHGEAR FOR WATER TREATMENT - A (DC CONTROL-1) | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L+, L- | B064-006FT0207 → B064-006FT0005 → B064-006AC0006 → M0501 → D0503-L44 → M0502 → D0504-L44 → M0503 → D0501-L44 → M0328 → D0324-L44 → M0329 → B114-997AT0021 → B114-017AT0020 → B114-017AT0025 → B025-017ET0042 → B025-017ET0041 → B025-017ET0040 → B025-017ET0016 → B025-017ET0039 → B025-017ET0038 → B025-017ET0036 → B025-017ET0035 → B025-017ET0033 → B025-017ET0032 → B025-017ET0031 → B025-017ET0030 → B025-017ET0021 → B025-017ET0022 → B025-997ET0004 → M0205 → D0205-L23 → M0206 → D0203-L15 → M0207 → D0204-L17 → B049-006AT0002 → B049-006AT0003 → END
B0-DCP-64702 | -P20 | 12 |  | PE-L1-2C16-01 | PE-L1-2C16-01 | ELE-SWG-0023 |  |  | 1 | 1212 | B0-DCP-64702-P2012 | 0.6/1kV CU/XLPE/LSZH | 2C x 16sqmm | PE-L1-2C16-01 | 1.3 | 220 | D | 520 | SWGR & MCC | B0-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B0-SWG-49601 | 400V SWITCHGEAR FOR WATER TREATMENT - A (DC CONTROL-1) | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L+, L- | B164-006JT0209 → B164-006JT0006 → B064-006AC0007 → M0501 → D0503-L43 → M0502 → D0504-L43 → M0503 → D0501-L43 → M0328 → D0324-L43 → M0329 → B114-996AT0021 → B114-016AT0020 → B114-016AT0025 → B025-016FT0042 → B025-016FT0041 → B025-016FT0040 → B025-996FT0016 → B025-016FT0039 → B025-016FT0038 → B025-016FT0036 → B025-016FT0035 → B025-016FT0033 → B025-016FT0032 → B025-016FT0031 → B025-016FT0030 → B025-016FT0028 → B025-016FT0029 → B025-996FT0005 → M0205 → D0205-L15 → M0206 → D0203-L15 → M0207 → D0204-L18 → B049-006BT0001 → B049-006BT0003 → END
B0-DB-49602 | -P20 | 02 |  | PE-L1-3C4-15 | PE-L1-3C4-15 | ELE-SWG-0024 |  |  | 1 | 1213 | B0-DB-49602-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 2.13 | 230 | N | 40 | SWGR & MCC | B0-DB-49602 | 400V-230V DIST. BOARD FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, N, PE | B0-SWG-49601 | 400V SWITCHGEAR FOR WATER TREATMENT - A (AUX. POWER) | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, N, PE | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0004 → END
B0-DB-49602 | -P20 | 03 |  | PE-L1-3C4-15 | PE-L1-3C4-15 | ELE-SWG-0024-1 |  |  | 1 | 1214 | B0-DB-49602-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 0.83 | 230 | N | 40 | SWGR & MCC | B0-DB-49602 | 400V-230V DIST. BOARD FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, N, PE | B0-SWG-49601 | 400V SWITCHGEAR FOR WATER TREATMENT - A (MOTOR SPACE HEATER) | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, N, PE | B049-006BT0008 → B049-006BT0009 → B049-006BT0014 → B049-006BT0004 → END
B0-DCP-64702 | -P20 | 13 |  | PE-L1-2C16-02 | PE-L1-2C16-02 | ELE-SWG-0025 |  |  | 1 | 1215 | B0-DCP-64702-P2013 | 0.6/1kV CU/XLPE/LSZH | 2C x 16sqmm | PE-L1-2C16-02 | 0.96 | 220 | D | 535 | SWGR & MCC | B0-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B0-SWG-49602 | 400V SWITCHGEAR FOR WATER TREATMENT - B (DC CONTROL-1) | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L+, L- | B064-006FT0208 → B064-006FT0207 → B064-006FT0005 → B064-006AC0008 → M0501 → D0503-L43 → M0502 → D0504-L43 → M0503 → D0501-L43 → M0328 → D0324-L43 → M0329 → B114-997AT0021 → B114-017AT0020 → B114-017AT0025 → B025-017ET0042 → B025-017ET0041 → B025-017ET0040 → B025-017ET0016 → B025-017ET0039 → B025-017ET0038 → B025-017ET0036 → B025-017ET0035 → B025-017ET0033 → B025-017ET0032 → B025-017ET0031 → B025-017ET0030 → B025-017ET0021 → B025-017ET0022 → B025-997ET0004 → M0205 → D0205-L15 → M0206 → D0203-L15 → M0207 → D0204-L18 → B049-006AT0002 → B049-006AT0003 → B049-006AT0011 → END
B0-DCP-64701 | -P20 | 13 |  | PE-L1-2C16-02 | PE-L1-2C16-02 | ELE-SWG-0026 |  |  | 1 | 1216 | B0-DCP-64701-P2013 | 0.6/1kV CU/XLPE/LSZH | 2C x 16sqmm | PE-L1-2C16-02 | 0.96 | 220 | D | 525 | SWGR & MCC | B0-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B0-SWG-49602 | 400V SWITCHGEAR FOR WATER TREATMENT - B (DC CONTROL-1) | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L+, L- | B164-006JT0209 → B164-006JT0006 → B064-006AC0007 → M0501 → D0503-L44 → M0502 → D0504-L44 → M0503 → D0501-L44 → M0328 → D0324-L44 → M0329 → B114-996AT0021 → B114-016AT0020 → B114-016AT0025 → B025-016FT0042 → B025-016FT0041 → B025-016FT0040 → B025-996FT0016 → B025-016FT0039 → B025-016FT0038 → B025-016FT0036 → B025-016FT0035 → B025-016FT0033 → B025-016FT0032 → B025-016FT0031 → B025-016FT0030 → B025-016FT0028 → B025-016FT0029 → B025-996FT0005 → M0205 → D0205-L23 → M0206 → D0203-L23 → M0207 → D0204-L17 → B049-006BT0001 → B049-006BT0003 → B049-006BT0014 → END
B0-DB-49601 | -P20 | 02 |  | PE-L1-3C4-15 | PE-L1-3C4-15 | ELE-SWG-0027 |  |  | 1 | 1217 | B0-DB-49601-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 2.43 | 230 | N | 30 | SWGR & MCC | B0-DB-49601 | 400V-230V DIST. BOARD FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, N, PE | B0-SWG-49602 | 400V SWITCHGEAR FOR WATER TREATMENT - B (AUX. POWER) | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, N, PE | B049-006BT0004 → B049-006BT0014 → END
B0-DB-49601 | -P20 | 03 |  | PE-L1-3C4-15 | PE-L1-3C4-15 | ELE-SWG-0027-1 |  |  | 1 | 1218 | B0-DB-49601-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 0.68 | 230 | N | 30 | SWGR & MCC | B0-DB-49601 | 400V-230V DIST. BOARD FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, N, PE | B0-SWG-49602 | 400V SWITCHGEAR FOR WATER TREATMENT - B (MOTOR SPACE HEATER) | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, N, PE | B049-006BT0004 → B049-006BT0014 → END
B0-DB-72602 | -P20 | 05 |  | PE-L1-3C4-15 | PE-L1-3C4-15 | ELE-SWG-0036 |  |  | 1 | 1219 | B0-DB-72602-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 0.78 | 230 | N | 40 | SWGR & MCC | B0-DB-72602 | 400V-230V DIST. BOARD FOR WORKSHOP - B | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, N, PE | B0-MCC-72601 | 400V MCC FOR WORKSHOP - A (AUX. POWER) | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, N, PE | B071-006AT0001 → B071-006BT0002 → END
B0-DB-72601 | -P20 | 07 |  | PE-L1-3C4-15 | PE-L1-3C4-15 | ELE-SWG-0039 |  |  | 1 | 1220 | B0-DB-72601-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 0.78 | 230 | N | 40 | SWGR & MCC | B0-DB-72601 | 400V-230V DIST. BOARD FOR WORKSHOP - A | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, N, PE | B0-MCC-72602 | 400V MCC FOR WORKSHOP - B (AUX. POWER) | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, N, PE | B071-006AT0001 → B071-006BT0002 → END
B1-DB-64601 | -P20 | 07 |  | PE-L1-3C4-15 | PE-L1-3C4-15 | ELE-DU-6001 |  | DONE | 1 | 1221 | B1-DB-64601-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 1.35 | 230 | N | 90 | DC & UPS | B1-DB-64601 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-CH-64701 | BLOCK #1 BATTERY CHARGER - A AUX. POWER | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0090 → B064-016AT0216 → B064-016AT0215 → B064-016AT0214 → B064-016AT0213 → B064-016AT0032 → B064-996AT0120 → M0501 → B064-006AC0020 → B164-006GT0003 → B164-006GT0002 → B164-006GT0203 → END
B1-DB-64602 | -P20 | 10 |  | PE-L1-3C4-15 | PE-L1-3C4-15 | ELE-DU-6002 |  | DONE | 1 | 1222 | B1-DB-64602-P2010 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 0.75 | 230 | N | 100 | DC & UPS | B1-DB-64602 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-UPS-64701 | BLOCK #1 UPS INVERTER - A AUX. POWER | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0106 → B064-016AT0217 → B064-016AT0090 → B064-016AT0216 → B064-016AT0215 → B064-016AT0214 → B064-016AT0213 → B064-016AT0032 → B064-996AT0120 → M0501 → B064-006AC0020 → B164-006GT0003 → B164-006GT0002 → B164-006GT0001 → B164-006GT0201 → END
B1-DCP-64701 | -P20 | 17 |  | PE-L1-1C500-29 | PE-L1-1C500-29 | ELE-DU-6003 | DONE(10/6) | DONE | 1 | 1223 | B1-DCP-64701-P2017 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-29 | 34 | 220 | D | 320 | DC & UPS | B1-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L+ | B1-DCP-59701 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #1 - A | 1.1_MAIN BUILDING COMPLEX (BLOCK #1 ST#1) | L+ | B164-006GT0203 → B164-006GT0002 → B164-006GT0003 → B064-006AC0009 → M0501 → D0517-L23 → M0510 → D0502-L35 → M0326 → D0320-L25 → M0325 → D0319-L31 → M0324 → D0327-L25 → M0321 → D0317-L14 → M0320 → D0323-L14 → M0319 → D0316-L14 → M0318 → D0315-L25 → M0315 → D0314-L25 → B159-006AT0017 → B159-006AT0018 → B159-006AT0005 → END
B1-DCP-64701 | -P20 | 18 |  | PE-L1-1C500-30 | PE-L1-1C500-30 |  | DONE(10/27) | DONE | 1 | 1224 | B1-DCP-64701-P2018 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-30 | 34 | 220 | D | 320 | DC & UPS | B1-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L- | B1-DCP-59701 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #1 - A | 1.1_MAIN BUILDING COMPLEX (BLOCK #1 ST#1) | L- | B164-006GT0203 → B164-006GT0002 → B164-006GT0003 → B064-006AC0009 → M0501 → D0517-L23 → M0510 → D0502-L35 → M0326 → D0320-L25 → M0325 → D0319-L31 → M0324 → D0327-L25 → M0321 → D0317-L14 → M0320 → D0323-L14 → M0319 → D0316-L14 → M0318 → D0315-L25 → M0315 → D0314-L25 → B159-006AT0017 → B159-006AT0018 → B159-006AT0005 → END
B1-DCP-64702 | -P20 | 17 |  | PE-L1-1C500-31 | PE-L1-1C500-31 | ELE-DU-6004 | DONE(10/6) | DONE | 1 | 1225 | B1-DCP-64702-P2017 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-31 | 34 | 220 | D | 340 | DC & UPS | B1-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L+ | B1-DCP-59702 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #1 - B | 1.1_MAIN BUILDING COMPLEX (BLOCK #1 ST#1) | L+ | B164-006HT0204 → B164-006HT0203 → B164-006HT0002 → B164-006HT0003 → B064-006AC0010 → M0501 → D0517-L24 → M0510 → D0502-L36 → M0326 → D0320-L36 → M0325 → D0319-L32 → M0324 → D0327-L26 → M0321 → D0317-L15 → M0320 → D0323-L15 → M0319 → D0316-L15 → M0318 → D0315-L16 → M0315 → D0314-L26 → B159-006BT0013 → B159-006BT0024 → B159-006BT0023 → B159-006BT0022 → B159-006BT0010 → B159-006BT0018 → B159-006BT0005 → END
B1-DCP-64702 | -P20 | 18 |  | PE-L1-1C500-32 | PE-L1-1C500-32 |  | DONE(10/27) | DONE | 1 | 1226 | B1-DCP-64702-P2018 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-32 | 34 | 220 | D | 340 | DC & UPS | B1-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L- | B1-DCP-59702 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #1 - B | 1.1_MAIN BUILDING COMPLEX (BLOCK #1 ST#1) | L- | B164-006HT0204 → B164-006HT0203 → B164-006HT0002 → B164-006HT0003 → B064-006AC0010 → M0501 → D0517-L24 → M0510 → D0502-L36 → M0326 → D0320-L36 → M0325 → D0319-L32 → M0324 → D0327-L26 → M0321 → D0317-L15 → M0320 → D0323-L15 → M0319 → D0316-L15 → M0318 → D0315-L16 → M0315 → D0314-L26 → B159-006BT0013 → B159-006BT0024 → B159-006BT0023 → B159-006BT0022 → B159-006BT0010 → B159-006BT0018 → B159-006BT0005 → END
B1-DB-59601 | -P20 | 19 |  | PE-L1-3C4-15 | PE-L1-3C4-15 | ELE-DU-6005 |  |  | 1 | 1227 | B1-DB-59601-P2019 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 0.3 | 230 | N | 30 | DC & UPS | B1-DB-59601 | 400V-230V DIST. BOARD FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-DCP-59701 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #1 - A | 1.1_MAIN BUILDING COMPLEX (BLOCK #1 ST#1) | L1, N, PE | B159-006AT0003 → B159-006AT0014 → END
B1-UPSP-64701 | -P20 | 08 |  | PE-L1-5C70/35-05 | PE-L1-5C70/35-05 | ELE-DU-6006 | DONE(9/28) | DONE | 1 | 1228 | B1-UPSP-64701-P2008 | 0.6/1kV CU/XLPE/LSZH | 4C x 70sqmm + 1C X 35sqmm | PE-L1-5C70/35-05 | 10 | 400 | U | 330 | DC & UPS | B1-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B1-UPSP-59701 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR STG #1 - A | 1.1_MAIN BUILDING COMPLEX (BLOCK #1 ST#1) | L1, L2, L3, N, PE | B164-006GT0201 → B164-006GT0001 → B164-006GT0002 → B164-006GT0003 → B064-006AC0022 → M0501 → D0517-L23 → M0510 → D0502-L35 → M0326 → D0320-L33 → M0325 → D0319-L24 → M0324 → D0327-L24 → M0321 → D0317-L23 → M0320 → D0323-L22 → M0319 → D0316-L22 → M0318 → D0315-L23 → M0315 → D0314-L23 → B159-006AT0017 → B159-006AT0018 → B159-006AT0005 → B159-006AT0014 → END
B1-UPSP-64702 | -P20 | 07 |  | PE-L1-5C70/35-02 | PE-L1-5C70/35-02 | ELE-DU-6007 | DONE(10/6) | DONE | 1 | 1229 | B1-UPSP-64702-P2007 | 0.6/1kV CU/XLPE/LSZH | 4C x 70sqmm + 1C X 35sqmm | PE-L1-5C70/35-02 | 10 | 400 | U | 360 | DC & UPS | B1-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B1-UPSP-59702 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR STG #1 - B | 1.1_MAIN BUILDING COMPLEX (BLOCK #1 ST#1) | L1, L2, L3, N, PE | B164-006HT0202 → B164-006HT0007 → B164-006HT0008 → B164-006HT0009 → B164-006HT0010 → B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0022 → M0501 → D0517-L23 → M0510 → D0502-L36 → M0326 → D0320-L36 → M0325 → D0319-L32 → M0324 → D0327-L26 → M0321 → D0317-L15 → M0320 → D0323-L15 → M0319 → D0316-L15 → M0318 → D0315-L16 → M0315 → D0314-L26 → B159-006BT0013 → B159-006BT0024 → B159-006BT0023 → B159-006BT0022 → B159-006BT0010 → B159-006BT0018 → B159-006BT0006 → B159-006BT0019 → B159-006BT0003 → END
B1-DB-59602 | -P20 | 07 |  | PE-L1-3C4-15 | PE-L1-3C4-15 | ELE-DU-6008 |  |  | 1 | 1230 | B1-DB-59602-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 0.3 | 230 | N | 20 | DC & UPS | B1-DB-59602 | 400V-230V DIST. BOARD FOR ST #1 FOR BLOCK #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-UPSP-59701 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR STG #1 - A | 1.1_MAIN BUILDING COMPLEX (BLOCK #1 ST#1) | L1, N, PE | B159-006AT0005 → B159-006AT0014 → END
B1-ESWG-64601 | -P20 | 05 |  | PE-L1-1C240-04 | PE-L1-1C240-04 | ELE-DU-6009 |  | DONE | 1 | 1231 | B1-ESWG-64601-P2005 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-04 | 400 | 400 | E | 130 | DC & UPS | B1-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1 | B1-CH-64701 | BLOCK #1 BATTERY CHARGER - A | 1.2_LEB FOR BLOCK #1 | L1 | B164-016BT0105 → B164-016BT0104 → B164-016BT0103 → B164-016BT0102 → B164-016BT0101 → B164-016BT0100 → B164-996BT0024 → M0504 → D0531-L41 → M0510 → D0517-L21 → M0501 → B064-006AC0014 → B164-006HT0003 → B164-006HT0002 → B164-006HT0203 → END | B164-016BT0105 → B164-016BT0104 → B164-016BT0103 → B164-016BT0102 → B164-016BT0101 → B164-016BT0100 → B164-996BT0024 → M0504 → D0531-L41 → M0510 → D0517-L21 → M0501 → B064-006AC0014 → B164-006GT0003 → B164-006GT0002 → B164-006GT0203 → END |  |  |  |  | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B1-ESWG-64601 | -P20 | 06 |  | PE-L1-1C240-04 | PE-L1-1C240-04 |  |  | DONE | 1 | 1232 | B1-ESWG-64601-P2006 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-04 | 400 | 400 | E | 130 | DC & UPS | B1-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L2 | B1-CH-64701 | BLOCK #1 BATTERY CHARGER - A | 1.2_LEB FOR BLOCK #1 | L2 | B164-016BT0105 → B164-016BT0104 → B164-016BT0103 → B164-016BT0102 → B164-016BT0101 → B164-016BT0100 → B164-996BT0024 → M0504 → D0531-L41 → M0510 → D0517-L21 → M0501 → B064-006AC0014 → B164-006HT0003 → B164-006HT0002 → B164-006HT0203 → END | B164-016BT0105 → B164-016BT0104 → B164-016BT0103 → B164-016BT0102 → B164-016BT0101 → B164-016BT0100 → B164-996BT0024 → M0504 → D0531-L41 → M0510 → D0517-L21 → M0501 → B064-006AC0014 → B164-006GT0003 → B164-006GT0002 → B164-006GT0203 → END |  |  |  |  | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B1-ESWG-64601 | -P20 | 07 |  | PE-L1-1C240-04 | PE-L1-1C240-04 |  |  | DONE | 1 | 1233 | B1-ESWG-64601-P2007 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-04 | 400 | 400 | E | 130 | DC & UPS | B1-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L3 | B1-CH-64701 | BLOCK #1 BATTERY CHARGER - A | 1.2_LEB FOR BLOCK #1 | L3 | B164-016BT0105 → B164-016BT0104 → B164-016BT0103 → B164-016BT0102 → B164-016BT0101 → B164-016BT0100 → B164-996BT0024 → M0504 → D0531-L41 → M0510 → D0517-L21 → M0501 → B064-006AC0014 → B164-006HT0003 → B164-006HT0002 → B164-006HT0203 → END | B164-016BT0105 → B164-016BT0104 → B164-016BT0103 → B164-016BT0102 → B164-016BT0101 → B164-016BT0100 → B164-996BT0024 → M0504 → D0531-L41 → M0510 → D0517-L21 → M0501 → B064-006AC0014 → B164-006GT0003 → B164-006GT0002 → B164-006GT0203 → END |  |  |  |  | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B1-ESWG-64601 | -P20 | 08 |  | PE-L1-1C240-04 | PE-L1-1C240-04 |  |  | DONE | 1 | 1234 | B1-ESWG-64601-P2008 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-04 | 400 | 400 | E | 130 | DC & UPS | B1-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1 | B1-CH-64701 | BLOCK #1 BATTERY CHARGER - A | 1.2_LEB FOR BLOCK #1 | L1 | B164-016BT0105 → B164-016BT0104 → B164-016BT0103 → B164-016BT0102 → B164-016BT0101 → B164-016BT0100 → B164-996BT0024 → M0504 → D0531-L41 → M0510 → D0517-L21 → M0501 → B064-006AC0015 → B164-006HT0003 → B164-006HT0002 → B164-006HT0203 → END | [5 empty] | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B1-ESWG-64601 | -P20 | 09 |  | PE-L1-1C240-04 | PE-L1-1C240-04 |  |  | DONE | 1 | 1235 | B1-ESWG-64601-P2009 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-04 | 400 | 400 | E | 130 | DC & UPS | B1-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L2 | B1-CH-64701 | BLOCK #1 BATTERY CHARGER - A | 1.2_LEB FOR BLOCK #1 | L2 | B164-016BT0105 → B164-016BT0104 → B164-016BT0103 → B164-016BT0102 → B164-016BT0101 → B164-016BT0100 → B164-996BT0024 → M0504 → D0531-L41 → M0510 → D0517-L21 → M0501 → B064-006AC0015 → B164-006HT0003 → B164-006HT0002 → B164-006HT0203 → END | [5 empty] | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B1-ESWG-64601 | -P20 | 10 |  | PE-L1-1C240-04 | PE-L1-1C240-04 |  |  | DONE | 1 | 1236 | B1-ESWG-64601-P2010 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-04 | 400 | 400 | E | 130 | DC & UPS | B1-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L3 | B1-CH-64701 | BLOCK #1 BATTERY CHARGER - A | 1.2_LEB FOR BLOCK #1 | L3 | B164-016BT0105 → B164-016BT0104 → B164-016BT0103 → B164-016BT0102 → B164-016BT0101 → B164-016BT0100 → B164-996BT0024 → M0504 → D0531-L41 → M0510 → D0517-L21 → M0501 → B064-006AC0015 → B164-006HT0003 → B164-006HT0002 → B164-006HT0203 → END | [5 empty] | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B1-ESWG-64601 | -P20 | 11 |  | PE-L1-1C240-04 | PE-L1-1C240-04 |  |  | DONE | 1 | 1237 | B1-ESWG-64601-P2011 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-04 | 400 | 400 | E | 130 | DC & UPS | B1-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | N | B1-CH-64701 | BLOCK #1 BATTERY CHARGER - A | 1.2_LEB FOR BLOCK #1 | N | B164-016BT0105 → B164-016BT0104 → B164-016BT0103 → B164-016BT0102 → B164-016BT0101 → B164-016BT0100 → B164-996BT0024 → M0504 → D0531-L41 → M0510 → D0517-L21 → M0501 → B064-006AC0014 → B164-006HT0003 → B164-006HT0002 → B164-006HT0203 → END | B164-016BT0105 → B164-016BT0104 → B164-016BT0103 → B164-016BT0102 → B164-016BT0101 → B164-016BT0100 → B164-996BT0024 → M0504 → D0531-L41 → M0510 → D0517-L21 → M0501 → B064-006AC0014 → B164-006GT0003 → B164-006GT0002 → B164-006GT0203 → END |  |  |  |  | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B1-ESWG-64601 | -P20 | 12 |  | PE-L1-1C240-04 | PE-L1-1C240-04 |  |  | DONE | 1 | 1238 | B1-ESWG-64601-P2012 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-04 | 400 | 400 | E | 130 | DC & UPS | B1-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | PE | B1-CH-64701 | BLOCK #1 BATTERY CHARGER - A | 1.2_LEB FOR BLOCK #1 | PE | B164-016BT0105 → B164-016BT0104 → B164-016BT0103 → B164-016BT0102 → B164-016BT0101 → B164-016BT0100 → B164-996BT0024 → M0504 → D0531-L41 → M0510 → D0517-L21 → M0501 → B064-006AC0015 → B164-006HT0003 → B164-006HT0002 → B164-006HT0203 → END | [5 empty] | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B1-ESWG-64602 | -P20 | 05 |  | PE-L1-1C240-06 | PE-L1-1C240-06 | ELE-DU-6010 |  | DONE | 1 | 1239 | B1-ESWG-64602-P2005 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-06 | 400 | 400 | E | 140 | DC & UPS | B1-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1 | B1-CH-64702 | BLOCK #1 BATTERY CHARGER - B | 1.2_LEB FOR BLOCK #1 | L1 | B164-016FT0112 → B164-016FT0299 → B164-016FT0095 → B164-016FT0094 → B164-016FT0093 → B164-016FT0092 → B164-996FT0022 → M0504 → D0531-L42 → M0510 → D0517-L22 → M0501 → B064-006AC0016 → B164-006GT0005 → B164-006GT0207 → B164-006GT0208 → B164-006GT0009 → B164-006GT0204 → END | [5 empty] | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B1-ESWG-64602 | -P20 | 06 |  | PE-L1-1C240-06 | PE-L1-1C240-06 |  |  | DONE | 1 | 1240 | B1-ESWG-64602-P2006 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-06 | 400 | 400 | E | 140 | DC & UPS | B1-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L2 | B1-CH-64702 | BLOCK #1 BATTERY CHARGER - B | 1.2_LEB FOR BLOCK #1 | L2 | B164-016FT0112 → B164-016FT0299 → B164-016FT0095 → B164-016FT0094 → B164-016FT0093 → B164-016FT0092 → B164-996FT0022 → M0504 → D0531-L42 → M0510 → D0517-L22 → M0501 → B064-006AC0016 → B164-006GT0005 → B164-006GT0207 → B164-006GT0208 → B164-006GT0009 → B164-006GT0204 → END | [5 empty] | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B1-ESWG-64602 | -P20 | 07 |  | PE-L1-1C240-06 | PE-L1-1C240-06 |  |  | DONE | 1 | 1241 | B1-ESWG-64602-P2007 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-06 | 400 | 400 | E | 140 | DC & UPS | B1-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L3 | B1-CH-64702 | BLOCK #1 BATTERY CHARGER - B | 1.2_LEB FOR BLOCK #1 | L3 | B164-016FT0112 → B164-016FT0299 → B164-016FT0095 → B164-016FT0094 → B164-016FT0093 → B164-016FT0092 → B164-996FT0022 → M0504 → D0531-L42 → M0510 → D0517-L22 → M0501 → B064-006AC0016 → B164-006GT0005 → B164-006GT0207 → B164-006GT0208 → B164-006GT0009 → B164-006GT0204 → END | [5 empty] | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B1-ESWG-64602 | -P20 | 08 |  | PE-L1-1C240-06 | PE-L1-1C240-06 |  |  | DONE | 1 | 1242 | B1-ESWG-64602-P2008 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-06 | 400 | 400 | E | 140 | DC & UPS | B1-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1 | B1-CH-64702 | BLOCK #1 BATTERY CHARGER - B | 1.2_LEB FOR BLOCK #1 | L1 | B164-016FT0112 → B164-016FT0299 → B164-016FT0095 → B164-016FT0094 → B164-016FT0093 → B164-016FT0092 → B164-996FT0022 → M0504 → D0531-L42 → M0510 → D0517-L22 → M0501 → B064-006AC0017 → B164-006GT0005 → B164-006GT0207 → B164-006GT0208 → B164-006GT0009 → B164-006GT0204 → END | [5 empty] | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B1-ESWG-64602 | -P20 | 09 |  | PE-L1-1C240-06 | PE-L1-1C240-06 |  |  | DONE | 1 | 1243 | B1-ESWG-64602-P2009 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-06 | 400 | 400 | E | 140 | DC & UPS | B1-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L2 | B1-CH-64702 | BLOCK #1 BATTERY CHARGER - B | 1.2_LEB FOR BLOCK #1 | L2 | B164-016FT0112 → B164-016FT0299 → B164-016FT0095 → B164-016FT0094 → B164-016FT0093 → B164-016FT0092 → B164-996FT0022 → M0504 → D0531-L42 → M0510 → D0517-L22 → M0501 → B064-006AC0017 → B164-006GT0005 → B164-006GT0207 → B164-006GT0208 → B164-006GT0009 → B164-006GT0204 → END | [5 empty] | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B1-ESWG-64602 | -P20 | 10 |  | PE-L1-1C240-06 | PE-L1-1C240-06 |  |  | DONE | 1 | 1244 | B1-ESWG-64602-P2010 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-06 | 400 | 400 | E | 140 | DC & UPS | B1-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L3 | B1-CH-64702 | BLOCK #1 BATTERY CHARGER - B | 1.2_LEB FOR BLOCK #1 | L3 | B164-016FT0112 → B164-016FT0299 → B164-016FT0095 → B164-016FT0094 → B164-016FT0093 → B164-016FT0092 → B164-996FT0022 → M0504 → D0531-L42 → M0510 → D0517-L22 → M0501 → B064-006AC0017 → B164-006GT0005 → B164-006GT0207 → B164-006GT0208 → B164-006GT0009 → B164-006GT0204 → END | [5 empty] | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B1-ESWG-64602 | -P20 | 11 |  | PE-L1-1C240-06 | PE-L1-1C240-06 |  |  | DONE | 1 | 1245 | B1-ESWG-64602-P2011 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-06 | 400 | 400 | E | 140 | DC & UPS | B1-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | N | B1-CH-64702 | BLOCK #1 BATTERY CHARGER - B | 1.2_LEB FOR BLOCK #1 | N | B164-016FT0112 → B164-016FT0299 → B164-016FT0095 → B164-016FT0094 → B164-016FT0093 → B164-016FT0092 → B164-996FT0022 → M0504 → D0531-L42 → M0510 → D0517-L22 → M0501 → B064-006AC0016 → B164-006GT0005 → B164-006GT0207 → B164-006GT0208 → B164-006GT0009 → B164-006GT0204 → END | [5 empty] | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B1-ESWG-64602 | -P20 | 12 |  | PE-L1-1C240-06 | PE-L1-1C240-06 |  |  | DONE | 1 | 1246 | B1-ESWG-64602-P2012 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-06 | 400 | 400 | E | 140 | DC & UPS | B1-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | PE | B1-CH-64702 | BLOCK #1 BATTERY CHARGER - B | 1.2_LEB FOR BLOCK #1 | PE | B164-016FT0112 → B164-016FT0299 → B164-016FT0095 → B164-016FT0094 → B164-016FT0093 → B164-016FT0092 → B164-996FT0022 → M0504 → D0531-L42 → M0510 → D0517-L22 → M0501 → B064-006AC0017 → B164-006GT0005 → B164-006GT0207 → B164-006GT0208 → B164-006GT0009 → B164-006GT0204 → END | [5 empty] | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B1-DCP-64701 | -P20 | 23 |  | PE-L1-1C185-03 | PE-L1-1C185-03 | ELE-DU-6011 |  | DONE | 1 | 1247 | B1-DCP-64701-P2023 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-03 | 120 | 220 | D | 40 | DC & UPS | B1-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L+ | B1-UPS-64701 | BLOCK #1 UPS INVERTER - A | 1.2_LEB FOR BLOCK #1 | L+ | B164-006GT0203 → B164-006GT0001 → B164-006GT0201 → END
B1-DCP-64701 | -P20 | 24 |  | PE-L1-1C185-03 | PE-L1-1C185-03 |  |  | DONE | 1 | 1248 | B1-DCP-64701-P2024 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-03 | 120 | 220 | D | 40 | DC & UPS | B1-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L+ | B1-UPS-64701 | BLOCK #1 UPS INVERTER - A | 1.2_LEB FOR BLOCK #1 | L+ | B164-006GT0203 → B164-006GT0001 → B164-006GT0201 → END
B1-DCP-64701 | -P20 | 25 |  | PE-L1-1C185-03 | PE-L1-1C185-03 |  |  | DONE | 1 | 1249 | B1-DCP-64701-P2025 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-03 | 120 | 220 | D | 40 | DC & UPS | B1-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L- | B1-UPS-64701 | BLOCK #1 UPS INVERTER - A | 1.2_LEB FOR BLOCK #1 | L- | B164-006GT0203 → B164-006GT0001 → B164-006GT0201 → END
B1-DCP-64701 | -P20 | 26 |  | PE-L1-1C185-03 | PE-L1-1C185-03 |  |  | DONE | 1 | 1250 | B1-DCP-64701-P2026 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-03 | 120 | 220 | D | 40 | DC & UPS | B1-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L- | B1-UPS-64701 | BLOCK #1 UPS INVERTER - A | 1.2_LEB FOR BLOCK #1 | L- | B164-006GT0203 → B164-006GT0001 → B164-006GT0201 → END
B1-DCP-64702 | -P20 | 23 |  | PE-L1-1C185-02 | PE-L1-1C185-02 | ELE-DU-6012 |  | DONE | 1 | 1251 | B1-DCP-64702-P2023 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-02 | 120 | 220 | D | 30 | DC & UPS | B1-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L+ | B1-UPS-64702 | BLOCK #1 UPS INVERTER - B | 1.2_LEB FOR BLOCK #1 | L+ | B164-006HT0204 → B164-006HT0007 → B164-006HT0202 → END | B164-006GT0204 → B164-006GT0007 → B164-006GT0202 → END
B1-DCP-64702 | -P20 | 24 |  | PE-L1-1C185-02 | PE-L1-1C185-02 |  |  | DONE | 1 | 1252 | B1-DCP-64702-P2024 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-02 | 120 | 220 | D | 30 | DC & UPS | B1-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L+ | B1-UPS-64702 | BLOCK #1 UPS INVERTER - B | 1.2_LEB FOR BLOCK #1 | L+ | B164-006HT0204 → B164-006HT0007 → B164-006HT0202 → END | B164-006GT0204 → B164-006GT0007 → B164-006GT0202 → END
B1-DCP-64702 | -P20 | 25 |  | PE-L1-1C185-02 | PE-L1-1C185-02 |  |  | DONE | 1 | 1253 | B1-DCP-64702-P2025 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-02 | 120 | 220 | D | 30 | DC & UPS | B1-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L- | B1-UPS-64702 | BLOCK #1 UPS INVERTER - B | 1.2_LEB FOR BLOCK #1 | L- | B164-006HT0204 → B164-006HT0007 → B164-006HT0202 → END | B164-006GT0204 → B164-006GT0007 → B164-006GT0202 → END
B1-DCP-64702 | -P20 | 26 |  | PE-L1-1C185-02 | PE-L1-1C185-02 |  |  | DONE | 1 | 1254 | B1-DCP-64702-P2026 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-02 | 120 | 220 | D | 30 | DC & UPS | B1-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L- | B1-UPS-64702 | BLOCK #1 UPS INVERTER - B | 1.2_LEB FOR BLOCK #1 | L- | B164-006HT0204 → B164-006HT0007 → B164-006HT0202 → END | B164-006GT0204 → B164-006GT0007 → B164-006GT0202 → END
B1-EMCC-64601 | -P20 | 06 | 재배정 미배정Drum사용으로 추가 발주 원인임. | PE-L1-5C120/70-03 | PE-L1-5C120/70-01 | ELE-DU-6013 | 미배정Drum사용으로 추가 발주 원인임. | DONE | 1 | 1255 | B1-EMCC-64601-P2006 | 0.6/1kV CU/XLPE/LSZH | 4C x 120sqmm + 1C X 70sqmm | PE-L1-5C120/70-01 | 120 | 400 | E | 130 | DC & UPS | B1-EMCC-64601 | 400V EMERGENCY MCC FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B1-AVR-64701 | BLOCK #1 UPS BYPASS LINE - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B164-016BT0105 → B164-016BT0104 → B164-016BT0103 → B164-016BT0102 → B164-016BT0101 → B164-016BT0100 → B164-996BT0024 → M0504 → D0531-L41 → M0510 → D0517-L31 → M0501 → B064-006AC0018 → B164-006GT0003 → B164-006GT0002 → B164-006GT0001 → B164-006GT0201 → END
B1-EMCC-64602 | -P20 | 05 |  | PE-L1-5C120/70-01 | PE-L1-5C120/70-01 | ELE-DU-6014 |  | DONE | 1 | 1256 | B1-EMCC-64602-P2005 | 0.6/1kV CU/XLPE/LSZH | 4C x 120sqmm + 1C X 70sqmm | PE-L1-5C120/70-01 | 120 | 400 | E | 150 | DC & UPS | B1-EMCC-64602 | 400V EMERGENCY MCC FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B1-AVR-64702 | BLOCK #1 UPS BYPASS LINE - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B164-016FT0112 → B164-016FT0299 → B164-016FT0095 → B164-016FT0094 → B164-016FT0093 → B164-016FT0092 → B164-996FT0022 → M0504 → D0531-L42 → M0510 → D0517-L31 → M0501 → B064-006AC0019 → B164-006HT0005 → B164-006HT0004 → B164-006HT0205 → B164-006HT0206 → B164-006HT0008 → B164-006HT0007 → B164-006HT0202 → END
B1-DB-64602 | -P20 | 11 |  | PE-L1-3C4-15 | PE-L1-3C4-15 | ELE-DU-6015 |  | DONE | 1 | 1257 | B1-DB-64602-P2011 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 0.15 | 230 | N | 110 | DC & UPS | B1-DB-64602 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-FC-64701 | BLOCK #1 BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0106 → B064-016AT0217 → B064-016AT0090 → B064-016AT0216 → B064-016AT0215 → B064-016AT0214 → B064-016AT0213 → B064-016AT0032 → B064-996AT0120 → M0501 → B064-006AC0020 → B164-006HT0005 → B164-006HT0207 → B164-006HT0208 → B164-006HT0009 → B164-006HT0008 → B164-006HT0007 → END
B1-UPSP-64701 | -P20 | 15 |  | PE-L1-5C95/50-01 | PE-L1-5C95/50-01 | ELE-DU-6016 |  | DONE | 1 | 1258 | B1-UPSP-64701-P2015 | 0.6/1kV CU/XLPE/LSZH | 4C x 95sqmm + 1C X 50sqmm | PE-L1-5C95/50-01 | 24 | 400 | U | 410 | DC & UPS | B1-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B1-UPSP-73701 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ADMIN. - BLOCK#1 - A | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / SERVER ROOM | L1, L2, L3, N, PE | B164-006GT0201 → B164-006GT0001 → B164-006GT0002 → B164-006GT0003 → B064-006AC0007 → M0501 → B064-996AT0120 → B064-016AT0033 → B064-016AT0034 → B064-016AT0035 → B064-016AT0036 → B064-016AT0037 → B064-016AT0309 → B064-016AT0017 → B064-016AT0122 → B064-016AT0314 → B064-016AC0001 → B064-006AC0025 → B064-016AC0009 → B073-006AT0102 → B073-006AT0104 → B073-006AT0106 → B073-006AT0108 → B073-006AT0001 → B073-006AT0003 → B073-006AT0006 → B073-006AT0007 → B073-996AT0009 → B073-996AT0021 → B073-016AT0001 → B073-016AT0014 → B073-016AT0015 → B073-016AT0013 → END
B1-UPSP-64702 | -P20 | 14 | 현장포설일정 변경으로 인한 Drum 재배정(7/28) | PE-L1-4C95/50-02 | PE-L1-4C95/50-02 | ELE-DU-6017 |  | DONE | 1 | 1259 | B1-UPSP-64702-P2014 | 0.6/1kV CU/XLPE/LSZH | 3C x 95sqmm + 1C X 50sqmm | PE-L1-4C95/50-02 | 24 | 400 | U | 440 | DC & UPS | B1-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B1-UPSP-73702 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ADMIN. - BLOCK#1 - B | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / SERVER ROOM | L1, L2, L3, PE | B164-006HT0202 → B164-006HT0007 → B164-006HT0008 → B164-006HT0206 → B164-006HT0205 → B164-006HT0004 → B164-006HT0005 → B064-006AC0008 → M0501 → B064-996AT0120 → B064-016AT0032 → B064-016AT0212 → B064-016AT0011 → B064-016AT0012 → B064-016AT0013 → B064-016AT0014 → B064-016AT0015 → B064-016AT0016 → B064-016AT0017 → B064-016AT0122 → B064-016AT0314 → B064-016AC0004 → B064-006AC0028 → B064-016AC0012 → B073-006AT0102 → B073-006AT0104 → B073-006AT0106 → B073-006AT0108 → B073-006AT0001 → B073-006AT0003 → B073-006AT0006 → B073-006AT0007 → B073-996AT0009 → B073-996AT0021 → B073-016AT0001 → B073-016AT0014 → B073-016AT0015 → B073-016AT0013 → END
B1-UPSP-64702 | -P20 | 14 | 현장포설일정 변경으로 인한 Drum 재배정(7/28) | PE-L1-1C95-01 | PE-L1-1C95-01 | ELE-DU-6017 |  | DONE | 1 | 1260 | B1-UPSP-64702-P2015 | 0.6/1kV CU/XLPE/LSZH | 1C x 95sqmm | PE-L1-1C95-01 | 24 | 400 | U | 440 | DC & UPS | B1-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | N | B1-UPSP-73702 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ADMIN. - BLOCK#1 - B | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / SERVER ROOM | N | B164-006HT0202 → B164-006HT0007 → B164-006HT0008 → B164-006HT0206 → B164-006HT0205 → B164-006HT0004 → B164-006HT0005 → B064-006AC0008 → M0501 → B064-996AT0120 → B064-016AT0032 → B064-016AT0212 → B064-016AT0011 → B064-016AT0012 → B064-016AT0013 → B064-016AT0014 → B064-016AT0015 → B064-016AT0016 → B064-016AT0017 → B064-016AT0122 → B064-016AT0314 → B064-016AC0004 → B064-006AC0028 → B064-016AC0012 → B073-006AT0102 → B073-006AT0104 → B073-006AT0106 → B073-006AT0108 → B073-006AT0001 → B073-006AT0003 → B073-006AT0006 → B073-006AT0007 → B073-996AT0009 → B073-996AT0021 → B073-016AT0001 → B073-016AT0014 → B073-016AT0015 → B073-016AT0013 → END
B2-DB-64601 | -P20 | 11 |  | PE-L1-3C4-25 | PE-L1-3C4-25 | ELE-DU-7001 |  |  | 1 | 1261 | B2-DB-64601-P2011 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-25 | 1.2 | 230 | N | 90 | DC & UPS | B2-DB-64601 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-CH-64701 | BLOCK #2 BATTERY CHARGER - A AUX. POWER | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016BT0024 → B264-016BT0025 → B264-016BT0026 → B264-016BT0027 → B264-016BT0028 → B264-996BT0012 → M0407 → B264-006AC0011 → B264-017ET0062 → B264-017ET0063 → END
B2-DB-64602 | -P20 | 05 |  | PE-L1-3C4-25 | PE-L1-3C4-25 | ELE-DU-7002 |  |  | 1 | 1262 | B2-DB-64602-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-25 | 1.2 | 230 | N | 90 | DC & UPS | B2-DB-64602 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-UPS-64701 | BLOCK #2 UPS INVERTER - A AUX. POWER | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016BT0045 → B264-016BT0046 → B264-016BT0047 → B264-996BT0013 → M0407 → B264-006AC0011 → B264-016ET0062 → B264-016ET0063 → END
B2-DCP-64701 | -P20 | 17 |  | PE-L1-1C400-01 | PE-L1-1C400-01 | ELE-DU-7003 |  |  | 1 | 1263 | B2-DCP-64701-P2017 | 0.6/1kV CU/XLPE/LSZH | 1C x 400sqmm | PE-L1-1C400-01 | 34 | 220 | D | 240 | DC & UPS | B2-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L+ | B2-DCP-59701 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #2 - A | 1.1_MAIN BUILDING COMPLEX (BLOCK #2 ST#2) | L+ | B264-016FT0063 → B264-016FT0062 → B264-006AC0005 → M0407 → D0302-L34 → M0302 → D0303-L34 → M0303 → D0305-L25 → M0306 → D0321-L25 → M0307 → D0306-L23 → M0308 → D0308-L23 → M0310 → D0309-L23 → M0311 → D0310-L23 → B259-006BT0013 → B259-006BT0024 → B259-006BT0023 → B259-006BT0022 → B259-006BT0010 → B259-006BT0018 → B259-006BT0005 → END
B2-DCP-64701 | -P20 | 18 |  | PE-L1-1C400-01 | PE-L1-1C400-01 |  |  |  | 1 | 1264 | B2-DCP-64701-P2018 | 0.6/1kV CU/XLPE/LSZH | 1C x 400sqmm | PE-L1-1C400-01 | 34 | 220 | D | 240 | DC & UPS | B2-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L- | B2-DCP-59701 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #2 - A | 1.1_MAIN BUILDING COMPLEX (BLOCK #2 ST#2) | L- | B264-016FT0063 → B264-016FT0062 → B264-006AC0005 → M0407 → D0302-L34 → M0302 → D0303-L34 → M0303 → D0305-L25 → M0306 → D0321-L25 → M0307 → D0306-L23 → M0308 → D0308-L23 → M0310 → D0309-L23 → M0311 → D0310-L23 → B259-006BT0013 → B259-006BT0024 → B259-006BT0023 → B259-006BT0022 → B259-006BT0010 → B259-006BT0018 → B259-006BT0005 → END
B2-DCP-64702 | -P20 | 17 |  | PE-L1-1C400-02 | PE-L1-1C400-02 | ELE-DU-7004 |  |  | 1 | 1265 | B2-DCP-64702-P2017 | 0.6/1kV CU/XLPE/LSZH | 1C x 400sqmm | PE-L1-1C400-02 | 34 | 220 | D | 240 | DC & UPS | B2-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L+ | B2-DCP-59702 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #2 - B | 1.1_MAIN BUILDING COMPLEX (BLOCK #2 ST#2) | L+ | B264-016ET0063 → B264-016ET0062 → B264-006AC0009 → M0407 → D0302-L27 → M0302 → D0303-L27 → M0303 → D0305-L22 → M0306 → D0321-L26 → M0307 → D0306-L33 → M0308 → D0308-L22 → M0310 → D0309-L22 → M0311 → D0310-L22 → B259-006AT0017 → B259-006AT0016 → B259-006AT0015 → END
B2-DCP-64702 | -P20 | 18 |  | PE-L1-1C400-02 | PE-L1-1C400-02 |  |  |  | 1 | 1266 | B2-DCP-64702-P2018 | 0.6/1kV CU/XLPE/LSZH | 1C x 400sqmm | PE-L1-1C400-02 | 34 | 220 | D | 240 | DC & UPS | B2-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L- | B2-DCP-59702 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #2 - B | 1.1_MAIN BUILDING COMPLEX (BLOCK #2 ST#2) | L- | B264-016ET0063 → B264-016ET0062 → B264-006AC0009 → M0407 → D0302-L27 → M0302 → D0303-L27 → M0303 → D0305-L22 → M0306 → D0321-L26 → M0307 → D0306-L33 → M0308 → D0308-L22 → M0310 → D0309-L22 → M0311 → D0310-L22 → B259-006AT0017 → B259-006AT0016 → B259-006AT0015 → END
B2-DB-59601 | -P20 | 19 |  | PE-L1-3C4-25 | PE-L1-3C4-25 | ELE-DU-7005 |  |  | 1 | 1267 | B2-DB-59601-P2019 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-25 | 0.3 | 230 | N | 30 | DC & UPS | B2-DB-59601 | 400V-230V DIST. BOARD FOR ST #2 FOR BLOCK #2 - A | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B2-DCP-59701 | 220V DC LOCAL DISTRIBUTION PANEL FOR STG #2 - A | 1.1_MAIN BUILDING COMPLEX (BLOCK #2 ST#2) | L1, N, PE | B259-006AT0003 → B259-006AT0014 → END
B2-UPSP-64701 | -P20 | 08 |  | PE-L1-5C70/35-05 | PE-L1-5C70/35-05 | ELE-DU-7006 |  |  | 1 | 1268 | B2-UPSP-64701-P2008 | 0.6/1kV CU/XLPE/LSZH | 4C x 70sqmm + 1C X 35sqmm | PE-L1-5C70/35-05 | 10 | 400 | U | 250 | DC & UPS | B2-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, N, PE | B2-UPSP-59701 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR STG #2 - A | 1.1_MAIN BUILDING COMPLEX (BLOCK #2 ST#2) | L1, L2, L3, N, PE | B264-016DT0061 → B264-016DT0248 → B264-016ET0062 → B264-006AC0007 → M0407 → D0302-L36 → M0302 → D0303-L36 → M0303 → D0305-L26 → M0306 → D0321-L26 → M0307 → D0306-L33 → M0308 → D0308-L24 → M0310 → D0309-L24 → M0311 → D0310-L24 → B259-006BT0013 → B259-006BT0024 → B259-006BT0023 → B259-006BT0022 → B259-006BT0010 → B259-006BT0018 → B259-006BT0006 → B259-006BT0019 → B259-006BT0003 → END
B2-UPSP-64702 | -P20 | 07 | Route변경_길이감소 | PE-L1-5C70/35-05 | PE-L1-5C70/35-05 | ELE-DU-7007 |  |  | 1 | 1269 | B2-UPSP-64702-P2007 | 0.6/1kV CU/XLPE/LSZH | 4C x 70sqmm + 1C X 35sqmm | PE-L1-5C70/35-05 | 10 | 400 | U | 230 | DC & UPS | B2-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, N, PE | B2-UPSP-59702 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR STG #2 - B | 1.1_MAIN BUILDING COMPLEX (BLOCK #2 ST#2) | L1, L2, L3, N, PE | B264-016ET0061 → B264-016ET0248 → B264-016ET0062 → B264-006AC0012 → M0407 → D0302-L37 → M0302 → D0303-L37 → M0303 → D0305-L27 → M0306 → D0321-L27 → M0307 → D0306-L25 → M0308 → D0308-L15 → M0310 → D0309-L15 → M0311 → D0310-L25 → B259-006AT0017 → B259-006AT0016 → B259-006AT0015 → B259-006AT0014 → END
B2-DB-59602 | -P20 | 07 |  | PE-L1-3C4-25 | PE-L1-3C4-25 | ELE-DU-7008 |  |  | 1 | 1270 | B2-DB-59602-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-25 | 0.3 | 230 | N | 20 | DC & UPS | B2-DB-59602 | 400V-230V DIST. BOARD FOR ST #2 FOR BLOCK #2 - B | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | L1, N, PE | B2-UPSP-59701 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR STG #2 - A | 1.1_MAIN BUILDING COMPLEX (BLOCK #2 ST#2) | L1, N, PE | B259-006AT0005 → B259-006AT0014 → END
B2-ESWG-64601 | -P20 | 05 |  | PE-L1-1C240-05 | PE-L1-1C240-05 | ELE-DU-7009 |  |  | 1 | 1271 | B2-ESWG-64601-P2005 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-05 | 400 | 400 | E | 70 | DC & UPS | B2-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1 | B2-CH-64701 | BLOCK #2 BATTERY CHARGER - A | 1.3_LEB FOR BLOCK #2 | L1 | B264-016BT0030 → B264-016BT0029 → B264-996BT0012 → M0407 → B264-006AC0013 → B264-016DT0062 → B264-016DT0063 → END | [5 empty] | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B2-ESWG-64601 | -P20 | 06 |  | PE-L1-1C240-05 | PE-L1-1C240-05 |  |  |  | 1 | 1272 | B2-ESWG-64601-P2006 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-05 | 400 | 400 | E | 70 | DC & UPS | B2-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L2 | B2-CH-64701 | BLOCK #2 BATTERY CHARGER - A | 1.3_LEB FOR BLOCK #2 | L2 | B264-016BT0030 → B264-016BT0029 → B264-996BT0012 → M0407 → B264-006AC0013 → B264-016DT0062 → B264-016DT0063 → END | [5 empty] | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B2-ESWG-64601 | -P20 | 07 |  | PE-L1-1C240-05 | PE-L1-1C240-05 |  |  |  | 1 | 1273 | B2-ESWG-64601-P2007 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-05 | 400 | 400 | E | 70 | DC & UPS | B2-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L3 | B2-CH-64701 | BLOCK #2 BATTERY CHARGER - A | 1.3_LEB FOR BLOCK #2 | L3 | B264-016BT0030 → B264-016BT0029 → B264-996BT0012 → M0407 → B264-006AC0013 → B264-016DT0062 → B264-016DT0063 → END | [5 empty] | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B2-ESWG-64601 | -P20 | 08 |  | PE-L1-1C240-05 | PE-L1-1C240-05 |  |  |  | 1 | 1274 | B2-ESWG-64601-P2008 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-05 | 400 | 400 | E | 70 | DC & UPS | B2-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1 | B2-CH-64701 | BLOCK #2 BATTERY CHARGER - A | 1.3_LEB FOR BLOCK #2 | L1 | B264-016BT0030 → B264-016BT0029 → B264-996BT0012 → M0407 → B264-006AC0014 → B264-016DT0062 → B264-016DT0063 → END | [5 empty] | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B2-ESWG-64601 | -P20 | 09 |  | PE-L1-1C240-05 | PE-L1-1C240-05 |  |  |  | 1 | 1275 | B2-ESWG-64601-P2009 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-05 | 400 | 400 | E | 70 | DC & UPS | B2-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L2 | B2-CH-64701 | BLOCK #2 BATTERY CHARGER - A | 1.3_LEB FOR BLOCK #2 | L2 | B264-016BT0030 → B264-016BT0029 → B264-996BT0012 → M0407 → B264-006AC0014 → B264-016DT0062 → B264-016DT0063 → END | [5 empty] | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B2-ESWG-64601 | -P20 | 10 |  | PE-L1-1C240-05 | PE-L1-1C240-05 |  |  |  | 1 | 1276 | B2-ESWG-64601-P2010 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-05 | 400 | 400 | E | 70 | DC & UPS | B2-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L3 | B2-CH-64701 | BLOCK #2 BATTERY CHARGER - A | 1.3_LEB FOR BLOCK #2 | L3 | B264-016BT0030 → B264-016BT0029 → B264-996BT0012 → M0407 → B264-006AC0014 → B264-016DT0062 → B264-016DT0063 → END | [5 empty] | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B2-ESWG-64601 | -P20 | 11 |  | PE-L1-1C240-05 | PE-L1-1C240-05 |  |  |  | 1 | 1277 | B2-ESWG-64601-P2011 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-05 | 400 | 400 | E | 70 | DC & UPS | B2-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | N | B2-CH-64701 | BLOCK #2 BATTERY CHARGER - A | 1.3_LEB FOR BLOCK #2 | N | B264-016BT0030 → B264-016BT0029 → B264-996BT0012 → M0407 → B264-006AC0013 → B264-016DT0062 → B264-016DT0063 → END | [5 empty] | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B2-ESWG-64601 | -P20 | 12 |  | PE-L1-1C240-05 | PE-L1-1C240-05 |  |  |  | 1 | 1278 | B2-ESWG-64601-P2012 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-05 | 400 | 400 | E | 70 | DC & UPS | B2-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | PE | B2-CH-64701 | BLOCK #2 BATTERY CHARGER - A | 1.3_LEB FOR BLOCK #2 | PE | B264-016BT0030 → B264-016BT0029 → B264-996BT0012 → M0407 → B264-006AC0014 → B264-016DT0062 → B264-016DT0063 → END | [5 empty] | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B2-ESWG-64602 | -P20 | 05 |  | PE-L1-1C240-05 | PE-L1-1C240-05 | ELE-DU-7010 |  |  | 1 | 1279 | B2-ESWG-64602-P2005 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-05 | 400 | 400 | E | 70 | DC & UPS | B2-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1 | B2-CH-64702 | BLOCK #2 BATTERY CHARGER - B | 1.3_LEB FOR BLOCK #2 | L1 | B264-016CT0049 → B264-016CT0048 → B264-016CT0227 → B264-996CT0017 → M0407 → B264-006AC0006 → B264-016FT0062 → B264-016FT0063 → END | [5 empty] | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B2-ESWG-64602 | -P20 | 06 |  | PE-L1-1C240-05 | PE-L1-1C240-05 |  |  |  | 1 | 1280 | B2-ESWG-64602-P2006 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-05 | 400 | 400 | E | 70 | DC & UPS | B2-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L2 | B2-CH-64702 | BLOCK #2 BATTERY CHARGER - B | 1.3_LEB FOR BLOCK #2 | L2 | B264-016CT0049 → B264-016CT0048 → B264-016CT0227 → B264-996CT0017 → M0407 → B264-006AC0006 → B264-016FT0062 → B264-016FT0063 → END | [5 empty] | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B2-ESWG-64602 | -P20 | 07 |  | PE-L1-1C240-05 | PE-L1-1C240-05 |  |  |  | 1 | 1281 | B2-ESWG-64602-P2007 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-05 | 400 | 400 | E | 70 | DC & UPS | B2-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L3 | B2-CH-64702 | BLOCK #2 BATTERY CHARGER - B | 1.3_LEB FOR BLOCK #2 | L3 | B264-016CT0049 → B264-016CT0048 → B264-016CT0227 → B264-996CT0017 → M0407 → B264-006AC0006 → B264-016FT0062 → B264-016FT0063 → END | [5 empty] | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B2-ESWG-64602 | -P20 | 08 |  | PE-L1-1C240-05 | PE-L1-1C240-05 |  |  |  | 1 | 1282 | B2-ESWG-64602-P2008 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-05 | 400 | 400 | E | 70 | DC & UPS | B2-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1 | B2-CH-64702 | BLOCK #2 BATTERY CHARGER - B | 1.3_LEB FOR BLOCK #2 | L1 | B264-016CT0049 → B264-016CT0048 → B264-016CT0227 → B264-996CT0017 → M0407 → B264-006AC0007 → B264-016FT0062 → B264-016FT0063 → END | [5 empty] | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B2-ESWG-64602 | -P20 | 09 |  | PE-L1-1C240-05 | PE-L1-1C240-05 |  |  |  | 1 | 1283 | B2-ESWG-64602-P2009 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-05 | 400 | 400 | E | 70 | DC & UPS | B2-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L2 | B2-CH-64702 | BLOCK #2 BATTERY CHARGER - B | 1.3_LEB FOR BLOCK #2 | L2 | B264-016CT0049 → B264-016CT0048 → B264-016CT0227 → B264-996CT0017 → M0407 → B264-006AC0007 → B264-016FT0062 → B264-016FT0063 → END | [5 empty] | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B2-ESWG-64602 | -P20 | 10 |  | PE-L1-1C240-05 | PE-L1-1C240-05 |  |  |  | 1 | 1284 | B2-ESWG-64602-P2010 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-05 | 400 | 400 | E | 70 | DC & UPS | B2-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L3 | B2-CH-64702 | BLOCK #2 BATTERY CHARGER - B | 1.3_LEB FOR BLOCK #2 | L3 | B264-016CT0049 → B264-016CT0048 → B264-016CT0227 → B264-996CT0017 → M0407 → B264-006AC0007 → B264-016FT0062 → B264-016FT0063 → END | [5 empty] | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B2-ESWG-64602 | -P20 | 11 |  | PE-L1-1C240-05 | PE-L1-1C240-05 |  |  |  | 1 | 1285 | B2-ESWG-64602-P2011 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-05 | 400 | 400 | E | 70 | DC & UPS | B2-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | N | B2-CH-64702 | BLOCK #2 BATTERY CHARGER - B | 1.3_LEB FOR BLOCK #2 | N | B264-016CT0049 → B264-016CT0048 → B264-016CT0227 → B264-996CT0017 → M0407 → B264-006AC0006 → B264-016FT0062 → B264-016FT0063 → END | [5 empty] | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B2-ESWG-64602 | -P20 | 12 |  | PE-L1-1C240-05 | PE-L1-1C240-05 |  |  |  | 1 | 1286 | B2-ESWG-64602-P2012 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-05 | 400 | 400 | E | 70 | DC & UPS | B2-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | PE | B2-CH-64702 | BLOCK #2 BATTERY CHARGER - B | 1.3_LEB FOR BLOCK #2 | PE | B264-016CT0049 → B264-016CT0048 → B264-016CT0227 → B264-996CT0017 → M0407 → B264-006AC0007 → B264-016FT0062 → B264-016FT0063 → END | [5 empty] | Vendor |  |  | 1 | PPEO 0114-SR12 | 1
B2-DCP-64701 | -P20 | 21 |  | PE-L1-1C185-03 | PE-L1-1C185-03 | ELE-DU-7011 |  |  | 1 | 1287 | B2-DCP-64701-P2021 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-03 | 120 | 220 | D | 40 | DC & UPS | B2-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L+ | B2-UPS-64701 | BLOCK #2 UPS INVERTER - A | 1.3_LEB FOR BLOCK #2 | L+ | B264-016FT0063 → B264-016FT0247 → B264-016FT0061 → END
B2-DCP-64701 | -P20 | 22 |  | PE-L1-1C185-03 | PE-L1-1C185-03 |  |  |  | 1 | 1288 | B2-DCP-64701-P2022 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-03 | 120 | 220 | D | 40 | DC & UPS | B2-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L+ | B2-UPS-64701 | BLOCK #2 UPS INVERTER - A | 1.3_LEB FOR BLOCK #2 | L+ | B264-016FT0063 → B264-016FT0247 → B264-016FT0061 → END
B2-DCP-64701 | -P20 | 23 |  | PE-L1-1C185-03 | PE-L1-1C185-03 |  |  |  | 1 | 1289 | B2-DCP-64701-P2023 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-03 | 120 | 220 | D | 40 | DC & UPS | B2-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L- | B2-UPS-64701 | BLOCK #2 UPS INVERTER - A | 1.3_LEB FOR BLOCK #2 | L- | B264-016FT0063 → B264-016FT0247 → B264-016FT0061 → END
B2-DCP-64701 | -P20 | 24 |  | PE-L1-1C185-03 | PE-L1-1C185-03 |  |  |  | 1 | 1290 | B2-DCP-64701-P2024 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-03 | 120 | 220 | D | 40 | DC & UPS | B2-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L- | B2-UPS-64701 | BLOCK #2 UPS INVERTER - A | 1.3_LEB FOR BLOCK #2 | L- | B264-016FT0063 → B264-016FT0247 → B264-016FT0061 → END
B2-DCP-64702 | -P20 | 21 |  | PE-L1-1C185-03 | PE-L1-1C185-03 | ELE-DU-7012 |  |  | 1 | 1291 | B2-DCP-64702-P2021 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-03 | 120 | 220 | D | 40 | DC & UPS | B2-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L+ | B2-UPS-64702 | BLOCK #2 UPS INVERTER - B | 1.3_LEB FOR BLOCK #2 | L+ | B264-016ET0063 → B264-016ET0247 → B264-016ET0061 → END
B2-DCP-64702 | -P20 | 22 |  | PE-L1-1C185-03 | PE-L1-1C185-03 |  |  |  | 1 | 1292 | B2-DCP-64702-P2022 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-03 | 120 | 220 | D | 40 | DC & UPS | B2-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L+ | B2-UPS-64702 | BLOCK #2 UPS INVERTER - B | 1.3_LEB FOR BLOCK #2 | L+ | B264-016ET0063 → B264-016ET0247 → B264-016ET0061 → END
B2-DCP-64702 | -P20 | 23 |  | PE-L1-1C185-03 | PE-L1-1C185-03 |  |  |  | 1 | 1293 | B2-DCP-64702-P2023 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-03 | 120 | 220 | D | 40 | DC & UPS | B2-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L- | B2-UPS-64702 | BLOCK #2 UPS INVERTER - B | 1.3_LEB FOR BLOCK #2 | L- | B264-016ET0063 → B264-016ET0247 → B264-016ET0061 → END
B2-DCP-64702 | -P20 | 24 |  | PE-L1-1C185-03 | PE-L1-1C185-03 |  |  |  | 1 | 1294 | B2-DCP-64702-P2024 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-03 | 120 | 220 | D | 40 | DC & UPS | B2-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L- | B2-UPS-64702 | BLOCK #2 UPS INVERTER - B | 1.3_LEB FOR BLOCK #2 | L- | B264-016ET0063 → B264-016ET0247 → B264-016ET0061 → END
B2-EMCC-64601 | -P20 | 06 | 재배정 (10/6) | PE-L1-5C120/70-05 | PE-L1-5C120/70-03 | ELE-DU-7013 |  |  | 1 | 1295 | B2-EMCC-64601-P2006 | 0.6/1kV CU/XLPE/LSZH | 4C x 120sqmm + 1C X 70sqmm | PE-L1-5C120/70-03 | 120 | 400 | E | 70 | DC & UPS | B2-EMCC-64601 | 400V EMERGENCY MCC FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, N, PE | B2-AVR-64701 | BLOCK #2 UPS BYPASS LINE - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, N, PE | B264-016BT0030 → B264-016BT0029 → B264-996BT0012 → M0407 → B264-006AC0010 → B264-016DT0062 → B264-016DT0063 → END
B2-EMCC-64602 | -P20 | 05 | 재배정 (10/6) | PE-L1-5C120/70-05 | PE-L1-5C120/70-01 | ELE-DU-7014 |  |  | 1 | 1296 | B2-EMCC-64602-P2005 | 0.6/1kV CU/XLPE/LSZH | 4C x 120sqmm + 1C X 70sqmm | PE-L1-5C120/70-01 | 120 | 400 | E | 70 | DC & UPS | B2-EMCC-64602 | 400V EMERGENCY MCC FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, N, PE | B2-AVR-64702 | BLOCK #2 UPS BYPASS LINE - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, N, PE | B264-016CT0049 → B264-016CT0048 → B264-996CT0017 → M0407 → B264-006AC0011 → B264-016ET0062 → B264-016ET0063 → END
B2-DB-64602 | -P20 | 06 |  | PE-L1-3C4-25 | PE-L1-3C4-25 | ELE-DU-7015 |  |  | 1 | 1297 | B2-DB-64602-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-25 | 0.15 | 230 | N | 70 | DC & UPS | B2-DB-64602 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-FC-64701 | BLOCK #2 BATTERY FUSE BOX | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016BT0045 → B264-016BT0046 → B264-016BT0047 → B264-996BT0013 → M0407 → B264-016FT0062 → B264-016FT0248 → B264-016FT0060 → END
B2-UPSP-64701 | -P20 | 12 |  | PE-L1-5C120/70-06 | PE-L1-5C120/70-06 | ELE-DU-7016 |  |  | 1 | 1298 | B2-UPSP-64701-P2012 | 0.6/1kV CU/XLPE/LSZH | 4C x 120sqmm + 1C X 70sqmm | PE-L1-5C120/70-06 | 24 | 400 | U | 850 | DC & UPS | B2-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, N, PE | B2-UPSP-73701 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ADMIN. - BLOCK#2 - A | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / SERVER ROOM | L1, L2, L3, N, PE | B264-016DT0061 → B264-016DT0248 → B264-016DT0062 → B264-006AC0015 → M0407 → B025-016CT0106 → B025-016CT0105 → B025-016CT0104 → B025-016CT0103 → B025-016CT0102 → B025-016CT0101 → B025-016CT0100 → B025-016CT0099 → B025-016CT0098 → B025-016CT0097 → B025-016CT0096 → B025-016CT0095 → B025-016CT0094 → B025-016CT0093 → B164-016AT0263 → B164-016AT0115 → B164-016AT0114 → B164-016AT0217 → B164-016AT0090 → B164-016AT0216 → B164-016AT0215 → B164-016AT0055 → B164-016AT0056 → B164-016AT0057 → B164-016AT0058 → B164-016AT0059 → B164-016AT0060 → B164-016AT0254 → B164-016AT0253 → B164-016AT0123 → B164-016AT0313 → B164-016AT0314 → B064-016AC0002 → B064-006AC0026 → B064-016AC0010 → B073-007AT0102 → B073-007AT0104 → B073-007AT0106 → B073-007AT0108 → B073-007AT0001 → B073-007AT0003 → B073-007AT0006 → B073-007AT0007 → B073-997AT0009 → B073-997AT0021 → B073-017AT0001 → B073-017AT0014 → B073-017AT0015 → B073-017AT0013 → END
B2-UPSP-64702 | -P20 | 13 |  | PE-L1-5C120/70-07 | PE-L1-5C120/70-07 | ELE-DU-7017 | B2-UPSP-64702-P2013 |  | 1 | 1299 | B2-UPSP-64702-P2014 | 0.6/1kV CU/XLPE/LSZH | 4C x 120sqmm + 1C X 70sqmm | PE-L1-5C120/70-07 | 24 | 400 | U | 850 | DC & UPS | B2-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, L2, L3, N, PE | B2-UPSP-73702 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ADMIN. - BLOCK#2 - B | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / SERVER ROOM | L1, L2, L3, N, PE | B264-016DT0061 → B264-016DT0248 → B264-016DT0062 → B264-006AC0016 → M0407 → B025-016CT0106 → B025-016CT0105 → B025-016CT0104 → B025-016CT0103 → B025-016CT0102 → B025-016CT0101 → B025-016CT0100 → B025-016CT0099 → B025-016CT0098 → B025-016CT0097 → B025-016CT0096 → B025-016CT0095 → B025-016CT0094 → B025-016CT0093 → B164-016AT0263 → B164-016AT0115 → B164-016AT0114 → B164-016AT0217 → B164-016AT0090 → B164-016AT0216 → B164-016AT0215 → B164-016AT0055 → B164-016AT0056 → B164-016AT0057 → B164-016AT0058 → B164-016AT0059 → B164-016AT0060 → B164-016AT0254 → B164-016AT0253 → B164-016AT0123 → B164-016AT0313 → B164-016AT0314 → B064-016AC0003 → B064-006AC0027 → B064-016AC0011 → B073-007AT0102 → B073-007AT0104 → B073-007AT0106 → B073-007AT0108 → B073-007AT0001 → B073-007AT0003 → B073-007AT0006 → B073-007AT0007 → B073-997AT0009 → B073-997AT0021 → B073-017AT0001 → B073-017AT0014 → B073-017AT0015 → B073-017AT0013 → END
B0-DB-64601 | -P20 | 07 | 재배정 | PE-L1-3C4-15 | PE-L1-3C4-09 | ELE-DU-0001 |  | DONE | 1 | 1300 | B0-DB-64601-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-09 | 0.9 | 230 | N | 40 | DC & UPS | B0-DB-64601 | 400V-230V DIST. BOARD FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-CH-64701 | COMMON BATTERY CHARGER - A AUX. POWER | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0012 → B064-996AT0020 → M0501 → B064-006AC0020 → B064-006FT0005 → B064-006FT0207 → END
B0-DB-64601 | -P20 | 08 | 재배정 | PE-L1-3C4-16 | PE-L1-3C4-04 | ELE-DU-0002 |  | DONE | 1 | 1301 | B0-DB-64601-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-04 | 1.5 | 230 | N | 50 | DC & UPS | B0-DB-64601 | 400V-230V DIST. BOARD FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-UPS-64701 | COMMON UPS INVERTER - A AUX. POWER | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0012 → B064-996AT0020 → M0501 → B064-006AC0020 → B164-006GT0203 → B164-006GT0002 → B164-006GT0003 → END
B0-UPSP-64701 | -P20 | 08 |  | PE-L1-5C70/35-04 | PE-L1-5C70/35-04 | ELE-DU-0006 |  |  | 1 | 1302 | B0-UPSP-64701-P2008 | 0.6/1kV CU/XLPE/LSZH | 4C x 70sqmm + 1C X 35sqmm | PE-L1-5C70/35-04 | 13 | 400 | U | 490 | DC & UPS | B0-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B0-UPSP-69701 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ACC - A | 16_CEP BUILDING W/ACC LER | L1, L2, L3, N, PE | B164-006HT0205 → B164-006HT0004 → B164-006HT0005 → B064-006AC0005 → M0501 → D0503-L41 → M0502 → D0504-L41 → M0503 → D0501-L41 → M0328 → D0324-L41 → M0329 → B114-997AT0021 → B114-017AT0020 → B114-017AT0019 → B114-017AT0018 → B114-017AT0017 → B114-017AT0016 → B114-017AT0015 → B114-017AT0014 → B114-017AT0013 → B114-017AT0024 → B025-017BT0126 → B025-017BT0127 → B025-017BT0128 → B025-997BT0014 → M0105 → D0110-L24 → M0112 → D0111-L24 → M0113 → D0113-L44 → B169-007AT0044 → B169-007AT0004 → B169-007AT0005 → END
B0-UPSP-64702 | -P20 | 09 |  | PE-L1-5C70/35-03 | PE-L1-5C70/35-03 | ELE-DU-0007 |  |  | 1 | 1303 | B0-UPSP-64702-P2009 | 0.6/1kV CU/XLPE/LSZH | 4C x 70sqmm + 1C X 35sqmm | PE-L1-5C70/35-03 | 13 | 400 | U | 480 | DC & UPS | B0-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B0-UPSP-69702 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ACC - B | 16_CEP BUILDING W/ACC LER | L1, L2, L3, N, PE | B064-006FT0206 → B064-006FT0009 → B064-006FT0208 → B064-006FT0207 → B064-006FT0005 → B064-006AC0006 → M0501 → D0503-L36 → M0502 → D0504-L36 → M0503 → D0501-L36 → M0328 → D0324-L36 → M0329 → B114-996BT0046 → B114-016BT0045 → B114-016BT0044 → B114-016BT0043 → B114-016BT0042 → B114-016BT0041 → B114-016BT0040 → B114-016BT0039 → B114-016BT0038 → B215-016BT0023 → B025-016BT0123 → B025-016BT0124 → B025-016BT0125 → B025-996BT0013 → M0105 → D0110-L25 → M0112 → D0111-L25 → M0113 → D0113-L35 → B169-006AT0044 → B169-006AT0011 → B169-006AT0012 → END
B1-DB-69603 | -P20 | 17 |  | PE-L1-3C4-04 | PE-L1-3C4-04 | ELE-DU-0008 |  |  | 1 | 1304 | B1-DB-69603-P2017 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-04 | 0.3 | 230 | N | 60 | DC & UPS | B1-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B0-UPSP-69701 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ACC - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0015 → B169-006AT0053 → B169-006AT0009 → B169-006AT0010 → B169-006AT0011 → B169-006AT0012 → END
B0-ESWG-64601 | -P20 | 01 |  | PE-L1-1C185-03 | PE-L1-1C185-03 | ELE-DU-0009 |  | DONE | 1 | 1305 | B0-ESWG-64601-P2001 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-03 | 370 | 400 | E | 60 | DC & UPS | B0-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1 | B0-CH-64701 | COMMON BATTERY CHARGER - A | 1.2_LEB FOR BLOCK #1 | L1 | B064-016AT0015 → B064-016AT0014 → B064-016AT0232 → B064-016AT0034 → B064-016AT0033 → B064-996AT0120 → M0501 → B064-006AC0012 → B164-006JT0209 → END
B0-ESWG-64601 | -P20 | 02 |  | PE-L1-1C185-03 | PE-L1-1C185-03 |  |  | DONE | 1 | 1306 | B0-ESWG-64601-P2002 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-03 | 370 | 400 | E | 60 | DC & UPS | B0-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L2 | B0-CH-64701 | COMMON BATTERY CHARGER - A | 1.2_LEB FOR BLOCK #1 | L2 | B064-016AT0015 → B064-016AT0014 → B064-016AT0232 → B064-016AT0034 → B064-016AT0033 → B064-996AT0120 → M0501 → B064-006AC0012 → B164-006JT0209 → END
B0-ESWG-64601 | -P20 | 03 |  | PE-L1-1C185-03 | PE-L1-1C185-03 |  |  | DONE | 1 | 1307 | B0-ESWG-64601-P2003 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-03 | 370 | 400 | E | 60 | DC & UPS | B0-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L3 | B0-CH-64701 | COMMON BATTERY CHARGER - A | 1.2_LEB FOR BLOCK #1 | L3 | B064-016AT0015 → B064-016AT0014 → B064-016AT0232 → B064-016AT0034 → B064-016AT0033 → B064-996AT0120 → M0501 → B064-006AC0012 → B164-006JT0209 → END
B0-ESWG-64601 | -P20 | 04 |  | PE-L1-1C185-03 | PE-L1-1C185-03 |  |  | DONE | 1 | 1308 | B0-ESWG-64601-P2004 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-03 | 370 | 400 | E | 60 | DC & UPS | B0-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1 | B0-CH-64701 | COMMON BATTERY CHARGER - A | 1.2_LEB FOR BLOCK #1 | L1 | B064-016AT0015 → B064-016AT0014 → B064-016AT0232 → B064-016AT0034 → B064-016AT0033 → B064-996AT0120 → M0501 → B064-006AC0012 → B164-006JT0209 → END
B0-ESWG-64601 | -P20 | 05 |  | PE-L1-1C185-03 | PE-L1-1C185-03 |  |  | DONE | 1 | 1309 | B0-ESWG-64601-P2005 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-03 | 370 | 400 | E | 60 | DC & UPS | B0-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L2 | B0-CH-64701 | COMMON BATTERY CHARGER - A | 1.2_LEB FOR BLOCK #1 | L2 | B064-016AT0015 → B064-016AT0014 → B064-016AT0232 → B064-016AT0034 → B064-016AT0033 → B064-996AT0120 → M0501 → B064-006AC0012 → B164-006JT0209 → END
B0-ESWG-64601 | -P20 | 06 |  | PE-L1-1C185-03 | PE-L1-1C185-03 |  |  | DONE | 1 | 1310 | B0-ESWG-64601-P2006 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-03 | 370 | 400 | E | 60 | DC & UPS | B0-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L3 | B0-CH-64701 | COMMON BATTERY CHARGER - A | 1.2_LEB FOR BLOCK #1 | L3 | B064-016AT0015 → B064-016AT0014 → B064-016AT0232 → B064-016AT0034 → B064-016AT0033 → B064-996AT0120 → M0501 → B064-006AC0012 → B164-006JT0209 → END
B0-ESWG-64601 | -P20 | 07 |  | PE-L1-1C185-03 | PE-L1-1C185-03 |  |  | DONE | 1 | 1311 | B0-ESWG-64601-P2007 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-03 | 370 | 400 | E | 60 | DC & UPS | B0-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | N | B0-CH-64701 | COMMON BATTERY CHARGER - A | 1.2_LEB FOR BLOCK #1 | N | B064-016AT0015 → B064-016AT0014 → B064-016AT0232 → B064-016AT0034 → B064-016AT0033 → B064-996AT0120 → M0501 → B064-006AC0012 → B164-006JT0209 → END
B0-ESWG-64601 | -P20 | 08 |  | PE-L1-1C185-03 | PE-L1-1C185-03 |  |  | DONE | 1 | 1312 | B0-ESWG-64601-P2008 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-03 | 370 | 400 | E | 60 | DC & UPS | B0-ESWG-64601 | 400V EMERGENCY SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | PE | B0-CH-64701 | COMMON BATTERY CHARGER - A | 1.2_LEB FOR BLOCK #1 | PE | B064-016AT0015 → B064-016AT0014 → B064-016AT0232 → B064-016AT0034 → B064-016AT0033 → B064-996AT0120 → M0501 → B064-006AC0012 → B164-006JT0209 → END
B0-ESWG-64602 | -P20 | 01 |  | PE-L1-1C185-02 | PE-L1-1C185-02 | ELE-DU-0010 |  | DONE | 1 | 1313 | B0-ESWG-64602-P2001 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-02 | 370 | 400 | E | 90 | DC & UPS | B0-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1 | B0-CH-64702 | COMMON BATTERY CHARGER - B | 1.2_LEB FOR BLOCK #1 | L1 | B064-016CT0036 → B064-016CT0035 → B064-016CT0034 → B064-016CT0033 → B064-996CT0020 → M0501 → B064-006AC0013 → B064-006FT0003 → B064-006FT0205 → B064-006FT0206 → B064-006FT0009 → B064-006FT0208 → END
B0-ESWG-64602 | -P20 | 02 |  | PE-L1-1C185-04 | PE-L1-1C185-04 |  |  |  | 1 | 1314 | B0-ESWG-64602-P2002 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-04 | 370 | 400 | E | 90 | DC & UPS | B0-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L2 | B0-CH-64702 | COMMON BATTERY CHARGER - B | 1.2_LEB FOR BLOCK #1 | L2 | B064-016CT0036 → B064-016CT0035 → B064-016CT0034 → B064-016CT0033 → B064-996CT0020 → M0501 → B064-006AC0013 → B064-006FT0003 → B064-006FT0205 → B064-006FT0206 → B064-006FT0009 → B064-006FT0208 → END
B0-ESWG-64602 | -P20 | 03 |  | PE-L1-1C185-04 | PE-L1-1C185-04 |  |  | DONE | 1 | 1315 | B0-ESWG-64602-P2003 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-04 | 370 | 400 | E | 90 | DC & UPS | B0-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L3 | B0-CH-64702 | COMMON BATTERY CHARGER - B | 1.2_LEB FOR BLOCK #1 | L3 | B064-016CT0036 → B064-016CT0035 → B064-016CT0034 → B064-016CT0033 → B064-996CT0020 → M0501 → B064-006AC0013 → B064-006FT0003 → B064-006FT0205 → B064-006FT0206 → B064-006FT0009 → B064-006FT0208 → END
B0-ESWG-64602 | -P20 | 04 |  | PE-L1-1C185-04 | PE-L1-1C185-04 |  |  | DONE | 1 | 1316 | B0-ESWG-64602-P2004 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-04 | 370 | 400 | E | 90 | DC & UPS | B0-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1 | B0-CH-64702 | COMMON BATTERY CHARGER - B | 1.2_LEB FOR BLOCK #1 | L1 | B064-016CT0036 → B064-016CT0035 → B064-016CT0034 → B064-016CT0033 → B064-996CT0020 → M0501 → B064-006AC0013 → B064-006FT0003 → B064-006FT0205 → B064-006FT0206 → B064-006FT0009 → B064-006FT0208 → END
B0-ESWG-64602 | -P20 | 05 |  | PE-L1-1C185-04 | PE-L1-1C185-04 |  |  | DONE | 1 | 1317 | B0-ESWG-64602-P2005 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-04 | 370 | 400 | E | 90 | DC & UPS | B0-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L2 | B0-CH-64702 | COMMON BATTERY CHARGER - B | 1.2_LEB FOR BLOCK #1 | L2 | B064-016CT0036 → B064-016CT0035 → B064-016CT0034 → B064-016CT0033 → B064-996CT0020 → M0501 → B064-006AC0013 → B064-006FT0003 → B064-006FT0205 → B064-006FT0206 → B064-006FT0009 → B064-006FT0208 → END
B0-ESWG-64602 | -P20 | 06 |  | PE-L1-1C185-04 | PE-L1-1C185-04 |  |  |  | 1 | 1318 | B0-ESWG-64602-P2006 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-04 | 370 | 400 | E | 90 | DC & UPS | B0-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L3 | B0-CH-64702 | COMMON BATTERY CHARGER - B | 1.2_LEB FOR BLOCK #1 | L3 | B064-016CT0036 → B064-016CT0035 → B064-016CT0034 → B064-016CT0033 → B064-996CT0020 → M0501 → B064-006AC0013 → B064-006FT0003 → B064-006FT0205 → B064-006FT0206 → B064-006FT0009 → B064-006FT0208 → END
B0-ESWG-64602 | -P20 | 07 |  | PE-L1-1C185-04 | PE-L1-1C185-04 |  |  |  | 1 | 1319 | B0-ESWG-64602-P2007 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-04 | 370 | 400 | E | 90 | DC & UPS | B0-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | N | B0-CH-64702 | COMMON BATTERY CHARGER - B | 1.2_LEB FOR BLOCK #1 | N | B064-016CT0036 → B064-016CT0035 → B064-016CT0034 → B064-016CT0033 → B064-996CT0020 → M0501 → B064-006AC0013 → B064-006FT0003 → B064-006FT0205 → B064-006FT0206 → B064-006FT0009 → B064-006FT0208 → END
B0-ESWG-64602 | -P20 | 08 |  | PE-L1-1C185-04 | PE-L1-1C185-04 |  |  |  | 1 | 1320 | B0-ESWG-64602-P2008 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-04 | 370 | 400 | E | 90 | DC & UPS | B0-ESWG-64602 | 400V EMERGENCY SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | PE | B0-CH-64702 | COMMON BATTERY CHARGER - B | 1.2_LEB FOR BLOCK #1 | PE | B064-016CT0036 → B064-016CT0035 → B064-016CT0034 → B064-016CT0033 → B064-996CT0020 → M0501 → B064-006AC0013 → B064-006FT0003 → B064-006FT0205 → B064-006FT0206 → B064-006FT0009 → B064-006FT0208 → END
B0-DCP-64701 | -P20 | 14 |  | PE-L1-1C185-02 | PE-L1-1C185-02 | ELE-DU-0011 |  | DONE | 1 | 1321 | B0-DCP-64701-P2014 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-02 | 150 | 220 | D | 30 | DC & UPS | B0-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L+ | B0-UPS-64701 | COMMON UPS INVERTER - A | 1.2_LEB FOR BLOCK #1 | L+ | B164-006HT0207 → B164-006HT0004 → B164-006HT0205 → END
B0-DCP-64701 | -P20 | 15 |  | PE-L1-1C185-02 | PE-L1-1C185-02 |  |  | DONE | 1 | 1322 | B0-DCP-64701-P2015 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-02 | 150 | 220 | D | 30 | DC & UPS | B0-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L+ | B0-UPS-64701 | COMMON UPS INVERTER - A | 1.2_LEB FOR BLOCK #1 | L+ | B164-006HT0207 → B164-006HT0004 → B164-006HT0205 → END
B0-DCP-64701 | -P20 | 16 |  | PE-L1-1C185-02 | PE-L1-1C185-02 |  |  | DONE | 1 | 1323 | B0-DCP-64701-P2016 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-02 | 150 | 220 | D | 30 | DC & UPS | B0-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L- | B0-UPS-64701 | COMMON UPS INVERTER - A | 1.2_LEB FOR BLOCK #1 | L- | B164-006HT0207 → B164-006HT0004 → B164-006HT0205 → END
B0-DCP-64701 | -P20 | 17 |  | PE-L1-1C185-02 | PE-L1-1C185-02 |  |  | DONE | 1 | 1324 | B0-DCP-64701-P2017 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-02 | 150 | 220 | D | 30 | DC & UPS | B0-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L- | B0-UPS-64701 | COMMON UPS INVERTER - A | 1.2_LEB FOR BLOCK #1 | L- | B164-006HT0207 → B164-006HT0004 → B164-006HT0205 → END
B0-DCP-64702 | -P20 | 14 |  | PE-L1-1C185-02 | PE-L1-1C185-02 | ELE-DU-0012 |  | DONE | 1 | 1325 | B0-DCP-64702-P2014 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-02 | 150 | 220 | D | 30 | DC & UPS | B0-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L+ | B0-UPS-64702 | COMMON UPS INVERTER - B | 1.2_LEB FOR BLOCK #1 | L+ | B064-006FT0208 → B064-006FT0009 → B064-006FT0206 → END
B0-DCP-64702 | -P20 | 15 |  | PE-L1-1C185-02 | PE-L1-1C185-02 |  |  | DONE | 1 | 1326 | B0-DCP-64702-P2015 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-02 | 150 | 220 | D | 30 | DC & UPS | B0-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L+ | B0-UPS-64702 | COMMON UPS INVERTER - B | 1.2_LEB FOR BLOCK #1 | L+ | B064-006FT0208 → B064-006FT0009 → B064-006FT0206 → END
B0-DCP-64702 | -P20 | 16 |  | PE-L1-1C185-02 | PE-L1-1C185-02 |  |  | DONE | 1 | 1327 | B0-DCP-64702-P2016 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-02 | 150 | 220 | D | 30 | DC & UPS | B0-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L- | B0-UPS-64702 | COMMON UPS INVERTER - B | 1.2_LEB FOR BLOCK #1 | L- | B064-006FT0208 → B064-006FT0009 → B064-006FT0206 → END
B0-DCP-64702 | -P20 | 17 |  | PE-L1-1C185-02 | PE-L1-1C185-02 |  |  | DONE | 1 | 1328 | B0-DCP-64702-P2017 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-02 | 150 | 220 | D | 30 | DC & UPS | B0-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L- | B0-UPS-64702 | COMMON UPS INVERTER - B | 1.2_LEB FOR BLOCK #1 | L- | B064-006FT0208 → B064-006FT0009 → B064-006FT0206 → END
B0-EMCC-64601 | -P20 | 04 | 재배정 | PE-L1-5C150/95-03 | PE-L1-5C150/95-02 | ELE-DU-0013 | DONE(10/27) | DONE | 1 | 1329 | B0-EMCC-64601-P2004 | 0.6/1kV CU/XLPE/LSZH | 4C x 150sqmm + 1C X 95sqmm | PE-L1-5C150/95-02 | 150 | 400 | E | 80 | DC & UPS | B0-EMCC-64601 | 400V EMERGENCY MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B0-AVR-64701 | COMMON UPS BYPASS LINE - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B064-016AT0016 → B064-016AT0015 → B064-016AT0014 → B064-016AT0232 → B064-016AT0034 → B064-016AT0033 → B064-996AT0120 → M0501 → B064-006AC0020 → B064-006FT0003 → B064-006FT0205 → END
B0-EMCC-64602 | -P20 | 03 |  | PE-L1-5C150/95-03 | PE-L1-5C150/95-03 | ELE-DU-0014 | DONE(9/28) | DONE | 1 | 1330 | B0-EMCC-64602-P2003 | 0.6/1kV CU/XLPE/LSZH | 4C x 150sqmm + 1C X 95sqmm | PE-L1-5C150/95-03 | 150 | 400 | E | 80 | DC & UPS | B0-EMCC-64602 | 400V EMERGENCY MCC FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B0-AVR-64702 | COMMON UPS BYPASS LINE - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, N, PE | B064-016CT0036 → B064-016CT0035 → B064-016CT0034 → B064-016CT0033 → B064-996CT0020 → M0501 → B064-006AC0021 → B164-006HT0006 → B164-006HT0209 → B164-006HT0210 → B164-006HT0010 → B164-006HT0009 → B164-006HT0206 → END
B0-DB-64601 | -P20 | 09 | 재배정 | PE-L1-3C4-05 | PE-L1-3C4-17 | ELE-DU-0015 |  |  | 1 | 1331 | B0-DB-64601-P2009 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-17 | 0.15 | 230 | N | 50 | DC & UPS | B0-DB-64601 | 400V-230V DIST. BOARD FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-FC-64701 | COMMON BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0012 → B064-996AT0020 → M0501 → B064-006AC0020 → B164-006HT0005 → B164-006HT0207 → B164-006HT0208 → B164-006HT0009 → END
B0-DCP-64701 | -P20 | 18 |  | PE-L1-1C500-33 | PE-L1-1C500-33 | ELE-DU-0016 |  |  | 1 | 1332 | B0-DCP-64701-P2018 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-33 | 31 | 220 | D | 480 | DC & UPS | B0-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L+ | B0-DCP-69701 | 220V DC LOCAL DISTRIBUTION PANEL FOR ACC - A | 16_CEP BUILDING W/ACC LER | L+ | B164-006HT0207 → B164-006HT0005 → B064-006AC0003 → M0501 → D0503-L42 → M0502 → D0504-L42 → M0503 → D0501-L42 → M0328 → D0324-L42 → M0329 → B114-997AT0021 → B114-017AT0020 → B114-017AT0019 → B114-017AT0018 → B114-017AT0017 → B114-017AT0016 → B114-017AT0015 → B114-017AT0014 → B114-017AT0013 → B114-017AT0024 → B025-017BT0126 → B025-017BT0127 → B025-017BT0128 → B025-997BT0014 → M0105 → D0110-L31 → M0112 → D0111-L24 → M0113 → D0113-L44 → B169-007AT0044 → B169-007AT0004 → B169-007AT0005 → END
B0-DCP-64701 | -P20 | 19 |  | PE-L1-1C500-34 | PE-L1-1C500-34 |  |  |  | 1 | 1333 | B0-DCP-64701-P2019 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-34 | 31 | 220 | D | 480 | DC & UPS | B0-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L- | B0-DCP-69701 | 220V DC LOCAL DISTRIBUTION PANEL FOR ACC - A | 16_CEP BUILDING W/ACC LER | L- | B164-006HT0207 → B164-006HT0005 → B064-006AC0003 → M0501 → D0503-L42 → M0502 → D0504-L42 → M0503 → D0501-L42 → M0328 → D0324-L42 → M0329 → B114-997AT0021 → B114-017AT0020 → B114-017AT0019 → B114-017AT0018 → B114-017AT0017 → B114-017AT0016 → B114-017AT0015 → B114-017AT0014 → B114-017AT0013 → B114-017AT0024 → B025-017BT0126 → B025-017BT0127 → B025-017BT0128 → B025-997BT0014 → M0105 → D0110-L31 → M0112 → D0111-L24 → M0113 → D0113-L44 → B169-007AT0044 → B169-007AT0004 → B169-007AT0005 → END
B0-DCP-64702 | -P20 | 18 |  | PE-L1-1C500-35 | PE-L1-1C500-35 | ELE-DU-0017 |  |  | 1 | 1334 | B0-DCP-64702-P2018 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-35 | 31 | 220 | D | 470 | DC & UPS | B0-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L+ | B0-DCP-69702 | 220V DC LOCAL DISTRIBUTION PANEL FOR ACC - B | 16_CEP BUILDING W/ACC LER | L+ | B164-006JT0210 → B164-006JT0209 → B164-006JT0006 → B064-006AC0004 → M0501 → D0503-L42 → M0502 → D0504-L42 → M0503 → D0501-L42 → M0328 → D0324-L42 → M0329 → B114-996BT0046 → B114-016BT0045 → B114-016BT0044 → B114-016BT0043 → B114-016BT0042 → B114-016BT0041 → B114-016BT0040 → B114-016BT0039 → B114-016BT0038 → B215-016BT0023 → B025-016BT0123 → B025-016BT0124 → B025-016BT0125 → B025-996BT0013 → M0105 → D0110-L32 → M0112 → D0111-L32 → M0113 → D0113-L32 → B169-006AT0044 → B169-006AT0011 → B169-006AT0012 → END
B0-DCP-64702 | #REF! | 19 |  | PE-L1-1C500-36 | PE-L1-1C500-36 |  |  |  | 1 | 1335 | B0-DCP-64702-P2019 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-36 | 31 | 220 | D | 470 | DC & UPS | B0-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L- | B0-DCP-69702 | 220V DC LOCAL DISTRIBUTION PANEL FOR ACC - B | 16_CEP BUILDING W/ACC LER | L- | B164-006JT0210 → B164-006JT0209 → B164-006JT0006 → B064-006AC0004 → M0501 → D0503-L42 → M0502 → D0504-L42 → M0503 → D0501-L42 → M0328 → D0324-L42 → M0329 → B114-996BT0046 → B114-016BT0045 → B114-016BT0044 → B114-016BT0043 → B114-016BT0042 → B114-016BT0041 → B114-016BT0040 → B114-016BT0039 → B114-016BT0038 → B215-016BT0023 → B025-016BT0123 → B025-016BT0124 → B025-016BT0125 → B025-996BT0013 → M0105 → D0110-L32 → M0112 → D0111-L32 → M0113 → D0113-L32 → B169-006AT0044 → B169-006AT0011 → B169-006AT0012 → END
B1-DB-69601 | -P20 | 19 |  | PE-L1-3C4-16 | PE-L1-3C4-16 | ELE-DU-0018 |  |  | 1 | 1336 | B1-DB-69601-P2019 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-16 | 0.3 | 230 | N | 60 | DC & UPS | B1-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B0-DCP-69701 | 220V DC LOCAL DISTRIBUTION PANEL FOR ACC - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0015 → B169-006AT0053 → B169-006AT0009 → B169-006AT0010 → B169-006AT0011 → B169-006AT0012 → END
B1-DCP-64701 | -P20 | 27 |  | PE-L1-2C4-02 | PE-L1-2C4-02 | ELE-PRP-1001 |  | DONE | 1 | 1337 | B1-DCP-64701-P2027 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-02 | 1.02 | 220 | D | 120 | PROTECTION | B1-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-PRP-64701 | BLOCK #1 PROTECTION RELAY PANEL FOR GSUT GTG #1 | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006GT0203 → B164-006GT0002 → B164-006GT0003 → B064-006AC0018 → M0501 → B064-996GT0020 → B064-016GT0033 → B064-016GT0229 → B064-016GT0230 → B064-016GT0047 → B064-016GT0048 → B064-016GT0239 → B064-996GT0013 → B064-996GT0053 → B064-996GT0073 → B064-037AT0214 → B064-037AT0039 → B064-037AT0040 → B064-037AT0041 → B064-037AT0228 → B064-037AT0227 → B064-037AT0031 → END
B1-DCP-64702 | -P20 | 27 |  | PE-L1-2C4-02 | PE-L1-2C4-02 | ELE-PRP-1002 |  | DONE | 1 | 1338 | B1-DCP-64702-P2027 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-02 | 1.02 | 220 | D | 120 | PROTECTION | B1-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-PRP-64701 | BLOCK #1 PROTECTION RELAY PANEL FOR GSUT GTG #1 | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0204 → B164-006HT0008 → B164-006HT0009 → B164-006HT0010 → B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0023 → M0501 → B064-996AT0020 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0014 → B064-036AT0015 → B064-036AT0016 → B064-036AT0217 → B064-036AT0218 → B064-036AT0219 → B064-036AT0030 → B064-036AT0031 → END
B1-DB-64601 | -P20 | 08 | 재배정 | PE-L1-3C4-16 | PE-L1-3C4-04 | ELE-PRP-1003 |  | DONE | 1 | 1339 | B1-DB-64601-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-04 | 0.12 | 230 | N | 130 | PROTECTION | B1-DB-64601 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-PRP-64701 | BLOCK #1 PROTECTION RELAY PANEL FOR GSUT GTG #1 | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0090 → B064-016AT0216 → B064-016AT0215 → B064-016AT0214 → B064-016AT0213 → B064-016AT0212 → B064-016AT0011 → B064-016AT0012 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0014 → B064-036AT0015 → B064-036AT0016 → B064-036AT0217 → B064-036AT0218 → B064-036AT0219 → B064-036AT0030 → B064-036AT0031 → END
B1-DCP-64701 | -P20 | 28 |  | PE-L1-2C4-02 | PE-L1-2C4-02 | ELE-PRP-1004 |  | DONE | 1 | 1340 | B1-DCP-64701-P2028 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-02 | 0.51 | 220 | D | 120 | PROTECTION | B1-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-PRP-64702 | BLOCK #1 PROTECTION RELAY PANEL FOR UAT GTG #1 | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006GT0203 → B164-006GT0002 → B164-006GT0003 → B064-006AC0019 → M0501 → B064-996GT0020 → B064-016CT0033 → B064-016GT0229 → B064-016GT0230 → B064-016GT0047 → B064-016GT0048 → B064-016GT0239 → B064-996GT0013 → B064-996GT0053 → B064-996GT0073 → B064-037AT0214 → B064-037AT0039 → B064-037AT0040 → B064-037AT0041 → B064-037AT0228 → B064-037AT0227 → B064-037AT0031 → END
B1-DCP-64702 | -P20 | 28 |  | PE-L1-2C4-02 | PE-L1-2C4-02 | ELE-PRP-1005 |  | DONE | 1 | 1341 | B1-DCP-64702-P2028 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-02 | 0.51 | 220 | D | 120 | PROTECTION | B1-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-PRP-64702 | BLOCK #1 PROTECTION RELAY PANEL FOR UAT GTG #1 | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0204 → B164-006HT0008 → B164-006HT0009 → B164-006HT0010 → B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0023 → M0501 → B064-996AT0020 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0014 → B064-036AT0015 → B064-036AT0016 → B064-036AT0217 → B064-036AT0218 → B064-036AT0219 → B064-036AT0030 → B064-036AT0031 → END
B1-DB-64602 | -P20 | 12 |  | PE-L1-3C4-10 | PE-L1-3C4-10 | ELE-PRP-1006 |  | DONE | 1 | 1342 | B1-DB-64602-P2012 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-10 | 0.12 | 230 | N | 140 | PROTECTION | B1-DB-64602 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-PRP-64702 | BLOCK #1 PROTECTION RELAY PANEL FOR UAT GTG #1 | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0106 → B064-016AT0217 → B064-016AT0090 → B064-016AT0216 → B064-016AT0215 → B064-016AT0214 → B064-016AT0213 → B064-016AT0212 → B064-016AT0011 → B064-016AT0012 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0014 → B064-036AT0015 → B064-036AT0016 → B064-036AT0217 → B064-036AT0218 → B064-036AT0219 → B064-036AT0030 → B064-036AT0031 → END
B1-DCP-64702 | -P20 | 29 |  | PE-L1-2C4-02 | PE-L1-2C4-02 | ELE-PRP-1007 |  | DONE | 1 | 1343 | B1-DCP-64702-P2029 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-02 | 0.51 | 220 | D | 130 | PROTECTION | B1-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-PRP-64703 | BLOCK #1 PROTECTION RELAY PANEL FOR OVERALL GTG #1 | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0204 → B164-006HT0008 → B164-006HT0009 → B164-006HT0010 → B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0018 → M0501 → B064-996GT0020 → B064-016CT0033 → B064-016GT0229 → B064-016GT0230 → B064-016GT0047 → B064-016GT0048 → B064-016GT0239 → B064-996GT0013 → B064-996GT0053 → B064-996GT0073 → B064-037AT0214 → B064-037AT0039 → B064-037AT0040 → B064-037AT0041 → B064-037AT0228 → B064-037AT0227 → B064-037AT0031 → END
B1-DCP-64701 | -P20 | 29 |  | PE-L1-2C4-02 | PE-L1-2C4-02 | ELE-PRP-1008 |  | DONE | 1 | 1344 | B1-DCP-64701-P2029 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-02 | 0.51 | 220 | D | 110 | PROTECTION | B1-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-PRP-64703 | BLOCK #1 PROTECTION RELAY PANEL FOR OVERALL GTG #1 | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006GT0203 → B164-006GT0002 → B164-006GT0003 → B064-006AC0023 → M0501 → B064-996AT0020 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0014 → B064-036AT0015 → B064-036AT0016 → B064-036AT0217 → B064-036AT0218 → B064-036AT0219 → B064-036AT0030 → B064-036AT0031 → END
B1-DB-64602 | -P20 | 13 | 재배정 | PE-L1-3C4-16 | PE-L1-3C4-04 | ELE-PRP-1009 |  | DONE | 1 | 1345 | B1-DB-64602-P2013 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-04 | 0.12 | 230 | N | 140 | PROTECTION | B1-DB-64602 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-PRP-64703 | BLOCK #1 PROTECTION RELAY PANEL FOR OVERALL GTG #1 | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0106 → B064-016AT0217 → B064-016AT0090 → B064-016AT0216 → B064-016AT0215 → B064-016AT0214 → B064-016AT0213 → B064-016AT0212 → B064-016AT0011 → B064-016AT0012 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0014 → B064-036AT0015 → B064-036AT0016 → B064-036AT0217 → B064-036AT0218 → B064-036AT0219 → B064-036AT0030 → B064-036AT0031 → END
B1-DCP-64702 | -P20 | 30 |  | PE-L1-2C4-02 | PE-L1-2C4-02 | ELE-PRP-2001 |  | DONE | 1 | 1346 | B1-DCP-64702-P2030 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-02 | 1.02 | 220 | D | 120 | PROTECTION | B1-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-PRP-64704 | BLOCK #1 PROTECTION RELAY PANEL FOR GSUT GTG #2 | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0204 → B164-006HT0008 → B164-006HT0009 → B164-006HT0010 → B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0019 → M0501 → B064-996GT0020 → B064-016CT0033 → B064-016GT0229 → B064-016GT0230 → B064-016GT0047 → B064-016GT0048 → B064-016GT0239 → B064-996GT0013 → B064-996GT0053 → B064-996GT0073 → B064-037AT0214 → B064-037AT0039 → B064-037AT0040 → B064-037AT0041 → B064-037AT0228 → B064-037AT0035 → END
B1-DCP-64701 | -P20 | 30 |  | PE-L1-2C4-03 | PE-L1-2C4-03 | ELE-PRP-2002 |  | DONE | 1 | 1347 | B1-DCP-64701-P2030 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-03 | 1.02 | 220 | D | 110 | PROTECTION | B1-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-PRP-64704 | BLOCK #1 PROTECTION RELAY PANEL FOR GSUT GTG #2 | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006GT0203 → B164-006GT0002 → B164-006GT0003 → B064-006AC0023 → M0501 → B064-996AT0020 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0014 → B064-036AT0015 → B064-036AT0016 → B064-036AT0217 → B064-036AT0218 → B064-036AT0219 → B064-036AT0220 → B064-036AT0034 → B064-036AT0035 → END
B1-DB-64604 | -P20 | 09 | 재배정 | PE-L1-3C4-16 | PE-L1-3C4-04 | ELE-PRP-2003 |  | DONE | 1 | 1348 | B1-DB-64604-P2009 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-04 | 0.12 | 230 | N | 170 | PROTECTION | B1-DB-64604 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-PRP-64704 | BLOCK #1 PROTECTION RELAY PANEL FOR GSUT GTG #2 | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0111 → B064-016AT0296 → B064-016AT0094 → B064-016AT0278 → B064-016AT0277 → B064-016AT0067 → B064-016AT0068 → B064-016AT0290 → B064-016AT0240 → B064-016AT0049 → B064-016AT0048 → B064-016AT0234 → B064-016AT0233 → B064-016AT0232 → B064-016AT0013 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0014 → B064-036AT0015 → B064-036AT0016 → B064-036AT0217 → B064-036AT0218 → B064-036AT0219 → B064-036AT0220 → B064-036AT0034 → B064-036AT0035 → END
B1-DCP-64701 | -P20 | 31 |  | PE-L1-2C4-04 | PE-L1-2C4-04 | ELE-PRP-2004 |  | DONE | 1 | 1349 | B1-DCP-64701-P2031 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-04 | 0.51 | 220 | D | 110 | PROTECTION | B1-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-PRP-64705 | BLOCK #1 PROTECTION RELAY PANEL FOR UAT GTG #2 | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006GT0203 → B164-006GT0002 → B164-006GT0003 → B064-006AC0023 → M0501 → B064-996GT0020 → B064-016CT0033 → B064-016GT0229 → B064-016GT0230 → B064-016GT0047 → B064-016GT0048 → B064-016GT0239 → B064-996GT0013 → B064-996GT0053 → B064-996GT0073 → B064-037AT0214 → B064-037AT0039 → B064-037AT0040 → B064-037AT0041 → B064-037AT0228 → B064-037AT0035 → END
B1-DCP-64702 | -P20 | 31 |  | PE-L1-2C4-04 | PE-L1-2C4-04 | ELE-PRP-2005 |  | DONE | 1 | 1350 | B1-DCP-64702-P2031 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-04 | 0.51 | 220 | D | 120 | PROTECTION | B1-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-PRP-64705 | BLOCK #1 PROTECTION RELAY PANEL FOR UAT GTG #2 | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0204 → B164-006HT0008 → B164-006HT0009 → B164-006HT0010 → B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0024 → M0501 → B064-996AT0020 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0014 → B064-036AT0015 → B064-036AT0016 → B064-036AT0217 → B064-036AT0218 → B064-036AT0219 → B064-036AT0220 → B064-036AT0034 → B064-036AT0035 → END
B1-DB-64603 | -P20 | 10 | 재배정 | PE-L1-3C4-16 | PE-L1-3C4-04 | ELE-PRP-2006 |  | DONE | 1 | 1351 | B1-DB-64603-P2010 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-04 | 0.12 | 230 | N | 160 | PROTECTION | B1-DB-64603 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-PRP-64705 | BLOCK #1 PROTECTION RELAY PANEL FOR UAT GTG #2 | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0095 → B064-016AT0094 → B064-016AT0278 → B064-016AT0277 → B064-016AT0067 → B064-016AT0068 → B064-016AT0290 → B064-016AT0240 → B064-016AT0049 → B064-016AT0048 → B064-016AT0234 → B064-016AT0233 → B064-016AT0232 → B064-016AT0013 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0014 → B064-036AT0015 → B064-036AT0016 → B064-036AT0217 → B064-036AT0218 → B064-036AT0219 → B064-036AT0220 → B064-036AT0034 → B064-036AT0035 → END
B1-DCP-64702 | -P20 | 32 |  | PE-L1-2C4-04 | PE-L1-2C4-04 | ELE-PRP-2007 |  | DONE | 1 | 1352 | B1-DCP-64702-P2032 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-04 | 0.51 | 220 | D | 120 | PROTECTION | B1-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-PRP-64706 | BLOCK #1 PROTECTION RELAY PANEL FOR OVERALL GTG #2 | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0204 → B164-006HT0008 → B164-006HT0009 → B164-006HT0010 → B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0024 → M0501 → B064-996GT0020 → B064-016CT0033 → B064-016GT0229 → B064-016GT0230 → B064-016GT0047 → B064-016GT0048 → B064-016GT0239 → B064-996GT0013 → B064-996GT0053 → B064-996GT0073 → B064-037AT0214 → B064-037AT0039 → B064-037AT0040 → B064-037AT0041 → B064-037AT0228 → B064-037AT0035 → END
B1-DCP-64701 | -P20 | 32 |  | PE-L1-2C4-04 | PE-L1-2C4-04 | ELE-PRP-2008 |  | DONE | 1 | 1353 | B1-DCP-64701-P2032 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-04 | 0.51 | 220 | D | 110 | PROTECTION | B1-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-PRP-64706 | BLOCK #1 PROTECTION RELAY PANEL FOR OVERALL GTG #2 | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006GT0203 → B164-006GT0002 → B164-006GT0003 → B064-006AC0022 → M0501 → B064-996AT0020 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0014 → B064-036AT0015 → B064-036AT0016 → B064-036AT0217 → B064-036AT0218 → B064-036AT0219 → B064-036AT0220 → B064-036AT0034 → B064-036AT0035 → END
B1-DB-64603 | -P20 | 11 | 재배정 | PE-L1-3C4-16 | PE-L1-3C4-04 | ELE-PRP-2009 |  | DONE | 1 | 1354 | B1-DB-64603-P2011 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-04 | 0.12 | 230 | N | 160 | PROTECTION | B1-DB-64603 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-PRP-64706 | BLOCK #1 PROTECTION RELAY PANEL FOR OVERALL GTG #2 | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0095 → B064-016AT0094 → B064-016AT0278 → B064-016AT0277 → B064-016AT0067 → B064-016AT0068 → B064-016AT0290 → B064-016AT0240 → B064-016AT0049 → B064-016AT0048 → B064-016AT0234 → B064-016AT0233 → B064-016AT0232 → B064-016AT0013 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0014 → B064-036AT0015 → B064-036AT0016 → B064-036AT0217 → B064-036AT0218 → B064-036AT0219 → B064-036AT0220 → B064-036AT0034 → B064-036AT0035 → END
B2-DCP-64701 | -P20 | 25 |  | PE-L1-2C4-05 | PE-L1-2C4-05 | ELE-PRP-3001 |  |  | 1 | 1355 | B2-DCP-64701-P2025 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-05 | 1.02 | 220 | D | 100 | PROTECTION | B2-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-PRP-64701 | BLOCK #2 PROTECTION RELAY PANEL FOR GSUT GTG #1 | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-016FT0063 → B264-016FT0062 → B264-006AC0009 → M0407 → B264-996AT0013 → B264-016AT0048 → B264-016AT0049 → B264-016AT0050 → B264-016AT0240 → B264-016AT0055 → B264-016AT0056 → B264-016AT0057 → B264-016AT0244 → END
B2-DCP-64702 | -P20 | 25 |  | PE-L1-2C4-05 | PE-L1-2C4-05 | ELE-PRP-3002 |  |  | 1 | 1356 | B2-DCP-64702-P2025 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-05 | 1.02 | 220 | D | 100 | PROTECTION | B2-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-PRP-64701 | BLOCK #2 PROTECTION RELAY PANEL FOR GSUT GTG #1 | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-017ET0063 → B264-017ET0062 → B264-006AC0010 → M0407 → B264-996BT0013 → B264-016BT0048 → B264-016BT0049 → B264-016BT0050 → B264-016BT0240 → B264-016BT0055 → B264-016BT0056 → B264-016BT0057 → B264-016BT0244 → END
B2-DB-64601 | -P20 | 12 |  | PE-L1-3C4-21 | PE-L1-3C4-21 | ELE-PRP-3003 |  |  | 1 | 1357 | B2-DB-64601-P2012 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-21 | 0.12 | 230 | N | 90 | PROTECTION | B2-DB-64601 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-PRP-64701 | BLOCK #2 PROTECTION RELAY PANEL FOR GSUT GTG #1 | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016AT0024 → B264-016AT0025 → B264-016AT0026 → B264-016AT0027 → B264-016AT0028 → B264-016AT0029 → B264-016AT0030 → B264-016AT0031 → B264-016AT0032 → B264-016AT0033 → B264-016AT0034 → B264-016AT0244 → END
B2-DCP-64701 | -P20 | 26 |  | PE-L1-2C4-05 | PE-L1-2C4-05 | ELE-PRP-3004 |  |  | 1 | 1358 | B2-DCP-64701-P2026 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-05 | 0.51 | 220 | D | 100 | PROTECTION | B2-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-PRP-64702 | BLOCK #2 PROTECTION RELAY PANEL FOR UAT GTG #1 | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-017ET0063 → B264-017ET0062 → B264-006AC0015 → M0407 → B264-996AT0013 → B264-016AT0048 → B264-016AT0049 → B264-016AT0050 → B264-016AT0240 → B264-016AT0055 → B264-016AT0056 → B264-016AT0057 → B264-016AT0244 → END
B2-DCP-64702 | -P20 | 26 |  | PE-L1-2C4-05 | PE-L1-2C4-05 | ELE-PRP-3005 |  |  | 1 | 1359 | B2-DCP-64702-P2026 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-05 | 0.51 | 220 | D | 100 | PROTECTION | B2-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-PRP-64702 | BLOCK #2 PROTECTION RELAY PANEL FOR UAT GTG #1 | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-016FT0063 → B264-016FT0062 → B264-006AC0016 → M0407 → B264-996BT0013 → B264-016BT0048 → B264-016BT0049 → B264-016BT0050 → B264-016BT0240 → B264-016BT0055 → B264-016BT0056 → B264-016BT0057 → B264-016BT0244 → END
B2-DB-64601 | -P20 | 13 |  | PE-L1-3C4-21 | PE-L1-3C4-21 | ELE-PRP-3006 |  |  | 1 | 1360 | B2-DB-64601-P2013 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-21 | 0.12 | 230 | N | 90 | PROTECTION | B2-DB-64601 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-PRP-64702 | BLOCK #2 PROTECTION RELAY PANEL FOR UAT GTG #1 | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016BT0024 → B264-016BT0025 → B264-016BT0026 → B264-016BT0027 → B264-016BT0028 → B264-016BT0029 → B264-016BT0030 → B264-016BT0031 → B264-016BT0032 → B264-016BT0033 → B264-016BT0034 → B264-016BT0244 → END
B2-DCP-64702 | -P20 | 27 |  | PE-L1-2C4-05 | PE-L1-2C4-05 | ELE-PRP-3007 |  |  | 1 | 1361 | B2-DCP-64702-P2027 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-05 | 0.51 | 220 | D | 100 | PROTECTION | B2-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-PRP-64703 | BLOCK #2 PROTECTION RELAY PANEL FOR OVERALL GTG #1 | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-016FT0063 → B264-016FT0062 → B264-006AC0015 → M0407 → B264-996BT0013 → B264-016BT0048 → B264-016BT0049 → B264-016BT0050 → B264-016BT0240 → B264-016BT0055 → B264-016BT0056 → B264-016BT0057 → B264-016BT0244 → END
B2-DCP-64701 | -P20 | 27 |  | PE-L1-2C4-05 | PE-L1-2C4-05 | ELE-PRP-3008 |  |  | 1 | 1362 | B2-DCP-64701-P2027 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-05 | 0.51 | 220 | D | 100 | PROTECTION | B2-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-PRP-64703 | BLOCK #2 PROTECTION RELAY PANEL FOR OVERALL GTG #1 | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-016DT0063 → B264-016DT0062 → B264-006AC0016 → M0407 → B264-996AT0013 → B264-016AT0048 → B264-016AT0049 → B264-016AT0050 → B264-016AT0240 → B264-016AT0055 → B264-016AT0056 → B264-016AT0057 → B264-016AT0244 → END
B2-DB-64601 | -P20 | 14 |  | PE-L1-3C4-28 | PE-L1-3C4-28 | ELE-PRP-3009 |  |  | 1 | 1363 | B2-DB-64601-P2014 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-28 | 0.12 | 230 | N | 90 | PROTECTION | B2-DB-64601 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-PRP-64703 | BLOCK #2 PROTECTION RELAY PANEL FOR OVERALL GTG #1 | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016AT0024 → B264-016AT0025 → B264-016AT0026 → B264-016AT0027 → B264-016AT0028 → B264-016AT0029 → B264-016AT0030 → B264-016AT0031 → B264-016AT0032 → B264-016AT0033 → B264-016AT0034 → B264-016AT0244 → END
B2-DCP-64702 | -P20 | 28 |  | PE-L1-2C4-10 | PE-L1-2C4-10 | ELE-PRP-4001 |  |  | 1 | 1364 | B2-DCP-64702-P2028 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-10 | 1.02 | 220 | D | 100 | PROTECTION | B2-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-PRP-64704 | BLOCK #2 PROTECTION RELAY PANEL FOR GSUT GTG #2 | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-016FT0063 → B264-016FT0062 → B264-006AC0016 → M0407 → B264-996BT0013 → B264-016BT0048 → B264-016BT0049 → B264-016BT0050 → B264-016BT0240 → B264-016BT0055 → B264-016BT0056 → B264-016BT0057 → B264-016BT0058 → B264-016BT0245 → END
B2-DCP-64701 | -P20 | 28 |  | PE-L1-2C4-10 | PE-L1-2C4-10 | ELE-PRP-4002 |  |  | 1 | 1365 | B2-DCP-64701-P2028 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-10 | 1.02 | 220 | D | 100 | PROTECTION | B2-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-PRP-64704 | BLOCK #2 PROTECTION RELAY PANEL FOR GSUT GTG #2 | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-016DT0063 → B264-016DT0062 → B264-006AC0015 → M0407 → B264-996AT0013 → B264-016AT0048 → B264-016AT0049 → B264-016AT0050 → B264-016AT0240 → B264-016AT0055 → B264-016AT0056 → B264-016AT0057 → B264-016AT0058 → B264-016AT0245 → END
B2-DB-64604 | -P20 | 09 |  | PE-L1-3C4-06 | PE-L1-3C4-06 | ELE-PRP-4003 |  |  | 1 | 1366 | B2-DB-64604-P2009 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-06 | 0.12 | 230 | N | 70 | PROTECTION | B2-DB-64604 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-PRP-64704 | BLOCK #2 PROTECTION RELAY PANEL FOR GSUT GTG #2 | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016BT0047 → B264-016BT0048 → B264-016BT0049 → B264-016BT0050 → B264-016BT0240 → B264-016BT0055 → B264-016BT0056 → B264-016BT0057 → B264-016BT0058 → B264-016BT0245 → END
B2-DCP-64701 | -P20 | 29 |  | PE-L1-2C4-10 | PE-L1-2C4-10 | ELE-PRP-4004 |  |  | 1 | 1367 | B2-DCP-64701-P2029 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-10 | 0.51 | 220 | D | 100 | PROTECTION | B2-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-PRP-64705 | BLOCK #2 PROTECTION RELAY PANEL FOR UAT GTG #2 | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-016DT0063 → B264-016DT0062 → B264-006AC0005 → M0407 → B264-996AT0013 → B264-016AT0048 → B264-016AT0049 → B264-016AT0050 → B264-016AT0240 → B264-016AT0055 → B264-016AT0056 → B264-016AT0057 → B264-016AT0058 → B264-016AT0245 → END
B2-DCP-64702 | -P20 | 29 |  | PE-L1-2C4-05 | PE-L1-2C4-05 | ELE-PRP-4005 |  |  | 1 | 1368 | B2-DCP-64702-P2029 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-05 | 0.51 | 220 | D | 100 | PROTECTION | B2-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-PRP-64705 | BLOCK #2 PROTECTION RELAY PANEL FOR UAT GTG #2 | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-016FT0063 → B264-016FT0062 → B264-006AC0006 → M0407 → B264-996BT0013 → B264-016BT0048 → B264-016BT0049 → B264-016BT0050 → B264-016BT0240 → B264-016BT0055 → B264-016BT0056 → B264-016BT0057 → B264-016BT0058 → B264-016BT0245 → END
B2-DB-64603 | -P20 | 12 |  | PE-L1-3C4-04 | PE-L1-3C4-04 | ELE-PRP-4006 |  |  | 1 | 1369 | B2-DB-64603-P2012 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-04 | 0.12 | 230 | N | 70 | PROTECTION | B2-DB-64603 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-PRP-64705 | BLOCK #2 PROTECTION RELAY PANEL FOR UAT GTG #2 | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016AT0027 → B264-016AT0028 → B264-016AT0029 → B264-016AT0030 → B264-016AT0031 → B264-016AT0032 → B264-016AT0033 → B264-016AT0034 → B264-016AT0035 → B264-016AT0245 → END
B2-DCP-64702 | -P20 | 30 |  | PE-L1-2C4-10 | PE-L1-2C4-10 | ELE-PRP-4007 |  |  | 1 | 1370 | B2-DCP-64702-P2030 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-10 | 0.51 | 220 | D | 100 | PROTECTION | B2-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-PRP-64706 | BLOCK #2 PROTECTION RELAY PANEL FOR OVERALL GTG #2 | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-016FT0063 → B264-016FT0062 → B264-006AC0008 → M0407 → B264-996BT0013 → B264-016BT0048 → B264-016BT0049 → B264-016BT0050 → B264-016BT0240 → B264-016BT0055 → B264-016BT0056 → B264-016BT0057 → B264-016BT0058 → B264-016BT0245 → END
B2-DCP-64701 | -P20 | 30 |  | PE-L1-2C4-10 | PE-L1-2C4-10 | ELE-PRP-4008 |  |  | 1 | 1371 | B2-DCP-64701-P2030 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-10 | 0.51 | 220 | D | 100 | PROTECTION | B2-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-PRP-64706 | BLOCK #2 PROTECTION RELAY PANEL FOR OVERALL GTG #2 | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-016DT0063 → B264-016DT0062 → B264-006AC0008 → M0407 → B264-996AT0013 → B264-016AT0048 → B264-016AT0049 → B264-016AT0050 → B264-016AT0240 → B264-016AT0055 → B264-016AT0056 → B264-016AT0057 → B264-016AT0058 → B264-016AT0245 → END
B2-DB-64603 | -P20 | 13 |  | PE-L1-3C4-04 | PE-L1-3C4-04 | ELE-PRP-4009 |  |  | 1 | 1372 | B2-DB-64603-P2013 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-04 | 0.12 | 230 | N | 70 | PROTECTION | B2-DB-64603 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-PRP-64706 | BLOCK #2 PROTECTION RELAY PANEL FOR OVERALL GTG #2 | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016AT0027 → B264-016AT0028 → B264-016AT0029 → B264-016AT0030 → B264-016AT0031 → B264-016AT0032 → B264-016AT0033 → B264-016AT0034 → B264-016AT0035 → B264-016AT0245 → END
B1-DCP-64702 | -P20 | 33 |  | PE-L1-2C6-01 | PE-L1-2C6-01 | ELE-PRP-5001 |  | DONE | 1 | 1373 | B1-DCP-64702-P2033 | 0.6/1kV CU/XLPE/LSZH | 2C x 6sqmm | PE-L1-2C6-01 | 1.02 | 220 | D | 120 | PROTECTION | B1-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-PRP-64707 | BLOCK #1 PROTECTION RELAY PANEL FOR GSUT STG | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006GT0204 → B164-006GT0203 → B164-006GT0002 → B164-006GT0003 → B064-006AC0003 → M0501 → B064-996GT0020 → B064-016GT0033 → B064-016GT0229 → B064-016GT0230 → B064-016GT0047 → B064-016GT0048 → B064-016GT0239 → B064-996GT0013 → B064-996GT0053 → B064-996GT0073 → B064-037AT0214 → B064-037AT0039 → B064-037AT0040 → B064-037AT0041 → B064-037AT0228 → B064-037AT0035 → B064-037AT0034 → END
B1-DCP-64701 | -P20 | 33 |  | PE-L1-2C6-02 | PE-L1-2C6-02 | ELE-PRP-5002 |  | DONE | 1 | 1374 | B1-DCP-64701-P2033 | 0.6/1kV CU/XLPE/LSZH | 2C x 6sqmm | PE-L1-2C6-02 | 1.02 | 220 | D | 110 | PROTECTION | B1-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-PRP-64707 | BLOCK #1 PROTECTION RELAY PANEL FOR GSUT STG | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0203 → B164-006HT0002 → B164-006HT0003 → B064-006AC0003 → M0501 → B064-996AT0020 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0014 → B064-036AT0015 → B064-036AT0016 → B064-036AT0217 → B064-036AT0218 → B064-036AT0219 → B064-036AT0220 → B064-036AT0034 → END
B1-DB-64603 | -P20 | 12 | 재배정 | PE-L1-3C4-16 | PE-L1-3C4-04 | ELE-PRP-5003 |  | DONE | 1 | 1375 | B1-DB-64603-P2012 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-04 | 0.12 | 230 | N | 160 | PROTECTION | B1-DB-64603 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-PRP-64707 | BLOCK #1 PROTECTION RELAY PANEL FOR GSUT STG | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0095 → B064-016AT0094 → B064-016AT0278 → B064-016AT0277 → B064-016AT0067 → B064-016AT0068 → B064-016AT0290 → B064-016AT0240 → B064-016AT0049 → B064-016AT0048 → B064-016AT0234 → B064-016AT0233 → B064-016AT0232 → B064-016AT0013 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0014 → B064-036AT0015 → B064-036AT0016 → B064-036AT0217 → B064-036AT0218 → B064-036AT0219 → B064-036AT0220 → B064-036AT0034 → END
B1-DCP-64702 | -P20 | 34 |  | PE-L1-2C4-03 | PE-L1-2C4-03 | ELE-PRP-5004 |  | DONE | 1 | 1376 | B1-DCP-64702-P2034 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-03 | 0.51 | 220 | D | 120 | PROTECTION | B1-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-PRP-64708 | BLOCK #1 PROTECTION RELAY PANEL FOR OVERALL STG | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006GT0204 → B164-006GT0203 → B164-006GT0002 → B164-006GT0003 → B064-006AC0003 → M0501 → B064-996GT0020 → B064-016GT0033 → B064-016GT0229 → B064-016GT0230 → B064-016GT0047 → B064-016GT0048 → B064-016GT0239 → B064-996GT0013 → B064-996GT0053 → B064-996GT0073 → B064-037AT0214 → B064-037AT0039 → B064-037AT0040 → B064-037AT0041 → B064-037AT0228 → B064-037AT0035 → B064-037AT0034 → END
B1-DCP-64701 | -P20 | 34 |  | PE-L1-2C4-03 | PE-L1-2C4-03 | ELE-PRP-5005 |  | DONE | 1 | 1377 | B1-DCP-64701-P2034 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-03 | 0.51 | 220 | D | 110 | PROTECTION | B1-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B1-PRP-64708 | BLOCK #1 PROTECTION RELAY PANEL FOR OVERALL STG | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0203 → B164-006HT0002 → B164-006HT0003 → B064-006AC0003 → M0501 → B064-996AT0020 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0014 → B064-036AT0015 → B064-036AT0016 → B064-036AT0217 → B064-036AT0218 → B064-036AT0219 → B064-036AT0220 → B064-036AT0034 → END
B1-DB-64603 | -P20 | 13 | 재배정 | PE-L1-3C4-16 | PE-L1-3C4-04 | ELE-PRP-5006 |  | DONE | 1 | 1378 | B1-DB-64603-P2013 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-04 | 0.12 | 230 | N | 160 | PROTECTION | B1-DB-64603 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-PRP-64708 | BLOCK #1 PROTECTION RELAY PANEL FOR OVERALL STG | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0095 → B064-016AT0094 → B064-016AT0278 → B064-016AT0277 → B064-016AT0067 → B064-016AT0068 → B064-016AT0290 → B064-016AT0240 → B064-016AT0049 → B064-016AT0048 → B064-016AT0234 → B064-016AT0233 → B064-016AT0232 → B064-016AT0013 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0014 → B064-036AT0015 → B064-036AT0016 → B064-036AT0217 → B064-036AT0218 → B064-036AT0219 → B064-036AT0220 → B064-036AT0034 → END
B2-DCP-64702 | -P20 | 31 |  | PE-L1-2C6-02 | PE-L1-2C6-02 | ELE-PRP-6001 |  |  | 1 | 1379 | B2-DCP-64702-P2031 | 0.6/1kV CU/XLPE/LSZH | 2C x 6sqmm | PE-L1-2C6-02 | 1.02 | 220 | D | 90 | PROTECTION | B2-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-PRP-64707 | BLOCK #2 PROTECTION RELAY PANEL FOR GSUT STG | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-016ET0063 → B264-016ET0062 → B264-006AC0001 → M0407 → B264-996AT0012 → B264-016AT0029 → B264-016AT0030 → B264-016AT0031 → B264-016AT0032 → B264-016AT0033 → B264-016AT0034 → B264-016AT0035 → B264-016AT0036 → END
B2-DCP-64701 | -P20 | 31 |  | PE-L1-2C6-02 | PE-L1-2C6-02 | ELE-PRP-6002 |  |  | 1 | 1380 | B2-DCP-64701-P2031 | 0.6/1kV CU/XLPE/LSZH | 2C x 6sqmm | PE-L1-2C6-02 | 1.02 | 220 | D | 80 | PROTECTION | B2-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-PRP-64707 | BLOCK #2 PROTECTION RELAY PANEL FOR GSUT STG | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-017ET0063 → B264-017ET0062 → B264-006AC0001 → M0407 → B264-996BT0012 → B264-016BT0030 → B264-016BT0031 → B264-016BT0032 → B264-016BT0033 → B264-016BT0034 → B264-016BT0035 → B264-016BT0036 → END
B2-DB-64603 | -P20 | 14 |  | PE-L1-3C4-21 | PE-L1-3C4-21 | ELE-PRP-6003 |  |  | 1 | 1381 | B2-DB-64603-P2014 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-21 | 0.12 | 230 | N | 60 | PROTECTION | B2-DB-64603 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-PRP-64707 | BLOCK #2 PROTECTION RELAY PANEL FOR GSUT STG | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016BT0027 → B264-016BT0028 → B264-016BT0029 → B264-016BT0030 → B264-016BT0031 → B264-016BT0032 → B264-016BT0033 → B264-016BT0034 → B264-016BT0035 → B264-016BT0036 → END
B2-DCP-64702 | -P20 | 32 |  | PE-L1-2C4-10 | PE-L1-2C4-10 | ELE-PRP-6004 |  |  | 1 | 1382 | B2-DCP-64702-P2032 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-10 | 0.51 | 220 | D | 80 | PROTECTION | B2-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-PRP-64708 | BLOCK #2 PROTECTION RELAY PANEL FOR OVERALL STG | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-016DT0063 → B264-016DT0062 → B264-006AC0001 → M0407 → B264-996AT0012 → B264-016AT0030 → B264-016AT0031 → B264-016AT0032 → B264-016AT0033 → B264-016AT0034 → B264-016AT0035 → B264-016AT0036 → END
B2-DCP-64701 | -P20 | 32 |  | PE-L1-2C4-10 | PE-L1-2C4-10 | ELE-PRP-6005 |  |  | 1 | 1383 | B2-DCP-64701-P2032 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-10 | 0.51 | 220 | D | 100 | PROTECTION | B2-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L+, L- | B2-PRP-64708 | BLOCK #2 PROTECTION RELAY PANEL FOR OVERALL STG | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-017ET0063 → B264-017ET0062 → B264-006AC0001 → M0407 → B264-996BT0012 → B264-016BT0030 → B264-016BT0031 → B264-016BT0032 → B264-016BT0033 → B264-016BT0034 → B264-016BT0035 → B264-016BT0036 → END → B264-016BT0031 → B264-016BT0032 → B264-016BT0033 → B264-016BT0034 → B264-016BT0035 → B264-016BT0036 → END
B2-DB-64603 | -P20 | 15 |  | PE-L1-3C4-21 | PE-L1-3C4-21 | ELE-PRP-6006 |  |  | 1 | 1384 | B2-DB-64603-P2015 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-21 | 0.12 | 230 | N | 60 | PROTECTION | B2-DB-64603 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-PRP-64708 | BLOCK #2 PROTECTION RELAY PANEL FOR OVERALL STG | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016BT0027 → B264-016BT0028 → B264-016BT0029 → B264-016BT0030 → B264-016BT0031 → B264-016BT0032 → B264-016BT0033 → B264-016BT0034 → B264-016BT0035 → B264-016BT0036 → END
B0-DCP-64702 | -P20 | 22 |  | PE-L1-2C4-04 | PE-L1-2C4-04 | ELE-PRP-7001 |  | DONE | 1 | 1385 | B0-DCP-64702-P2022 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-04 | 0.51 | 220 | D | 110 | PROTECTION | B0-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L+, L- | B0-PRP-64701 | PROTECTION RELAY PANEL FOR BACK UP TRANSFORMER | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0022 → M0501 → B064-996GT0020 → B064-016CT0033 → B064-016GT0229 → B064-016GT0230 → B064-016GT0047 → B064-016GT0048 → B064-016GT0239 → B064-996GT0013 → B064-996GT0053 → B064-996GT0073 → B064-037AT0214 → B064-037AT0039 → B064-037AT0040 → B064-037AT0041 → B064-037AT0228 → B064-037AT0227 → B064-037AT0031 → END
B0-DCP-64701 | -P20 | 22 |  | PE-L1-2C4-04 | PE-L1-2C4-04 | ELE-PRP-7002 |  | DONE | 1 | 1386 | B0-DCP-64701-P2022 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-04 | 0.51 | 220 | D | 100 | PROTECTION | B0-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L+, L- | B0-PRP-64701 | PROTECTION RELAY PANEL FOR BACK UP TRANSFORMER | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006GT0207 → B164-006GT0005 → B064-006AC0022 → M0501 → B064-996AT0020 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0014 → B064-036AT0015 → B064-036AT0016 → B064-036AT0217 → B064-036AT0218 → B064-036AT0219 → B064-036AT0030 → END
B0-DB-64602 | -P20 | 08 | 재배정 | PE-L1-3C4-16 | PE-L1-3C4-04 | ELE-PRP-7003 |  | DONE | 1 | 1387 | B0-DB-64602-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-04 | 0.12 | 230 | N | 100 | PROTECTION | B0-DB-64602 | 400V-230V DIST. BOARD FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-PRP-64701 | PROTECTION RELAY PANEL FOR BACK UP TRANSFORMER | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0032 → B064-016AT0033 → B064-016AT0034 → B064-016AT0232 → B064-016AT0013 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0205 → B064-036AT0024 → B064-036AT0025 → END
B1-UPSP-64701 | -P20 | 09 | 재배정 | PE-L1-3C4-16 | PE-L1-3C4-04 | ELE-FMS-1001 |  | DONE | 1 | 1388 | B1-UPSP-64701-P2009 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-04 | 0.22 | 230 | U | 80 | FMS | B1-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-PMCS-64701 | SUB HUB PANEL FOR BLOCK #1 MAIN | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B164-006GT0201 → B164-006GT0001 → B164-006GT0002 → B164-006GT0003 → B064-006AC0016 → M0501 → B064-996AT0120 → B064-016AT0032 → B064-016AT0213 → B064-016AT0214 → B064-016AT0063 → END
B1-UPSP-64702 | -P20 | 08 | 재배정 Route 확인 | PE-L1-3C4-16 | PE-L1-3C4-04 | ELE-FMS-1002 |  | DONE | 1 | 1389 | B1-UPSP-64702-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-04 | 0.22 | 230 | U | 90 | FMS | B1-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-PMCS-64701 | SUB HUB PANEL FOR BLOCK #1 MAIN | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B164-006HT0202 → B164-006HT0201 → B164-006HT0001 → B164-006HT0002 → B164-006HT0003 → B064-006AC0017 → M0501 → B064-996AT0020 → B064-016AT0012 → B064-016AT0011 → B064-016AT0212 → B064-016AT0213 → B064-016AT0214 → END | B164-006HT0202 → B164-006HT0201 → B164-006HT0001 → B164-006HT0002 → B164-006HT0003 → B064-006AC0017 → M0501 → B064-996GT0020 → B064-016GT0033 → B064-016GT0229 → B064-016GT0230 → B064-016GT0047 → B064-016GT0048 → B064-016GT0239 → B064-016GT0053 → B064-016GT0275 → B064-016GT0276 → B064-016GT0066 → B064-006AC0050 → END
B1-DB-64601 | -P20 | 09 | 재배정 | PE-L1-3C4-16 | PE-L1-3C4-06 | ELE-FMS-1003 |  | DONE | 1 | 1390 | B1-DB-64601-P2009 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-06 | 0.04 | 230 | N | 40 | FMS | B1-DB-64601 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-PMCS-64701 | SUB HUB PANEL FOR BLOCK #1 MAIN | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0217 → B064-016AT0090 → B064-016AT0216 → B064-016AT0215 → END
B1-UPSP-64702 | -P20 | 09 | 재배정 Route 확인 | PE-L1-3C4-16 | PE-L1-3C4-04 | ELE-FMS-1004 |  | DONE | 1 | 1391 | B1-UPSP-64702-P2009 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-04 | 0.22 | 230 | U | 90 | FMS | B1-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-PMCS-64702 | SUB HUB PANEL FOR BLOCK #1 BACK UP | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B164-006HT0202 → B164-006HT0201 → B164-006HT0001 → B164-006HT0002 → B164-006HT0003 → B064-006AC0017 → M0501 → B064-996AT0120 → B064-016AT0032 → B064-016AT0213 → B064-016AT0214 → B064-016AT0063 → END | B164-006HT0202 → B164-006HT0201 → B164-006HT0001 → B164-006HT0002 → B164-006HT0003 → B064-006AC0017 → M0501 → B064-996AT0120 → B064-016AT0032 → B064-016AT0213 → B064-016AT0214 → END
B1-UPSP-64701 | -P20 | 10 | 재배정 Route 확인 | PE-L1-3C4-16 | PE-L1-3C4-04 | ELE-FMS-1005 |  | DONE | 1 | 1392 | B1-UPSP-64701-P2010 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-04 | 0.22 | 230 | U | 80 | FMS | B1-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-PMCS-64702 | SUB HUB PANEL FOR BLOCK #1 BACK UP | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B164-006GT0201 → B164-006GT0001 → B164-006GT0002 → B164-006GT0003 → B064-006AC0016 → M0501 → B064-996AT0020 → B064-016AT0012 → B064-016AT0011 → B064-016AT0212 → B064-016AT0213 → B064-016AT0214 → END | B164-006GT0201 → B164-006GT0001 → B164-006GT0002 → B164-006GT0003 → B064-006AC0016 → M0501 → B064-996GT0020 → B064-016GT0033 → B064-016GT0229 → B064-016GT0230 → B064-016GT0047 → B064-016GT0048 → B064-016GT0239 → B064-016GT0053 → B064-016GT0275 → B064-016GT0276 → B064-016GT0066 → B064-006AC0050 → END
B1-DB-64603 | -P20 | 14 | 재배정 | PE-L1-3C4-16 | PE-L1-3C4-06 | ELE-FMS-1006 |  | DONE | 1 | 1393 | B1-DB-64603-P2014 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-06 | 0.04 | 230 | N | 60 | FMS | B1-DB-64603 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B1-PMCS-64702 | SUB HUB PANEL FOR BLOCK #1 BACK UP | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0095 → B064-016AT0094 → B064-016AT0278 → B064-016AT0277 → B064-016AT0066 → B064-016AT0065 → B064-016AT0064 → B064-016AT0063 → END
B0-UPSP-69701 | -P20 | 05 |  | PE-L1-3C4-16 | PE-L1-3C4-16 | ELE-FMS-1007 |  |  | 1 | 1394 | B0-UPSP-69701-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-16 | 0.22 | 230 | U | 60 | FMS | B0-UPSP-69701 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ACC - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-PMCS-69701 | SUB HUB PANEL FOR BLOCK #1 ACC | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006BT0054 → B169-006BT0018 → B169-006BT0017 → B169-006BT0016 → B169-006BT0031 → END
B0-UPSP-69702 | -P20 | 05 |  | PE-L1-3C4-16 | PE-L1-3C4-16 | ELE-FMS-1008 |  |  | 1 | 1395 | B0-UPSP-69702-P2005 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-16 | 0.22 | 230 | U | 50 | FMS | B0-UPSP-69702 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ACC - B | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-PMCS-69701 | SUB HUB PANEL FOR BLOCK #1 ACC | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0012 → B169-006AT0011 → B169-006AT0010 → B169-006AT0009 → B169-006AT0008 → END
B1-DB-69603 | -P20 | 18 |  | PE-L1-3C4-16 | PE-L1-3C4-16 | ELE-FMS-1009 |  |  | 1 | 1396 | B1-DB-69603-P2018 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-16 | 0.04 | 230 | N | 30 | FMS | B1-DB-69603 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #1 - C | 16_CEP BUILDING W/ACC LER | L1, N, PE | B1-PMCS-69701 | SUB HUB PANEL FOR BLOCK #1 ACC | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0009 → B169-006AT0008 → END
B2-UPSP-64701 | -P20 | 09 |  | PE-L1-3C4-04 | PE-L1-3C4-04 | ELE-FMS-2001 |  |  | 1 | 1397 | B2-UPSP-64701-P2009 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-04 | 0.22 | 230 | U | 90 | FMS | B2-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-PMCS-64701 | SUB HUB PANEL FOR BLOCK #2 MAIN | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016DT0061 → B264-016DT0060 → B264-006AC0001 → M0405 → B264-996AT0011 → B264-016AT0014 → B264-016AT0211 → B264-016AT0008 → B264-016AT0007 → END
B2-UPSP-64702 | -P20 | 08 |  | PE-L1-3C4-04 | PE-L1-3C4-04 | ELE-FMS-2002 |  |  | 1 | 1398 | B2-UPSP-64702-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-04 | 0.22 | 230 | U | 90 | FMS | B2-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-PMCS-64701 | SUB HUB PANEL FOR BLOCK #2 MAIN | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016ET0061 → B264-016ET0060 → B264-006AC0002 → M0405 → B264-016CT0209 → B264-016BT0014 → B264-016BT0211 → B264-016BT0008 → B264-016BT0007 → END
B2-DB-64601 | -P20 | 15 |  | PE-L1-3C4-04 | PE-L1-3C4-04 | ELE-FMS-2003 |  |  | 1 | 1399 | B2-DB-64601-P2015 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-04 | 0.04 | 230 | N | 30 | FMS | B2-DB-64601 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-PMCS-64701 | SUB HUB PANEL FOR BLOCK #2 MAIN | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016BT0024 → B264-016BT0204 → B264-016BT0203 → END
B2-UPSP-64702 | -P20 | 09 | 재배정 | PE-L1-3C4-04 | PE-L1-3C4-13 | ELE-FMS-2004 |  |  | 1 | 1400 | B2-UPSP-64702-P2009 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-13 | 0.22 | 230 | U | 90 | FMS | B2-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-PMCS-64702 | SUB HUB PANEL FOR BLOCK #2 BACK UP | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016ET0061 → B264-016ET0060 → B264-006AC0003 → M0405 → B264-016CT0209 → B264-016BT0014 → B264-016BT0211 → B264-016BT0008 → B264-016BT0007 → END
B2-UPSP-64701 | -P20 | 10 | 재배정 | PE-L1-3C4-04 | PE-L1-3C4-13 | ELE-FMS-2005 |  |  | 1 | 1401 | B2-UPSP-64701-P2010 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-13 | 0.22 | 230 | U | 90 | FMS | B2-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-PMCS-64702 | SUB HUB PANEL FOR BLOCK #2 BACK UP | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016DT0061 → B264-016DT0060 → B264-006AC0001 → M0405 → B264-996AT0011 → B264-016AT0014 → B264-016AT0211 → B264-016AT0008 → B264-016AT0007 → END
B2-DB-64603 | -P20 | 17 | 재배정 | PE-L1-3C4-04 | PE-L1-3C4-13 | ELE-FMS-2006 |  |  | 1 | 1402 | B2-DB-64603-P2017 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-13 | 0.04 | 230 | N | 50 | FMS | B2-DB-64603 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B2-PMCS-64702 | SUB HUB PANEL FOR BLOCK #2 BACK UP | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016BT0027 → B264-016BT0026 → B264-016BT0025 → B264-016BT0024 → B264-016BT0204 → B264-016BT0203 → END
B0-UPSP-69702 | -P20 | 06 |  | PE-L1-3C4-16 | PE-L1-3C4-16 | ELE-FMS-2007 |  |  | 1 | 1403 | B0-UPSP-69702-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-16 | 0.22 | 230 | U | 20 | FMS | B0-UPSP-69702 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ACC - B | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-PMCS-69701 | SUB HUB PANEL FOR BLOCK #2 ACC | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-007AT0005 → END
B0-UPSP-69701 | -P20 | 06 |  | PE-L1-3C4-17 | PE-L1-3C4-17 | ELE-FMS-2008 |  |  | 1 | 1404 | B0-UPSP-69701-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-17 | 0.22 | 230 | U | 20 | FMS | B0-UPSP-69701 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ACC - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-PMCS-69701 | SUB HUB PANEL FOR BLOCK #2 ACC | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0012 → END
B2-DB-69601 | -P20 | 19 |  | PE-L1-3C4-27 | PE-L1-3C4-27 | ELE-FMS-2009 |  |  | 1 | 1405 | B2-DB-69601-P2019 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-27 | 0.04 | 230 | N | 40 | FMS | B2-DB-69601 | 400V-230V DIST. BOARD FOR ACC#1 FOR BLOCK #2 - A | 16_CEP BUILDING W/ACC LER | L1, N, PE | B2-PMCS-69701 | SUB HUB PANEL FOR BLOCK #2 ACC | 16_CEP BUILDING W/ACC LER | L1, N, PE | B169-006AT0021 → B169-006AT0020 → B169-006AT0033 → END
B1-UPSP-59702 | -P20 | 04 |  | PE-L1-3C4-17 | PE-L1-3C4-17 | ELE-FMS-3001 |  |  | 1 | 1406 | B1-UPSP-59702-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-17 | 0.11 | 230 | U | 30 | FMS | B1-UPSP-59702 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR STG #1 - B | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-PMCS-59701 | SUB HUB PANEL FOR STG | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B159-006AT0003 → END
B1-UPSP-59701 | -P20 | 04 |  | PE-L1-3C4-17 | PE-L1-3C4-17 | ELE-FMS-3002 |  |  | 1 | 1407 | B1-UPSP-59701-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-17 | 0.11 | 230 | U | 20 | FMS | B1-UPSP-59701 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR STG #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-PMCS-59701 | SUB HUB PANEL FOR STG | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B159-006BT0003 → END
B1-DB-59601 | -P20 | 20 |  | PE-L1-3C4-17 | PE-L1-3C4-17 | ELE-FMS-3003 |  |  | 1 | 1408 | B1-DB-59601-P2020 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-17 | 0.04 | 230 | N | 30 | FMS | B1-DB-59601 | 400V-230V DIST. BOARD FOR ST #1 FOR BLOCK #1 - A | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B1-PMCS-59701 | SUB HUB PANEL FOR STG | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | L1, N, PE | B159-006AT0003 → END
B0-UPSP-64701 | -P20 | 09 | Route확인 | PE-L1-3C10-01 | PE-L1-3C10-01 | ELE-FMS-0001 |  | DONE | 1 | 1409 | B0-UPSP-64701-P2009 | 0.6/1kV CU/XLPE/LSZH | 3C x 10sqmm | PE-L1-3C10-01 | 3.3 | 230 | U | 100 | FMS | B0-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-PMCS-64702 | DB & COMM SERVER PANEL | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-006FT0205 → B064-006FT0003 → B064-006AC0018 → M0501 → B064-996GT0020 → B064-016CT0033 → B064-016GT0229 → B064-016GT0230 → B064-016GT0047 → B064-016GT0048 → B064-016GT0239 → B064-996GT0013 → B064-996GT0053 → B064-996GT0073 → B064-037AT0214 → B064-037AT0213 → B064-037AT0212 → B064-037AT0211 → B064-037AT0025 → END | B064-006FT0205 → B064-006FT0003 → B064-006AC0018 → M0501 → B064-996GT0020 → B064-016GT0033 → B064-016GT0229 → B064-016GT0230 → B064-016GT0047 → B064-016GT0048 → B064-016GT0239 → B064-996GT0013 → B064-996GT0053 → B064-996GT0073 → B064-037AT0214 → B064-037AT0213 → B064-037AT0212 → B064-037AT0211 → B064-037AT0025 → END
B0-UPSP-64702 | -P20 | 10 | Route확인 | PE-L1-3C10-01 | PE-L1-3C10-01 | ELE-FMS-0002 |  | DONE | 1 | 1410 | B0-UPSP-64702-P2010 | 0.6/1kV CU/XLPE/LSZH | 3C x 10sqmm | PE-L1-3C10-01 | 3.3 | 230 | U | 110 | FMS | B0-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-PMCS-64702 | DB & COMM SERVER PANEL | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B164-006HT0206 → B164-006HT0205 → B164-006HT0004 → B164-006HT0005 → B064-006AC0019 → M0501 → B064-996GT0020 → B064-016CT0033 → B064-016GT0229 → B064-016GT0230 → B064-016GT0047 → B064-016GT0048 → B064-016GT0239 → B064-996GT0013 → B064-996GT0053 → B064-996GT0073 → B064-037AT0214 → B064-037AT0213 → B064-037AT0212 → B064-037AT0211 → B064-037AT0025 → END | B164-006HT0206 → B164-006HT0205 → B164-006HT0004 → B164-006HT0005 → B064-006AC0019 → M0501 → B064-996AT0020 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0205 → B064-036AT0024 → B064-036AT0025 → END
B0-DB-64602 | -P20 | 09 | 재배정 | PE-L1-3C4-17 | PE-L1-3C4-05 | ELE-FMS-0003 |  | DONE | 1 | 1411 | B0-DB-64602-P2009 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-05 | 0.04 | 230 | N | 100 | FMS | B0-DB-64602 | 400V-230V DIST. BOARD FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-PMCS-64702 | DB & COMM SERVER PANEL | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0032 → B064-016AT0033 → B064-016AT0034 → B064-016AT0232 → B064-016AT0013 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0205 → B064-036AT0024 → B064-036AT0025 → END
B0-UPSP-64702 | -P20 | 11 | Route확인 | PE-L1-3C4-17 | PE-L1-3C4-17 | ELE-FMS-0004 |  |  | 1 | 1412 | B0-UPSP-64702-P2011 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-17 | 0.22 | 230 | U | 110 | FMS | B0-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-PMCS-64701 | MAIN HUB PANEL | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-006FT0206 → B064-006FT0009 → B064-006FT0208 → B064-006FT0207 → B064-006FT0005 → B064-006AC0017 → M0501 → B064-996GT0020 → B064-016CT0033 → B064-016GT0229 → B064-016GT0230 → B064-016GT0047 → B064-016GT0048 → B064-016GT0239 → B064-996GT0013 → B064-996GT0053 → B064-996GT0073 → B064-037AT0214 → B064-037AT0213 → B064-037AT0212 → B064-037AT0211 → B064-037AT0025 → END | B064-006FT0206 → B064-006FT0009 → B064-006FT0208 → B064-006FT0207 → B064-006FT0005 → B064-006AC0017 → M0501 → B064-996GT0020 → B064-016GT0033 → B064-016GT0229 → B064-016GT0230 → B064-016GT0047 → B064-016GT0048 → B064-016GT0239 → B064-996GT0013 → B064-996GT0053 → B064-996GT0073 → B064-037AT0214 → B064-037AT0213 → B064-037AT0212 → B064-037AT0211 → B064-037AT0025 → END
B0-UPSP-64701 | -P20 | 10 |  | PE-L1-3C4-17 | PE-L1-3C4-17 | ELE-FMS-0005 |  | DONE | 1 | 1413 | B0-UPSP-64701-P2010 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-17 | 0.22 | 230 | U | 80 | FMS | B0-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-PMCS-64701 | MAIN HUB PANEL | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B164-006HT0205 → B164-006HT0004 → B164-006HT0005 → B064-006AC0016 → M0501 → B064-996AT0020 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0205 → B064-036AT0024 → B064-036AT0025 → END
B0-DB-64602 | -P20 | 10 | 재배정 | PE-L1-3C4-17 | PE-L1-3C4-05 | ELE-FMS-0006 |  | DONE | 1 | 1414 | B0-DB-64602-P2010 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-05 | 0.04 | 230 | N | 100 | FMS | B0-DB-64602 | 400V-230V DIST. BOARD FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-PMCS-64701 | MAIN HUB PANEL | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0032 → B064-016AT0033 → B064-016AT0034 → B064-016AT0232 → B064-016AT0013 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0205 → B064-036AT0024 → B064-036AT0025 → END
B0-UPSP-64701 | -P20 | 11 | 재배정 | PE-L1-3C4-17 | PE-L1-3C4-05 | ELE-FMS-0007 |  | DONE | 1 | 1415 | B0-UPSP-64701-P2011 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-05 | 0.33 | 230 | U | 60 | FMS | B0-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-PMCS-64703 | SUB HUB PANEL FOR COMMON | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B164-006HT0205 → B164-006HT0004 → B164-006HT0005 → B064-006AC0016 → M0501 → B064-996CT0020 → B064-016CT0033 → B064-016CT0034 → B064-016CT0035 → END
B0-UPSP-64702 | -P20 | 12 | 재배정 | PE-L1-3C4-17 | PE-L1-3C4-05 | ELE-FMS-0008 |  | DONE | 1 | 1416 | B0-UPSP-64702-P2012 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-05 | 0.33 | 230 | U | 70 | FMS | B0-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-PMCS-64703 | SUB HUB PANEL FOR COMMON | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-006FT0206 → B064-006FT0009 → B064-006FT0208 → B064-006FT0207 → B064-006FT0005 → B064-006AC0017 → M0501 → B064-996AT0020 → B064-016AT0013 → B064-016AT0232 → B064-016AT0233 → END
B0-DB-64602 | -P20 | 02 | 재배정 | PE-L1-3C4-17 | PE-L1-3C4-15 | ELE-FMS-0009 |  | DONE | 1 | 1417 | B0-DB-64602-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 0.04 | 230 | N | 40 | FMS | B0-DB-64602 | 400V-230V DIST. BOARD FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-PMCS-64703 | SUB HUB PANEL FOR COMMON | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0032 → B064-016AT0033 → B064-016AT0034 → B064-016AT0233 → END
B0-UPSP-64702 | -P20 | 13 |  | PE-L1-3C4-17 | PE-L1-3C4-17 | ELE-FMS-0010 |  |  | 1 | 1418 | B0-UPSP-64702-P2013 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-17 | 0.11 | 230 | U | 560 | FMS | B0-UPSP-64702 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-PMCS-49701 | SUB HUB PANEL FOR WT | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, N, PE | B064-006FT0206 → B064-006FT0009 → B064-006FT0208 → B064-006FT0207 → B064-006FT0005 → B064-006AC0010 → M0501 → D0503-L35 → M0502 → D0504-L35 → M0503 → D0501-L35 → M0328 → D0324-L35 → M0329 → B114-997AT0021 → B114-017AT0020 → B114-017AT0025 → B025-017ET0042 → B025-017ET0041 → B025-017ET0040 → B025-017ET0016 → B025-017ET0039 → B025-017ET0038 → B025-017ET0036 → B025-017ET0035 → B025-017ET0033 → B025-017ET0032 → B025-017ET0031 → B025-017ET0030 → B025-017ET0021 → B025-017ET0022 → B025-997ET0004 → M0205 → D0205-L15 → M0206 → D0203-L15 → M0207 → D0204-L18 → B049-006AT0002 → B049-006AT0003 → B049-006AT0004 → B049-006AT0005 → END
B0-UPSP-64701 | -P20 | 12 |  | PE-L1-3C4-17 | PE-L1-3C4-17 | ELE-FMS-0011 |  |  | 1 | 1419 | B0-UPSP-64701-P2012 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-17 | 0.11 | 230 | U | 550 | FMS | B0-UPSP-64701 | 400/230V AC UPS MAIN DISTRIBUTION PANEL FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B0-PMCS-49701 | SUB HUB PANEL FOR WT | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, N, PE | B164-006HT0205 → B164-006HT0004 → B164-006HT0005 → B064-006AC0010 → M0501 → D0503-L36 → M0502 → D0504-L36 → M0503 → D0501-L36 → M0328 → D0324-L36 → M0329 → B114-996AT0021 → B114-016AT0020 → B114-016AT0025 → B025-016FT0042 → B025-016FT0041 → B025-016FT0040 → B025-996FT0016 → B025-016FT0039 → B025-016FT0038 → B025-016FT0036 → B025-016FT0035 → B025-016FT0033 → B025-016FT0032 → B025-016FT0031 → B025-016FT0030 → B025-016FT0028 → B025-016FT0029 → B025-996FT0005 → M0205 → D0205-L21 → M0206 → D0203-L21 → M0207 → D0204-L16 → B049-006BT0001 → B049-006BT0003 → B049-006BT0004 → END
B0-DB-49602 | -P20 | 04 |  | PE-L1-3C4-17 | PE-L1-3C4-17 | ELE-FMS-0012 |  |  | 1 | 1420 | B0-DB-49602-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-17 | 0.04 | 230 | N | 20 | FMS | B0-DB-49602 | 400V-230V DIST. BOARD FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, N, PE | B0-PMCS-49701 | SUB HUB PANEL FOR WT | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | L1, N, PE | B049-006CT0008 → B049-006CT0006 → END
B0-SWG-64601 | -P20 | 01 |  | PE-L1-1C500-01 | PE-L1-1C500-01 | ELE-AIS-0001 |  | DONE | 1 | 1421 | B0-SWG-64601-P2001 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-01 | 603.7 | 400 | N | 490 | AIS | B0-SWG-64601 | 400V SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1 | B0-SWG-22601 | 400V AIS SWITCHGEAR BUS - A | 38_OPERATIONAL CONTROL POINT | L1 | B064-016DT0020 → B064-016DT0021 → B064-016DT0022 → B064-016DT0023 → B064-016DT0310 → B064-016DT0247 → B064-016DT0248 → B064-016DT0300 → B064-016DT0304 → B064-996DT0026 → M0509 → D0507-L31 → M0524 → D0526-L11 → M0520 → D0514-L21 → M0516 → D0523-L25 → M0517 → D0515-L25 → M0518 → D0516-L25 → M0519 → D0527-L25 → M0425 → D0420-L21 → M0423 → D0416-L21 → M0422 → D0414-L13 → PKG SCOPE | 4
B0-SWG-64601 | -P20 | 02 |  | PE-L1-1C500-02 | PE-L1-1C500-02 |  |  | DONE | 1 | 1422 | B0-SWG-64601-P2002 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-02 | 603.7 | 400 | N | 490 | AIS | B0-SWG-64601 | 400V SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L2 | B0-SWG-22601 | 400V AIS SWITCHGEAR BUS - A | 38_OPERATIONAL CONTROL POINT | L2 | B064-016DT0020 → B064-016DT0021 → B064-016DT0022 → B064-016DT0023 → B064-016DT0310 → B064-016DT0247 → B064-016DT0248 → B064-016DT0300 → B064-016DT0304 → B064-996DT0026 → M0509 → D0507-L31 → M0524 → D0526-L11 → M0520 → D0514-L21 → M0516 → D0523-L25 → M0517 → D0515-L25 → M0518 → D0516-L25 → M0519 → D0527-L25 → M0425 → D0420-L21 → M0423 → D0416-L21 → M0422 → D0414-L13 → PKG SCOPE | 4
B0-SWG-64601 | -P20 | 03 |  | PE-L1-1C500-03 | PE-L1-1C500-03 |  |  | DONE | 1 | 1423 | B0-SWG-64601-P2003 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-03 | 603.7 | 400 | N | 490 | AIS | B0-SWG-64601 | 400V SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L3 | B0-SWG-22601 | 400V AIS SWITCHGEAR BUS - A | 38_OPERATIONAL CONTROL POINT | L3 | B064-016DT0020 → B064-016DT0021 → B064-016DT0022 → B064-016DT0023 → B064-016DT0310 → B064-016DT0247 → B064-016DT0248 → B064-016DT0300 → B064-016DT0304 → B064-996DT0026 → M0509 → D0507-L31 → M0524 → D0526-L11 → M0520 → D0514-L21 → M0516 → D0523-L25 → M0517 → D0515-L25 → M0518 → D0516-L25 → M0519 → D0527-L25 → M0425 → D0420-L21 → M0423 → D0416-L21 → M0422 → D0414-L13 → PKG SCOPE | 4
B0-SWG-64601 | -P20 | 04 |  | PE-L1-1C500-04 | PE-L1-1C500-04 |  |  | DONE | 1 | 1424 | B0-SWG-64601-P2004 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-04 | 603.7 | 400 | N | 490 | AIS | B0-SWG-64601 | 400V SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1 | B0-SWG-22601 | 400V AIS SWITCHGEAR BUS - A | 38_OPERATIONAL CONTROL POINT | L1 | B064-016DT0020 → B064-016DT0021 → B064-016DT0022 → B064-016DT0023 → B064-016DT0310 → B064-016DT0247 → B064-016DT0248 → B064-016DT0300 → B064-016DT0304 → B064-996DT0026 → M0509 → D0507-L32 → M0524 → D0526-L12 → M0520 → D0514-L22 → M0516 → D0523-L24 → M0517 → D0515-L24 → M0518 → D0516-L24 → M0519 → D0527-L24 → M0425 → D0420-L22 → M0423 → D0416-L22 → M0422 → D0414-L12 → PKG SCOPE | 3
B0-SWG-64601 | -P20 | 05 |  | PE-L1-1C500-05 | PE-L1-1C500-05 |  |  | DONE | 1 | 1425 | B0-SWG-64601-P2005 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-05 | 603.7 | 400 | N | 490 | AIS | B0-SWG-64601 | 400V SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L2 | B0-SWG-22601 | 400V AIS SWITCHGEAR BUS - A | 38_OPERATIONAL CONTROL POINT | L2 | B064-016DT0020 → B064-016DT0021 → B064-016DT0022 → B064-016DT0023 → B064-016DT0310 → B064-016DT0247 → B064-016DT0248 → B064-016DT0300 → B064-016DT0304 → B064-996DT0026 → M0509 → D0507-L32 → M0524 → D0526-L12 → M0520 → D0514-L22 → M0516 → D0523-L24 → M0517 → D0515-L24 → M0518 → D0516-L24 → M0519 → D0527-L24 → M0425 → D0420-L22 → M0423 → D0416-L22 → M0422 → D0414-L12 → PKG SCOPE | 3
B0-SWG-64601 | -P20 | 06 |  | PE-L1-1C500-06 | PE-L1-1C500-06 |  |  | DONE | 1 | 1426 | B0-SWG-64601-P2006 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-06 | 603.7 | 400 | N | 490 | AIS | B0-SWG-64601 | 400V SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L3 | B0-SWG-22601 | 400V AIS SWITCHGEAR BUS - A | 38_OPERATIONAL CONTROL POINT | L3 | B064-016DT0020 → B064-016DT0021 → B064-016DT0022 → B064-016DT0023 → B064-016DT0310 → B064-016DT0247 → B064-016DT0248 → B064-016DT0300 → B064-016DT0304 → B064-996DT0026 → M0509 → D0507-L32 → M0524 → D0526-L12 → M0520 → D0514-L22 → M0516 → D0523-L24 → M0517 → D0515-L24 → M0518 → D0516-L24 → M0519 → D0527-L24 → M0425 → D0420-L22 → M0423 → D0416-L22 → M0422 → D0414-L12 → PKG SCOPE | 3
B0-SWG-64601 | -P20 | 07 |  | PE-L1-1C500-07 | PE-L1-1C500-07 |  |  | DONE | 1 | 1427 | B0-SWG-64601-P2007 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-07 | 603.7 | 400 | N | 490 | AIS | B0-SWG-64601 | 400V SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | N | B0-SWG-22601 | 400V AIS SWITCHGEAR BUS - A | 38_OPERATIONAL CONTROL POINT | N | B064-016DT0020 → B064-016DT0021 → B064-016DT0022 → B064-016DT0023 → B064-016DT0310 → B064-016DT0247 → B064-016DT0248 → B064-016DT0300 → B064-016DT0304 → B064-996DT0026 → M0509 → D0507-L31 → M0524 → D0526-L11 → M0520 → D0514-L21 → M0516 → D0523-L25 → M0517 → D0515-L25 → M0518 → D0516-L25 → M0519 → D0527-L25 → M0425 → D0420-L21 → M0423 → D0416-L21 → M0422 → D0414-L13 → PKG SCOPE | 4
B0-SWG-64601 | -P20 | 08 |  | PE-L1-1C500-08 | PE-L1-1C500-08 |  |  | DONE | 1 | 1428 | B0-SWG-64601-P2008 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-08 | 603.7 | 400 | N | 490 | AIS | B0-SWG-64601 | 400V SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1 | B0-SWG-22601 | 400V AIS SWITCHGEAR BUS - A | 38_OPERATIONAL CONTROL POINT | L1 | B064-016DT0020 → B064-016DT0021 → B064-016DT0022 → B064-016DT0023 → B064-016DT0310 → B064-016DT0247 → B064-016DT0248 → B064-016DT0300 → B064-016DT0304 → B064-996DT0026 → M0509 → D0507-L41 → M0524 → D0526-L21 → M0520 → D0514-L31 → M0516 → D0523-L35 → M0517 → D0515-L35 → M0518 → D0516-L35 → M0519 → D0527-L35 → M0425 → D0420-L35 → M0423 → D0416-L31 → M0422 → D0414-L23 → PKG SCOPE | 4
B0-SWG-64601 | -P20 | 09 |  | PE-L1-1C500-09 | PE-L1-1C500-09 |  |  | DONE | 1 | 1429 | B0-SWG-64601-P2009 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-09 | 603.7 | 400 | N | 490 | AIS | B0-SWG-64601 | 400V SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L2 | B0-SWG-22601 | 400V AIS SWITCHGEAR BUS - A | 38_OPERATIONAL CONTROL POINT | L2 | B064-016DT0020 → B064-016DT0021 → B064-016DT0022 → B064-016DT0023 → B064-016DT0310 → B064-016DT0247 → B064-016DT0248 → B064-016DT0300 → B064-016DT0304 → B064-996DT0026 → M0509 → D0507-L41 → M0524 → D0526-L21 → M0520 → D0514-L31 → M0516 → D0523-L35 → M0517 → D0515-L35 → M0518 → D0516-L35 → M0519 → D0527-L35 → M0425 → D0420-L35 → M0423 → D0416-L31 → M0422 → D0414-L23 → PKG SCOPE | 4
B0-SWG-64601 | -P20 | 10 |  | PE-L1-1C500-10 | PE-L1-1C500-10 |  |  | DONE | 1 | 1430 | B0-SWG-64601-P2010 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-10 | 603.7 | 400 | N | 490 | AIS | B0-SWG-64601 | 400V SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L3 | B0-SWG-22601 | 400V AIS SWITCHGEAR BUS - A | 38_OPERATIONAL CONTROL POINT | L3 | B064-016DT0020 → B064-016DT0021 → B064-016DT0022 → B064-016DT0023 → B064-016DT0310 → B064-016DT0247 → B064-016DT0248 → B064-016DT0300 → B064-016DT0304 → B064-996DT0026 → M0509 → D0507-L41 → M0524 → D0526-L21 → M0520 → D0514-L31 → M0516 → D0523-L35 → M0517 → D0515-L35 → M0518 → D0516-L35 → M0519 → D0527-L35 → M0425 → D0420-L35 → M0423 → D0416-L31 → M0422 → D0414-L23 → PKG SCOPE | 4
B0-SWG-64601 | -P20 | 11 |  | PE-L1-1C500-11 | PE-L1-1C500-11 |  |  | DONE | 1 | 1431 | B0-SWG-64601-P2011 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-11 | 603.7 | 400 | N | 490 | AIS | B0-SWG-64601 | 400V SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1 | B0-SWG-22601 | 400V AIS SWITCHGEAR BUS - A | 38_OPERATIONAL CONTROL POINT | L1 | B064-016DT0020 → B064-016DT0021 → B064-016DT0022 → B064-016DT0023 → B064-016DT0310 → B064-016DT0247 → B064-016DT0248 → B064-016DT0300 → B064-016DT0304 → B064-996DT0026 → M0509 → D0507-L42 → M0524 → D0526-L22 → M0520 → D0514-L23 → M0516 → D0523-L23 → M0517 → D0515-L23 → M0518 → D0516-L23 → M0519 → D0527-L23 → M0425 → D0420-L23 → M0423 → D0416-L23 → M0422 → D0414-L22 → PKG SCOPE | 3
B0-SWG-64601 | -P20 | 12 |  | PE-L1-1C500-12 | PE-L1-1C500-12 |  |  | DONE | 1 | 1432 | B0-SWG-64601-P2012 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-12 | 603.7 | 400 | N | 490 | AIS | B0-SWG-64601 | 400V SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L2 | B0-SWG-22601 | 400V AIS SWITCHGEAR BUS - A | 38_OPERATIONAL CONTROL POINT | L2 | B064-016DT0020 → B064-016DT0021 → B064-016DT0022 → B064-016DT0023 → B064-016DT0310 → B064-016DT0247 → B064-016DT0248 → B064-016DT0300 → B064-016DT0304 → B064-996DT0026 → M0509 → D0507-L42 → M0524 → D0526-L22 → M0520 → D0514-L23 → M0516 → D0523-L23 → M0517 → D0515-L23 → M0518 → D0516-L23 → M0519 → D0527-L23 → M0425 → D0420-L23 → M0423 → D0416-L23 → M0422 → D0414-L22 → PKG SCOPE | 3
B0-SWG-64601 | -P20 | 13 |  | PE-L1-1C500-13 | PE-L1-1C500-13 |  |  | DONE | 1 | 1433 | B0-SWG-64601-P2013 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-13 | 603.7 | 400 | N | 490 | AIS | B0-SWG-64601 | 400V SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L3 | B0-SWG-22601 | 400V AIS SWITCHGEAR BUS - A | 38_OPERATIONAL CONTROL POINT | L3 | B064-016DT0020 → B064-016DT0021 → B064-016DT0022 → B064-016DT0023 → B064-016DT0310 → B064-016DT0247 → B064-016DT0248 → B064-016DT0300 → B064-016DT0304 → B064-996DT0026 → M0509 → D0507-L42 → M0524 → D0526-L22 → M0520 → D0514-L23 → M0516 → D0523-L23 → M0517 → D0515-L23 → M0518 → D0516-L23 → M0519 → D0527-L23 → M0425 → D0420-L23 → M0423 → D0416-L23 → M0422 → D0414-L22 → PKG SCOPE | 3
B0-SWG-64601 | -P20 | 14 |  | PE-L1-1C500-14 | PE-L1-1C500-14 |  |  | DONE | 1 | 1434 | B0-SWG-64601-P2014 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-14 | 603.7 | 400 | N | 490 | AIS | B0-SWG-64601 | 400V SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | N | B0-SWG-22601 | 400V AIS SWITCHGEAR BUS - A | 38_OPERATIONAL CONTROL POINT | N | B064-016DT0020 → B064-016DT0021 → B064-016DT0022 → B064-016DT0023 → B064-016DT0310 → B064-016DT0247 → B064-016DT0248 → B064-016DT0300 → B064-016DT0304 → B064-996DT0026 → M0509 → D0507-L41 → M0524 → D0526-L21 → M0520 → D0514-L31 → M0516 → D0523-L35 → M0517 → D0515-L35 → M0518 → D0516-L35 → M0519 → D0527-L35 → M0425 → D0420-L35 → M0423 → D0416-L31 → M0422 → D0414-L23 → PKG SCOPE | 4
B0-SWG-64602 | -P20 | 01 |  | PE-L1-1C500-15 | PE-L1-1C500-15 | ELE-AIS-0002 |  | DONE | 1 | 1435 | B0-SWG-64602-P2001 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-15 | 603.7 | 400 | N | 480 | AIS | B0-SWG-64602 | 400V SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1 | B0-SWG-22602 | 400V AIS SWITCHGEAR BUS - B | 38_OPERATIONAL CONTROL POINT | L1 | B064-016ET0027 → B064-016ET0028 → B064-016ET0029 → B064-016ET0030 → B064-016ET0245 → B064-016ET0246 → B064-016ET0297 → B064-016ET0302 → B064-996ET0025 → M0509 → D0507-L33 → M0524 → D0526-L13 → M0520 → D0514-L24 → M0516 → D0523-L22 → M0517 → D0515-L22 → M0518 → D0516-L22 → M0519 → D0527-L22 → M0425 → D0420-L24 → M0423 → D0416-L24 → M0422 → D0414-L11 → PKG SCOPE | 4
B0-SWG-64602 | -P20 | 02 |  | PE-L1-1C500-16 | PE-L1-1C500-16 |  |  | DONE | 1 | 1436 | B0-SWG-64602-P2002 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-16 | 603.7 | 400 | N | 480 | AIS | B0-SWG-64602 | 400V SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L2 | B0-SWG-22602 | 400V AIS SWITCHGEAR BUS - B | 38_OPERATIONAL CONTROL POINT | L2 | B064-016ET0027 → B064-016ET0028 → B064-016ET0029 → B064-016ET0030 → B064-016ET0245 → B064-016ET0246 → B064-016ET0297 → B064-016ET0302 → B064-996ET0025 → M0509 → D0507-L33 → M0524 → D0526-L13 → M0520 → D0514-L24 → M0516 → D0523-L22 → M0517 → D0515-L22 → M0518 → D0516-L22 → M0519 → D0527-L22 → M0425 → D0420-L24 → M0423 → D0416-L24 → M0422 → D0414-L11 → PKG SCOPE | 4
B0-SWG-64602 | -P20 | 03 |  | PE-L1-1C500-17 | PE-L1-1C500-17 |  |  | DONE | 1 | 1437 | B0-SWG-64602-P2003 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-17 | 603.7 | 400 | N | 480 | AIS | B0-SWG-64602 | 400V SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L3 | B0-SWG-22602 | 400V AIS SWITCHGEAR BUS - B | 38_OPERATIONAL CONTROL POINT | L3 | B064-016ET0027 → B064-016ET0028 → B064-016ET0029 → B064-016ET0030 → B064-016ET0245 → B064-016ET0246 → B064-016ET0297 → B064-016ET0302 → B064-996ET0025 → M0509 → D0507-L33 → M0524 → D0526-L13 → M0520 → D0514-L24 → M0516 → D0523-L22 → M0517 → D0515-L22 → M0518 → D0516-L22 → M0519 → D0527-L22 → M0425 → D0420-L24 → M0423 → D0416-L24 → M0422 → D0414-L11 → PKG SCOPE | 4
B0-SWG-64602 | -P20 | 04 |  | PE-L1-1C500-18 | PE-L1-1C500-18 |  |  | DONE | 1 | 1438 | B0-SWG-64602-P2004 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-18 | 603.7 | 400 | N | 480 | AIS | B0-SWG-64602 | 400V SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1 | B0-SWG-22602 | 400V AIS SWITCHGEAR BUS - B | 38_OPERATIONAL CONTROL POINT | L1 | B064-016ET0027 → B064-016ET0028 → B064-016ET0029 → B064-016ET0030 → B064-016ET0245 → B064-016ET0246 → B064-016ET0297 → B064-016ET0302 → B064-996ET0025 → M0509 → D0507-L34 → M0524 → D0526-L14 → M0520 → D0514-L25 → M0516 → D0523-L21 → M0517 → D0515-L21 → M0518 → D0516-L21 → M0519 → D0527-L21 → M0425 → D0420-L25 → M0423 → D0416-L25 → M0422 → D0414-L21 → PKG SCOPE | 3
B0-SWG-64602 | -P20 | 05 |  | PE-L1-1C500-19 | PE-L1-1C500-19 |  |  | DONE | 1 | 1439 | B0-SWG-64602-P2005 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-19 | 603.7 | 400 | N | 480 | AIS | B0-SWG-64602 | 400V SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L2 | B0-SWG-22602 | 400V AIS SWITCHGEAR BUS - B | 38_OPERATIONAL CONTROL POINT | L2 | B064-016ET0027 → B064-016ET0028 → B064-016ET0029 → B064-016ET0030 → B064-016ET0245 → B064-016ET0246 → B064-016ET0297 → B064-016ET0302 → B064-996ET0025 → M0509 → D0507-L34 → M0524 → D0526-L14 → M0520 → D0514-L25 → M0516 → D0523-L21 → M0517 → D0515-L21 → M0518 → D0516-L21 → M0519 → D0527-L21 → M0425 → D0420-L25 → M0423 → D0416-L25 → M0422 → D0414-L21 → PKG SCOPE | 3
B0-SWG-64602 | -P20 | 06 |  | PE-L1-1C500-20 | PE-L1-1C500-20 |  |  | DONE | 1 | 1440 | B0-SWG-64602-P2006 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-20 | 603.7 | 400 | N | 480 | AIS | B0-SWG-64602 | 400V SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L3 | B0-SWG-22602 | 400V AIS SWITCHGEAR BUS - B | 38_OPERATIONAL CONTROL POINT | L3 | B064-016ET0027 → B064-016ET0028 → B064-016ET0029 → B064-016ET0030 → B064-016ET0245 → B064-016ET0246 → B064-016ET0297 → B064-016ET0302 → B064-996ET0025 → M0509 → D0507-L34 → M0524 → D0526-L14 → M0520 → D0514-L25 → M0516 → D0523-L21 → M0517 → D0515-L21 → M0518 → D0516-L21 → M0519 → D0527-L21 → M0425 → D0420-L25 → M0423 → D0416-L25 → M0422 → D0414-L21 → PKG SCOPE | 3
B0-SWG-64602 | -P20 | 07 |  | PE-L1-1C500-21 | PE-L1-1C500-21 |  |  | DONE | 1 | 1441 | B0-SWG-64602-P2007 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-21 | 603.7 | 400 | N | 480 | AIS | B0-SWG-64602 | 400V SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | N | B0-SWG-22602 | 400V AIS SWITCHGEAR BUS - B | 38_OPERATIONAL CONTROL POINT | N | B064-016ET0027 → B064-016ET0028 → B064-016ET0029 → B064-016ET0030 → B064-016ET0245 → B064-016ET0246 → B064-016ET0297 → B064-016ET0302 → B064-996ET0025 → M0509 → D0507-L33 → M0524 → D0526-L13 → M0520 → D0514-L24 → M0516 → D0523-L22 → M0517 → D0515-L22 → M0518 → D0516-L22 → M0519 → D0527-L22 → M0425 → D0420-L24 → M0423 → D0416-L24 → M0422 → D0414-L11 → PKG SCOPE | 4
B0-SWG-64602 | -P20 | 08 |  | PE-L1-1C500-22 | PE-L1-1C500-22 |  |  | DONE | 1 | 1442 | B0-SWG-64602-P2008 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-22 | 603.7 | 400 | N | 480 | AIS | B0-SWG-64602 | 400V SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1 | B0-SWG-22602 | 400V AIS SWITCHGEAR BUS - B | 38_OPERATIONAL CONTROL POINT | L1 | B064-016ET0027 → B064-016ET0028 → B064-016ET0029 → B064-016ET0030 → B064-016ET0245 → B064-016ET0246 → B064-016ET0297 → B064-016ET0302 → B064-996ET0025 → M0509 → D0507-L44 → M0524 → D0526-L15 → M0520 → D0514-L15 → M0516 → D0523-L11 → M0517 → D0515-L11 → M0518 → D0516-L11 → M0519 → D0527-L11 → M0425 → D0420-L11 → M0423 → D0416-L15 → M0422 → D0414-L31 → PKG SCOPE | 4
B0-SWG-64602 | -P20 | 09 |  | PE-L1-1C500-23 | PE-L1-1C500-23 |  |  | DONE | 1 | 1443 | B0-SWG-64602-P2009 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-23 | 603.7 | 400 | N | 480 | AIS | B0-SWG-64602 | 400V SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L2 | B0-SWG-22602 | 400V AIS SWITCHGEAR BUS - B | 38_OPERATIONAL CONTROL POINT | L2 | B064-016ET0027 → B064-016ET0028 → B064-016ET0029 → B064-016ET0030 → B064-016ET0245 → B064-016ET0246 → B064-016ET0297 → B064-016ET0302 → B064-996ET0025 → M0509 → D0507-L44 → M0524 → D0526-L15 → M0520 → D0514-L15 → M0516 → D0523-L11 → M0517 → D0515-L11 → M0518 → D0516-L11 → M0519 → D0527-L11 → M0425 → D0420-L11 → M0423 → D0416-L15 → M0422 → D0414-L31 → PKG SCOPE | 4
B0-SWG-64602 | -P20 | 10 |  | PE-L1-1C500-24 | PE-L1-1C500-24 |  |  | DONE | 1 | 1444 | B0-SWG-64602-P2010 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-24 | 603.7 | 400 | N | 480 | AIS | B0-SWG-64602 | 400V SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L3 | B0-SWG-22602 | 400V AIS SWITCHGEAR BUS - B | 38_OPERATIONAL CONTROL POINT | L3 | B064-016ET0027 → B064-016ET0028 → B064-016ET0029 → B064-016ET0030 → B064-016ET0245 → B064-016ET0246 → B064-016ET0297 → B064-016ET0302 → B064-996ET0025 → M0509 → D0507-L44 → M0524 → D0526-L15 → M0520 → D0514-L15 → M0516 → D0523-L11 → M0517 → D0515-L11 → M0518 → D0516-L11 → M0519 → D0527-L11 → M0425 → D0420-L11 → M0423 → D0416-L15 → M0422 → D0414-L31 → PKG SCOPE | 4
B0-SWG-64602 | -P20 | 11 |  | PE-L1-1C500-25 | PE-L1-1C500-25 |  |  | DONE | 1 | 1445 | B0-SWG-64602-P2011 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-25 | 603.7 | 400 | N | 480 | AIS | B0-SWG-64602 | 400V SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1 | B0-SWG-22602 | 400V AIS SWITCHGEAR BUS - B | 38_OPERATIONAL CONTROL POINT | L1 | B064-016ET0027 → B064-016ET0028 → B064-016ET0029 → B064-016ET0030 → B064-016ET0245 → B064-016ET0246 → B064-016ET0297 → B064-016ET0302 → B064-996ET0025 → M0509 → D0507-L43 → M0524 → D0526-P23 → M0520 → D0514-L32 → M0516 → D0523-L34 → M0517 → D0515-L34 → M0518 → D0516-L34 → M0519 → D0527-L34 → M0425 → D0420-L34 → M0423 → D0416-L32 → M0420 → D0414-P32 → PKG SCOPE | 3
B0-SWG-64602 | -P20 | 12 |  | PE-L1-1C500-26 | PE-L1-1C500-26 |  |  | DONE | 1 | 1446 | B0-SWG-64602-P2012 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-26 | 603.7 | 400 | N | 480 | AIS | B0-SWG-64602 | 400V SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L2 | B0-SWG-22602 | 400V AIS SWITCHGEAR BUS - B | 38_OPERATIONAL CONTROL POINT | L2 | B064-016ET0027 → B064-016ET0028 → B064-016ET0029 → B064-016ET0030 → B064-016ET0245 → B064-016ET0246 → B064-016ET0297 → B064-016ET0302 → B064-996ET0025 → M0509 → D0507-L43 → M0524 → D0526-P23 → M0520 → D0514-L32 → M0516 → D0523-L34 → M0517 → D0515-L34 → M0518 → D0516-L34 → M0519 → D0527-L34 → M0425 → D0420-L34 → M0423 → D0416-L32 → M0420 → D0414-P32 → PKG SCOPE | 3
B0-SWG-64602 | -P20 | 13 |  | PE-L1-1C500-27 | PE-L1-1C500-27 |  |  | DONE | 1 | 1447 | B0-SWG-64602-P2013 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-27 | 603.7 | 400 | N | 480 | AIS | B0-SWG-64602 | 400V SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L3 | B0-SWG-22602 | 400V AIS SWITCHGEAR BUS - B | 38_OPERATIONAL CONTROL POINT | L3 | B064-016ET0027 → B064-016ET0028 → B064-016ET0029 → B064-016ET0030 → B064-016ET0245 → B064-016ET0246 → B064-016ET0297 → B064-016ET0302 → B064-996ET0025 → M0509 → D0507-L43 → M0524 → D0526-P23 → M0520 → D0514-L32 → M0516 → D0523-L34 → M0517 → D0515-L34 → M0518 → D0516-L34 → M0519 → D0527-L34 → M0425 → D0420-L34 → M0423 → D0416-L32 → M0420 → D0414-P32 → PKG SCOPE | 3
B0-SWG-64602 | -P20 | 14 |  | PE-L1-1C500-28 | PE-L1-1C500-28 |  |  | DONE | 1 | 1448 | B0-SWG-64602-P2014 | 0.6/1kV CU/XLPE/LSZH | 1C x 500sqmm | PE-L1-1C500-28 | 603.7 | 400 | N | 480 | AIS | B0-SWG-64602 | 400V SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | N | B0-SWG-22602 | 400V AIS SWITCHGEAR BUS - B | 38_OPERATIONAL CONTROL POINT | N | B064-016ET0027 → B064-016ET0028 → B064-016ET0029 → B064-016ET0030 → B064-016ET0245 → B064-016ET0246 → B064-016ET0297 → B064-016ET0302 → B064-996ET0025 → M0509 → D0507-L44 → M0524 → D0526-L15 → M0520 → D0514-L15 → M0516 → D0523-L11 → M0517 → D0515-L11 → M0518 → D0516-L11 → M0519 → D0527-L11 → M0425 → D0420-L11 → M0423 → D0416-L15 → M0422 → D0414-L31 → PKG SCOPE | 4
B1-DB-64601 | -P20 | 10 |  | PE-L1-3C4-19 | PE-L1-3C4-19 | ELE-AIS-0003 |  | DONE | 1 | 1449 | B1-DB-64601-P2010 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-19 | 0.02 | 230 | N | 110 | AIS | B1-DB-64601 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B04+S_B04/2 | MARSHALLING KIOSKS INTERFACE PANEL FOR GTG11 | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B164-016AT0092 → B164-016AT0091 → B064-016AT0216 → B164-016AT0215 → B064-016AT0214 → B064-016AT0213 → B064-016AT0212 → B064-016AT0011 → B064-016AT0012 → B064-016AT0013 → B064-016AT0014 → B064-016AT0015 → B064-016AT0016 → B064-016AT0017 → B064-016AT0222 → END | 1
B1-DB-64602 | -P20 | 14 | 110M이나 120m재단 | PE-L1-3C4-06 | PE-L1-3C4-06 | ELE-AIS-0003-1 |  | DONE | 1 | 1450 | B1-DB-64602-P2014 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-06 | 0.02 | 230 | N | 120 | AIS | B1-DB-64602 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B03+S_B03/2 | MARSHALLING KIOSKS INTERFACE PANEL FOR GTG12 | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0106 → B064-016AT0217 → B064-016AT0090 → B064-016AT0216 → B064-016AT0215 → B064-016AT0214 → B064-016AT0213 → B064-016AT0032 → B064-016AT0033 → B064-016AT0034 → B064-016AT0035 → B064-016AT0036 → B064-016AT0037 → B064-016AT0309 → B064-016AT0017 → B064-016AT0251 → END | 2
B1-DB-59602 | -P20 | 08 | From변경 | PE-L1-3C4-06 | PE-L1-3C4-06 | ELE-AIS-0003-2 | B1-DB-59602-P2008 |  | 1 | 1451 | B1-DB-64602-P2018 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-06 | 0.02 | 230 | N | 110 | AIS | B1-DB-64602 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B02+S_B02/2 | MARSHALLING KIOSKS INTERFACE PANEL FOR STG13 | 1.2_LEB FOR BLOCK #1 | L1, N, PE | B064-016AT0106 → B064-016AT0217 → B064-016AT0090 → B064-016AT0216 → B064-016AT0215 → B064-016AT0214 → B064-016AT0213 → B064-016AT0032 → B064-016AT0033 → B064-016AT0034 → B064-016AT0035 → B064-016AT0036 → B064-016AT0037 → B064-016AT0309 → B064-016AT0017 → B064-016AT0251 → END | 2
B1-DCP-64701 | -P20 | 35 |  | PE-L1-2C4-04 | PE-L1-2C4-04 | ELE-AIS-0004 |  | DONE | 1 | 1452 | B1-DCP-64701-P2035 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-04 | 0.15 | 220 | D | 110 | AIS | B1-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - A | 1.2_LEB FOR BLOCK #1 | L+, L- | K00+P91 | BLOCK#1 GENERATOR METERING CABINET | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006GT0203 → B164-006GT0002 → B164-006GT0003 → B064-006AC0021 → M0501 → B064-996AT0020 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0014 → B064-036AT0015 → B064-036AT0016 → B064-036AT0217 → B064-036AT0218 → B064-036AT0219 → B064-036AT0220 → B064-036AT0034 → B064-036AT0035 → END | 1
B1-DCP-64702 | -P20 | 35 |  | PE-L1-2C4-04 | PE-L1-2C4-04 | ELE-AIS-0005 |  | DONE | 1 | 1453 | B1-DCP-64702-P2035 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-04 | 0.15 | 220 | D | 120 | AIS | B1-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #1 - B | 1.2_LEB FOR BLOCK #1 | L+, L- | K00+P93 | BLOCK#1 SWGR METERING CABINET | 1.2_LEB FOR BLOCK #1 | L+, L- | B164-006HT0204 → B164-006HT0008 → B164-006HT0009 → B164-006HT0010 → B164-006HT0210 → B164-006HT0209 → B164-006HT0006 → B064-006AC0007 → M0501 → B064-996AT0020 → B064-016AT0222 → B064-996AT0005 → B064-996AT0045 → B064-996AT0065 → B064-036AT0008 → B064-036AT0203 → B064-036AT0013 → B064-036AT0014 → B064-036AT0015 → B064-036AT0016 → B064-036AT0217 → B064-036AT0218 → B064-036AT0219 → B064-036AT0220 → B064-036AT0034 → B064-036AT0035 → END | 1
B2-DB-64603 | -P20 | 19 |  | PE-L1-3C4-19 | PE-L1-3C4-19 | ELE-AIS-0006 |  |  | 1 | 1454 | B2-DB-64603-P2019 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-19 | 0.02 | 230 | N | 60 | AIS | B2-DB-64603 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | D11+S_D11/2 | MARSHALLING KIOSKS INTERFACE PANEL FOR GTG21 | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016AT0026 → B264-016AT0027 → B264-016AT0028 → B264-016AT0029 → B264-016AT0234 → B264-016AT0233 → B264-016AT0012 → B264-016AT0237 → END | 2
B2-DB-64602 | -P20 | 09 |  | PE-L1-3C4-06 | PE-L1-3C4-06 | ELE-AIS-0006-1 |  |  | 1 | 1455 | B2-DB-64602-P2009 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-06 | 0.02 | 230 | N | 90 | AIS | B2-DB-64602 | 400V-230V DIST. BOARD FOR GT/HRSG #1 FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L1, N, PE | D13+S_D13/2 | MARSHALLING KIOSKS INTERFACE PANEL FOR GTG22 | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016AT0045 → B264-016AT0046 → B264-016AT0209 → B264-016AT0026 → B264-016AT0027 → B264-016AT0028 → B264-016AT0029 → B264-016AT0234 → B264-016AT0233 → B264-016AT0012 → B264-016AT0237 → END | 1
B2-DB-59602 | -P20 | 08 | From변경 | PE-L1-3C4-06 | PE-L1-3C4-06 | ELE-AIS-0006-2 | B2-DB-59602-P2008 |  | 1 | 1456 | B2-DB-64603-P2021 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-06 | 0.02 | 230 | N | 60 | AIS | B2-DB-64603 | 400V-230V DIST. BOARD FOR GT/HRSG #2 FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L1, N, PE | D09+S_D09/2 | MARSHALLING KIOSKS INTERFACE PANEL FOR STG23 | 1.3_LEB FOR BLOCK #2 | L1, N, PE | B264-016AT0026 → B264-016AT0027 → B264-016AT0028 → B264-016AT0029 → B264-016AT0234 → B264-016AT0233 → B264-016AT0012 → B264-016AT0237 → END | 2
B2-DCP-64701 | -P20 | 33 |  | PE-L1-2C4-10 | PE-L1-2C4-10 | ELE-AIS-0007 |  |  | 1 | 1457 | B2-DCP-64701-P2033 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-10 | 0.1 | 220 | D | 100 | AIS | B2-DCP-64701 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - A | 1.3_LEB FOR BLOCK #2 | L+, L- | K00+P92 | BLOCK#2 GENERATOR METERING CABINET | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-017ET0063 → B264-017ET0062 → B264-006AC0013 → M0407 → B264-996AT0013 → B264-016AT0048 → B264-016AT0049 → B264-016AT0050 → B264-016AT0240 → B264-016AT0055 → B264-016AT0056 → B264-016AT0057 → B264-016AT0244 → END
B2-DCP-64702 | -P20 | 33 |  | PE-L1-2C4-10 | PE-L1-2C4-10 | ELE-AIS-0008 |  |  | 1 | 1458 | B2-DCP-64702-P2033 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-10 | 0.1 | 220 | D | 100 | AIS | B2-DCP-64702 | 220V DC MAIN DISTRIBUTION PANEL FOR BLOCK #2 - B | 1.3_LEB FOR BLOCK #2 | L+, L- | K00+P94 | BLOCK#2 SWGR METERING CABINET | 1.3_LEB FOR BLOCK #2 | L+, L- | B264-016ET0063 → B264-016ET0062 → B264-006AC0014 → M0407 → B264-996BT0013 → B264-016BT0048 → B264-016BT0049 → B264-016BT0050 → B264-016BT0240 → B264-016BT0055 → B264-016BT0056 → B264-016BT0057 → B264-016BT0244 → END
B1-SWG-64301 | -P10 | 04 |  | PE-M1-3C120-01 | PE-M1-3C120-01 | ELE-TRF-6001 |  | DONE | 1 | 1459 | B1-SWG-64301-P1004 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-01 | 2000 | 10000 | N | 40 | TR FEEDER | B1-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B1-XFR-64601 | 10/0.4KV TRANSFORMER - GT / HRSG #1A FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B164-013ET0066 → B164-013ET0269 → B164-013ET0270 → B164-013ET0101 → B164-013ET0100 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B1-SWG-64302 | -P10 | 04 |  | PE-M1-3C120-01 | PE-M1-3C120-01 | ELE-TRF-6002 |  | DONE | 1 | 1460 | B1-SWG-64302-P1004 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-01 | 2000 | 10000 | N | 30 | TR FEEDER | B1-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B1-XFR-64602 | 10/0.4KV TRANSFORMER - GT / HRSG #1B FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B064-013HT0083 → B064-013HT0273 → B064-013HT0274 → B064-013HT0107 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B1-SWG-64301 | -P10 | 05 |  | PE-M1-3C120-03 | PE-M1-3C120-03 | ELE-TRF-6003 |  | DONE | 1 | 1461 | B1-SWG-64301-P1005 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-03 | 2000 | 10000 | N | 40 | TR FEEDER | B1-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B1-XFR-64603 | 10/0.4KV TRANSFORMER - GT / HRSG #2A FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B164-013ET0066 → B164-013ET0269 → B164-013ET0270 → B164-013ET0102 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B1-SWG-64302 | -P10 | 05 |  | PE-M1-3C120-03 | PE-M1-3C120-03 | ELE-TRF-6004 |  | DONE | 1 | 1462 | B1-SWG-64302-P1005 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-03 | 2000 | 10000 | N | 30 | TR FEEDER | B1-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B1-XFR-64604 | 10/0.4KV TRANSFORMER - GT / HRSG #2B FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B064-013HT0083 → B064-013HT0273 → B064-013HT0274 → B064-013HT0108 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B1-SWG-64303 | -P10 | 05 |  | PE-M1-3C120-02 | PE-M1-3C120-02 | ELE-TRF-6005 |  | DONE | 1 | 1463 | B1-SWG-64303-P1005 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-02 | 2000 | 10000 | N | 40 | TR FEEDER | B1-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B1-XFR-64605 | 10/0.4KV TRANSFORMER - EMERGENCY-A FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B064-013DT0059 → B064-013DT0060 → B064-013DT0301 → B064-013DT0302 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B0-SWG-64301 | -P10 | 03 |  | PE-M1-3C120-09 | PE-M1-3C120-09 | ELE-TRF-6006 |  | DONE | 1 | 1464 | B0-SWG-64301-P1003 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-09 | 2000 | 10000 | N | 80 | TR FEEDER | B0-SWG-64301 | 10KV SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B1-XFR-64606 | 10/0.4KV TRANSFORMER - EMERGENCY-B FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B064-013CT0040 → B064-013CT0041 → B064-013CT0042 → B064-013CT0043 → B064-013CT0044 → B064-013CT0246 → B064-013CT0297 → B064-013CT0298 → B064-013CT0299 → B064-013CT0112 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B1-SWG-64303 | -P10 | 06 |  | PE-M1-3C120-11 | PE-M1-3C120-11 | ELE-TRF-6006-001 | DONE(10/27) | DONE | 1 | 1465 | B1-SWG-64303-P1006 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-11 | 1250 | 10000 | N | 340 | TR FEEDER | B1-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B1-XFR-59601 | 10/0.4KV TRANSFORMER - ST #1A FOR BLOCK #1 | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | U1,V1,W1 | B064-013DT0059 → B064-013DT0058 → B064-013DT0057 → B064-013DT0056 → B064-013DT0260 → B064-013DT0261 → B064-013DT0262 → B064-993DT0024 → M0504 → D0531-M12 → M0510 → D0502-M12 → M0326 → D0320-M16 → M0325 → D0319-M12 → M0324 → D0327-M12 → M0321 → D0317-M12 → M0320 → D0323-M12 → M0319 → D0316-M12 → M0318 → D0315-M12 → M0315 → D0314-M12 → B159-003BT0017 → B159-003BT0016 → B159-003BT0008 → B159-003BT0009 → B159-003BT0020 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B1-SWG-64304 | -P10 | 04 |  | PE-M1-3C120-12 | PE-M1-3C120-12 | ELE-TRF-6006-002 | DONE(9/28) | DONE | 1 | 1466 | B1-SWG-64304-P1004 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-12 | 1250 | 10000 | N | 320 | TR FEEDER | B1-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B1-XFR-59602 | 10/0.4KV TRANSFORMER - ST #1B FOR BLOCK #1 | 1.1_MAIN BUILDING COMPLEX / STG #1 LER | U1,V1,W1 | B164-013AT0086 → B164-013AT0085 → B164-013AT0084 → B164-013AT0083 → B164-013AT0262 → B164-993AT0024 → M0504 → D0531-M11 → M0510 → D0502-M11 → M0326 → D0320-M17 → M0325 → D0319-M11 → M0324 → D0327-M11 → M0321 → D0317-M11 → M0320 → D0323-M11 → M0319 → D0316-M11 → M0318 → D0315-M11 → M0315 → D0314-M11 → B159-003AT0017 → B159-003AT0016 → B159-003AT0008 → B159-003AT0009 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B1-SWG-64303 | -P10 | 07 |  | PE-M1-3C120-14 | PE-M1-3C120-14 | ELE-TRF-6007 |  |  | 1 | 1467 | B1-SWG-64303-P1007 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-14 | 3000 | 10000 | N | 560 | TR FEEDER | B1-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B1-XFR-69601 | 10/0.4KV TRANSFORMER - ACC #1A FOR BLOCK #1 | 16_CEP BUILDING W/ACC LER | U1,V1,W1 | B164-013AT0059 → B164-013AT0058 → B164-013AT0275 → B164-013AT0052 → B164-013AT0228 → B164-013AT0227 → B164-013AT0226 → B164-993AT0019 → M0501 → D0503-M18 → M0502 → D0504-M18 → M0503 → D0501-M18 → M0328 → D0324-M18 → M0329 → B114-993CT0021 → B114-013CT0020 → B114-013CT0019 → B114-013CT0018 → B114-013CT0017 → B114-013CT0016 → B114-013CT0015 → B114-013CT0014 → B114-013CT0013 → B114-013CT0024 → B025-013CT0126 → B025-013CT0127 → B025-013CT0128 → B025-993CT0014 → M0105 → D0110-M11 → M0112 → D0111-M15 → M0113 → D0112-M13 → M0114 → D0114-M13 → B169-003AT0047 → B169-003AT0006 → B169-003AT0005 → B169-003AT0004 → B169-003AT0003 → B169-003AT0032 → B169-003AT0023 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B2-SWG-64304 | -P10 | 04 |  | PE-M1-3C120-25 | PE-M1-3C120-25 | ELE-TRF-6008 |  |  | 1 | 1468 | B2-SWG-64304-P1004 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-25 | 3000 | 10000 | N | 520 | TR FEEDER | B2-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1,V1,W1 | B1-XFR-69602 | 10/0.4KV TRANSFORMER - ACC #1B FOR BLOCK #1 | 16_CEP BUILDING W/ACC LER | U1,V1,W1 | B264-013PT0020 → B264-013PT0219 → B264-993PT0007 → M0405 → D0421-M21 → M0406 → D0301-M27 → M0301 → B215-993AT0001 → B215-013AT0002 → B215-013AT0003 → B215-013AT0004 → B215-013AT0005 → B215-013AT0006 → B215-013AT0007 → B215-013AT0008 → B215-013AT0009 → B215-013AT0010 → B215-013AT0011 → B215-013AT0012 → B215-013AT0023 → B025-013AT0123 → B025-013AT0124 → B025-013AT0125 → B025-993AT0013 → M0105 → D0103-M11 → M0106 → D0104-M11 → M0107 → D0105-M11 → M0108 → D0107-M11 → B169-003BT0051 → B169-003BT0027 → B169-003BT0026 → B169-003BT0025 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B1-SWG-64304 | -P10 | 05 |  | PE-M1-3C120-15 | PE-M1-3C120-15 | ELE-TRF-6008-001 |  |  | 1 | 1469 | B1-SWG-64304-P1005 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-15 | 3000 | 10000 | N | 550 | TR FEEDER | B1-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B1-XFR-69603 | 10/0.4KV TRANSFORMER - ACC #1C FOR BLOCK #1 | 16_CEP BUILDING W/ACC LER | U1,V1,W1 | B164-013AT0086 → B164-013AT0291 → B164-013AT0058 → B164-013AT0275 → B164-013AT0052 → B164-013AT0228 → B164-013AT0227 → B164-013AT0226 → B164-993AT0019 → M0501 → D0503-M21 → M0502 → D0504-M21 → M0503 → D0501-M21 → M0328 → D0324-M21 → M0329 → B114-993DT0046 → B114-013DT0045 → B114-013DT0019 → B114-013DT0018 → B114-013DT0017 → B114-013DT0016 → B114-013DT0015 → B114-013DT0014 → B114-013DT0013 → B114-013DT0024 → B025-013DT0126 → B025-013DT0127 → B025-013DT0128 → B025-993DT0014 → M0105 → D0110-M21 → M0112 → D0111-M21 → M0113 → D0112-M11 → M0114 → D0114-M11 → B169-003AT0047 → B169-003AT0006 → B169-003AT0005 → B169-003AT0004 → B169-003AT0003 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B2-SWG-64301 | -P10 | 04 |  | PE-M1-3C120-01 | PE-M1-3C120-01 | ELE-TRF-7001 |  |  | 1 | 1470 | B2-SWG-64301-P1004 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-01 | 2000 | 10000 | N | 40 | TR FEEDER | B2-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1,V1,W1 | B2-XFR-64601 | 10/0.4KV TRANSFORMER - GT / HRSG #1A FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1,V1,W1 | B264-013JT0002 → B264-013JT0003 → B264-013JT0210 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B2-SWG-64302 | -P10 | 04 |  | PE-M1-3C120-09 | PE-M1-3C120-09 | ELE-TRF-7002 |  |  | 1 | 1471 | B2-SWG-64302-P1004 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-09 | 2000 | 10000 | N | 40 | TR FEEDER | B2-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1,V1,W1 | B2-XFR-64602 | 10/0.4KV TRANSFORMER - GT / HRSG #1B FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1,V1,W1 | B264-013KT0017 → B264-013KT0018 → B264-013KT0209 → B264-013KT0046 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B2-SWG-64301 | -P10 | 05 |  | PE-M1-3C120-02 | PE-M1-3C120-02 | ELE-TRF-7003 |  |  | 1 | 1472 | B2-SWG-64301-P1005 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-02 | 2000 | 10000 | N | 60 | TR FEEDER | B2-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1,V1,W1 | B2-XFR-64603 | 10/0.4KV TRANSFORMER - GT / HRSG #2A FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1,V1,W1 | B264-013JT0002 → B264-013JT0003 → B264-013JT0210 → B264-013JT0039 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B2-SWG-64302 | -P10 | 05 |  | PE-M1-3C120-10 | PE-M1-3C120-10 | ELE-TRF-7004 |  |  | 1 | 1473 | B2-SWG-64302-P1005 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-10 | 2000 | 10000 | N | 50 | TR FEEDER | B2-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1,V1,W1 | B2-XFR-64604 | 10/0.4KV TRANSFORMER - GT / HRSG #2B FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1,V1,W1 | B264-013KT0017 → B264-013KT0018 → B264-013KT0209 → B264-013KT0047 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B2-SWG-64303 | -P10 | 05 |  | PE-M1-3C120-12 | PE-M1-3C120-12 | ELE-TRF-7007 |  |  | 1 | 1474 | B2-SWG-64303-P1005 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-12 | 2000 | 10000 | N | 40 | TR FEEDER | B2-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1,V1,W1 | B2-XFR-64605 | 10/0.4KV TRANSFORMER - EMERGENCY-A FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1,V1,W1 | B264-013AT0005 → B264-013AT0233 → B264-013AT0234 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B0-SWG-64302 | -P10 | 03 |  | PE-M1-3C120-26 | PE-M1-3C120-26 | ELE-TRF-7008 |  |  | 1 | 1475 | B0-SWG-64302-P1003 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-26 | 2000 | 10000 | N | 480 | TR FEEDER | B0-SWG-64302 | 10KV SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B2-XFR-64606 | 10/0.4KV TRANSFORMER - EMERGENCY-B FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1,V1,W1 | B064-013FT0042 → B064-013FT0041 → B064-013FT0040 → B064-013FT0039 → B064-013FT0214 → B064-013FT0215 → B064-013FT0216 → B064-013FT0219 → B064-013FT0115 → B064-013FT0259 → B025-013FT0109 → B025-013FT0110 → B025-013FT0111 → B025-013FT0112 → B025-013FT0113 → B025-013FT0114 → B025-013FT0115 → B025-013FT0116 → B025-013FT0117 → B025-013FT0118 → B025-013FT0119 → B025-013FT0120 → B025-013FT0121 → B025-013FT0122 → B264-013BT0249 → B264-013BT0236 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B2-SWG-64303 | -P10 | 06 |  | PE-M1-3C120-27 | PE-M1-3C120-27 | ELE-TRF-7008-001 |  |  | 1 | 1476 | B2-SWG-64303-P1006 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-27 | 1250 | 10000 | N | 220 | TR FEEDER | B2-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1,V1,W1 | B2-XFR-59601 | 10/0.4KV TRANSFORMER - ST #2A FOR BLOCK #2 | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | U1,V1,W1 | B264-013LT0005 → B264-013LT0215 → B264-993LT0004 → M0407 → D0302-M13 → M0302 → D0303-M13 → M0303 → D0305-M14 → M0306 → D0321-M14 → M0307 → D0306-M12 → M0308 → D0308-M12 → M0310 → D0309-M12 → M0311 → D0310-M11 → B259-003BT0017 → B259-003BT0016 → B259-003BT0008 → B259-003BT0009 → B259-003BT0020 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B2-SWG-64304 | -P10 | 05 |  | PE-M1-3C120-27 | PE-M1-3C120-27 | ELE-TRF-7008-002 |  |  | 1 | 1477 | B2-SWG-64304-P1005 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-27 | 1250 | 10000 | N | 210 | TR FEEDER | B2-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1,V1,W1 | B2-XFR-59602 | 10/0.4KV TRANSFORMER - ST #2B FOR BLOCK #2 | 1.1_MAIN BUILDING COMPLEX / STG #2 LER | U1,V1,W1 | B264-013PT0020 → B264-013PT0219 → B264-993PT0007 → M0407 → D0302-M12 → M0302 → D0303-M12 → M0303 → D0305-M13 → M0306 → D0321-M13 → M0307 → D0306-M13 → M0308 → D0308-M13 → M0310 → D0309-M11 → M0311 → D0310-M12 → B259-003AT0017 → B259-003AT0016 → B259-003AT0008 → B259-003AT0009 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B2-SWG-64303 | -P10 | 07 |  | PE-M1-3C120-28 | PE-M1-3C120-28 | ELE-TRF-7009 |  |  | 1 | 1478 | B2-SWG-64303-P1007 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-28 | 3000 | 10000 | N | 510 | TR FEEDER | B2-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1,V1,W1 | B2-XFR-69601 | 10/0.4KV TRANSFORMER - ACC #2A FOR BLOCK #2 | 16_CEP BUILDING W/ACC LER | U1,V1,W1 | B264-013LT0005 → B264-013LT0215 → B264-993LT0004 → M0405 → D0421-M22 → M0406 → D0301-M26 → M0301 → B215-993BT0001 → B215-013BT0002 → B215-013BT0003 → B215-013BT0004 → B215-013BT0005 → B215-013BT0006 → B215-013BT0007 → B215-013BT0008 → B215-013BT0009 → B215-013BT0010 → B215-013BT0011 → B215-013BT0012 → B215-013BT0023 → B025-013BT0123 → B025-013BT0124 → B025-013BT0125 → B025-993BT0013 → M0105 → D0103-M12 → M0106 → D0104-M12 → M0107 → D0105-M12 → M0108 → D0107-M12 → B169-003BT0051 → B169-003BT0027 → B169-003BT0026 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B1-SWG-64304 | -P10 | 06 |  | PE-M1-3C120-29 | PE-M1-3C120-29 | ELE-TRF-7009-001 |  |  | 1 | 1479 | B1-SWG-64304-P1006 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-29 | 3000 | 10000 | N | 520 | TR FEEDER | B1-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B2-XFR-69602 | 10/0.4KV TRANSFORMER - ACC #2B FOR BLOCK #2 | 16_CEP BUILDING W/ACC LER | U1,V1,W1 | B164-013BT0086 → B164-013BT0291 → B164-013BT0290 → B164-013BT0054 → B164-013BT0053 → B164-013BT0052 → B164-013BT0228 → B164-013BT0227 → B164-013BT0226 → B164-993BT0019 → M0501 → D0503-M22 → M0502 → D0504-M22 → M0503 → D0501-M22 → M0328 → D0324-M22 → M0329 → B114-993DT0046 → B114-013DT0045 → B114-013DT0019 → B114-013DT0018 → B114-013DT0017 → B114-013DT0016 → B114-013DT0015 → B114-013DT0014 → B114-013DT0013 → B114-013DT0024 → B025-013DT0126 → B025-013DT0127 → B025-013DT0128 → B025-993DT0014 → M0105 → D0103-M13 → M0106 → D0104-M13 → M0107 → D0105-M13 → M0108 → D0107-M13 → B169-003CT0028 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B2-SWG-64304 | -P10 | 06 |  | PE-M1-3C120-30 | PE-M1-3C120-30 | ELE-TRF-7009-002 |  |  | 1 | 1480 | B2-SWG-64304-P1006 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-30 | 3000 | 10000 | N | 520 | TR FEEDER | B2-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1,V1,W1 | B2-XFR-69603 | 10/0.4KV TRANSFORMER - ACC #2C FOR BLOCK #2 | 16_CEP BUILDING W/ACC LER | U1,V1,W1 | B264-013CT0020 → B264-013CT0231 → B264-993CT0014 → M0405 → D0421-M23 → M0406 → D0301-M25 → M0301 → B215-993BT0001 → B215-013BT0002 → B215-013BT0003 → B215-013BT0004 → B215-013BT0005 → B215-013BT0006 → B215-013BT0007 → B215-013BT0008 → B215-013BT0009 → B215-013BT0010 → B215-013BT0011 → B215-013BT0012 → B215-013BT0023 → B025-013BT0123 → B025-013BT0124 → B025-013BT0125 → B025-993BT0013 → M0105 → D0110-M22 → M0112 → D0111-M22 → M0113 → D0112-M12 → M0114 → D0114-M12 → B169-003AT0047 → B169-003AT0007 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B0-SWG-64301 | -P10 | 04 |  | PE-M1-3C120-10 | PE-M1-3C120-10 | ELE-TR-0001 |  | DONE | 1 | 1481 | B0-SWG-64301-P1004 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-10 | 2000 | 10000 | N | 50 | TR FEEDER | B0-SWG-64301 | 10KV SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B0-XFR-64601 | 10/0.4KV TRANSFORMER FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B064-013AT0040 → B064-013AT0229 → B064-013AT0027 → B064-013AT0232 → B064-013AT0013 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B0-SWG-64302 | -P10 | 04 |  | PE-M1-3C120-10 | PE-M1-3C120-10 | ELE-TR-0002 |  | DONE | 1 | 1482 | B0-SWG-64302-P1004 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-10 | 2000 | 10000 | N | 40 | TR FEEDER | B0-SWG-64302 | 10KV SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B0-XFR-64602 | 10/0.4KV TRANSFORMER FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B064-013BT0043 → B064-013BT0241 → B064-013BT0036 → B064-013BT0035 → B064-013BT0034 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B0-SWG-64301 | -P10 | 05 |  | PE-M1-3C120-11 | PE-M1-3C120-11 | ELE-TR-0003 |  | DONE | 1 | 1483 | B0-SWG-64301-P1005 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-11 | 2000 | 10000 | N | 50 | TR FEEDER | B0-SWG-64301 | 10KV SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B0-XFR-64603 | 10/0.4KV TRANSFORMER FOR COMMON EMERGENCY - A | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B064-013AT0040 → B064-013AT0229 → B064-013AT0027 → B064-013AT0232 → B064-013AT0014 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B0-SWG-64302 | -P10 | 05 |  | PE-M1-3C120-11 | PE-M1-3C120-11 | ELE-TR-0004 |  | DONE | 1 | 1484 | B0-SWG-64302-P1005 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-11 | 2000 | 10000 | N | 40 | TR FEEDER | B0-SWG-64302 | 10KV SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B0-XFR-64604 | 10/0.4KV TRANSFORMER FOR COMMON EMERGENCY - B | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B064-013BT0043 → B064-013BT0241 → B064-013BT0036 → B064-013BT0035 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B0-SWG-64301 | -P10 | 06 | Route변경 반영 | PE-M1-3C120-16 | PE-M1-3C120-16 | ELE-TR-0005 |  |  | 1 | 1485 | B0-SWG-64301-P1006 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-16 | 2500 | 10000 | N | 530 | TR FEEDER | B0-SWG-64301 | 10KV SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B0-XFR-49601 | 10/0.4KV TRANSFORMER FOR WATER TREATMENT - A | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | U1,V1,W1 | B064-013AT0040 → B064-013AT0226 → B064-993AT0019 → M0501 → D0503-M23 → M0502 → D0504-M23 → M0503 → D0501-M23 → M0328 → D0324-M23 → M0329 → B114-993AT0021 → B114-013AT0020 → B114-013AT0025 → B025-013TT0042 → B025-013TT0041 → B025-013TT0040 → B025-993TT0016 → B025-013TT0039 → B025-013TT0038 → B025-013TT0036 → B025-013TT0035 → B025-013TT0033 → B025-013TT0032 → B025-013TT0031 → B025-013TT0030 → B025-013TT0028 → B025-013TT0029 → B025-993TT0005 → M0205 → D0205-M11 → M0206 → D0203-M11 → M0207 → D0204-M11 → B049-003AT0001 → B049-003AT0003 → B049-003AT0014 → B049-003AT0010 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B0-SWG-64302 | -P10 | 06 |  | PE-M1-3C120-17 | PE-M1-3C120-17 | ELE-TR-0006 |  |  | 1 | 1486 | B0-SWG-64302-P1006 | 6/10kV CU/XLPE/CTS/LSZH | 3C x 120sqmm | PE-M1-3C120-17 | 2500 | 10000 | N | 550 | TR FEEDER | B0-SWG-64302 | 10KV SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | U1,V1,W1 | B0-XFR-49602 | 10/0.4KV TRANSFORMER FOR WATER TREATMENT - B | 10_WATER TREATMENT OF PROCESS AND DEMINERALIZED WATER ZLD BUILDING | U1,V1,W1 | B064-013BT0043 → B064-013BT0241 → B064-013BT0036 → B064-013BT0035 → B064-013BT0034 → B064-013BT0033 → B064-993BT0019 → M0501 → D0503-M24 → M0502 → D0504-M24 → M0503 → D0501-M24 → M0328 → D0324-M24 → M0329 → B114-993BT0021 → B114-013BT0020 → B114-013BT0025 → B025-013ST0042 → B025-013ST0041 → B025-013ST0040 → B025-993ST0016 → B025-013ST0039 → B025-013ST0038 → B025-013ST0036 → B025-013ST0035 → B025-013ST0033 → B025-013ST0032 → B025-013ST0031 → B025-013ST0030 → B025-013ST0028 → B025-013ST0029 → B025-993ST0005 → M0205 → D0205-M12 → M0206 → D0203-M12 → M0207 → D0204-M12 → B049-003BT0001 → B049-003BT0003 → END | [12 empty] | 2 | EPKT-17C3XIH2-G56
B1-SWG-64301 | -P10 | 06 |  | PE-M1-1C240-01 | PE-M1-1C240-01 | ELE-TIE-6001 |  | DONE | 1 | 1487 | B1-SWG-64301-P1006 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-01 | 16000 | 10000 | N | 30 | INCOMER FEEDER | B1-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1 | B0-SWG-64301 | TO 10KV SWGR COMMON - A | 1.2_LEB FOR BLOCK #1 | U1 | B064-013HT0271 → B064-013HT0231 → END | [5 empty] | Vendor |  |  | Vendor |  |  |  | 2 | EPKT-17D1XI-G58
B1-SWG-64301 | -P10 | 07 |  | PE-M1-1C240-01 | PE-M1-1C240-01 |  |  | DONE | 1 | 1488 | B1-SWG-64301-P1007 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-01 | 16000 | 10000 | N | 30 | INCOMER FEEDER | B1-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | V1 | B0-SWG-64301 | TO 10KV SWGR COMMON - A | 1.2_LEB FOR BLOCK #1 | V1 | B064-013HT0271 → B064-013HT0231 → END | [5 empty] | Vendor |  |  | Vendor |  |  |  | 2 | EPKT-17D1XI-G58
B1-SWG-64301 | -P10 | 08 |  | PE-M1-1C240-01 | PE-M1-1C240-01 |  |  | DONE | 1 | 1489 | B1-SWG-64301-P1008 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-01 | 16000 | 10000 | N | 30 | INCOMER FEEDER | B1-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | W1 | B0-SWG-64301 | TO 10KV SWGR COMMON - A | 1.2_LEB FOR BLOCK #1 | W1 | B064-013HT0271 → B064-013HT0231 → END | [5 empty] | Vendor |  |  | Vendor |  |  |  | 2 | EPKT-17D1XI-G58
B1-SWG-64301 | -P10 | 09 |  | PE-M1-1C240-01 | PE-M1-1C240-01 |  |  | DONE | 1 | 1490 | B1-SWG-64301-P1009 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-01 | 16000 | 10000 | N | 30 | INCOMER FEEDER | B1-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1 | B0-SWG-64301 | TO 10KV SWGR COMMON - A | 1.2_LEB FOR BLOCK #1 | U1 | B064-013HT0271 → B064-013HT0231 → END | [5 empty] | Vendor |  |  | Vendor |  |  |  | 2 | EPKT-17D1XI-G58
B1-SWG-64301 | -P10 | 10 |  | PE-M1-1C240-01 | PE-M1-1C240-01 |  |  | DONE | 1 | 1491 | B1-SWG-64301-P1010 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-01 | 16000 | 10000 | N | 30 | INCOMER FEEDER | B1-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | V1 | B0-SWG-64301 | TO 10KV SWGR COMMON - A | 1.2_LEB FOR BLOCK #1 | V1 | B064-013HT0271 → B064-013HT0231 → END | [5 empty] | Vendor |  |  | Vendor |  |  |  | 2 | EPKT-17D1XI-G58
B1-SWG-64301 | -P10 | 11 |  | PE-M1-1C240-01 | PE-M1-1C240-01 |  |  | DONE | 1 | 1492 | B1-SWG-64301-P1011 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-01 | 16000 | 10000 | N | 30 | INCOMER FEEDER | B1-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | W1 | B0-SWG-64301 | TO 10KV SWGR COMMON - A | 1.2_LEB FOR BLOCK #1 | W1 | B064-013HT0271 → B064-013HT0231 → END | [5 empty] | Vendor |  |  | Vendor |  |  |  | 2 | EPKT-17D1XI-G58
B1-SWG-64302 | -P10 | 06 |  | PE-M1-1C240-01 | PE-M1-1C240-01 | ELE-TIE-6002 |  | DONE | 1 | 1493 | B1-SWG-64302-P1006 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-01 | 16000 | 10000 | N | 40 | INCOMER FEEDER | B1-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1 | B0-SWG-64302 | TO 10KV SWGR COMMON - B | 1.2_LEB FOR BLOCK #1 | U1 | B064-013HT0083 → B064-013HT0272 → B064-013HT0271 → B064-013HT0231 → B064-013HT0047 → B064-013HT0048 → END | [5 empty] | Vendor |  |  | Vendor |  |  |  | 2 | EPKT-17D1XI-G58
B1-SWG-64302 | -P10 | 07 |  | PE-M1-1C240-01 | PE-M1-1C240-01 |  |  | DONE | 1 | 1494 | B1-SWG-64302-P1007 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-01 | 16000 | 10000 | N | 40 | INCOMER FEEDER | B1-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | V1 | B0-SWG-64302 | TO 10KV SWGR COMMON - B | 1.2_LEB FOR BLOCK #1 | V1 | B064-013HT0083 → B064-013HT0272 → B064-013HT0271 → B064-013HT0231 → B064-013HT0047 → B064-013HT0048 → END | [5 empty] | Vendor |  |  | Vendor |  |  |  | 2 | EPKT-17D1XI-G58
B1-SWG-64302 | -P10 | 08 |  | PE-M1-1C240-01 | PE-M1-1C240-01 |  |  | DONE | 1 | 1495 | B1-SWG-64302-P1008 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-01 | 16000 | 10000 | N | 40 | INCOMER FEEDER | B1-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | W1 | B0-SWG-64302 | TO 10KV SWGR COMMON - B | 1.2_LEB FOR BLOCK #1 | W1 | B064-013HT0083 → B064-013HT0272 → B064-013HT0271 → B064-013HT0231 → B064-013HT0047 → B064-013HT0048 → END | [5 empty] | Vendor |  |  | Vendor |  |  |  | 2 | EPKT-17D1XI-G58
B1-SWG-64302 | -P10 | 09 |  | PE-M1-1C240-01 | PE-M1-1C240-01 |  |  | DONE | 1 | 1496 | B1-SWG-64302-P1009 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-01 | 16000 | 10000 | N | 40 | INCOMER FEEDER | B1-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1 | B0-SWG-64302 | TO 10KV SWGR COMMON - B | 1.2_LEB FOR BLOCK #1 | U1 | B064-013HT0083 → B064-013HT0272 → B064-013HT0271 → B064-013HT0231 → B064-013HT0047 → B064-013HT0048 → END | [5 empty] | Vendor |  |  | Vendor |  |  |  | 2 | EPKT-17D1XI-G58
B1-SWG-64302 | -P10 | 10 |  | PE-M1-1C240-01 | PE-M1-1C240-01 |  |  | DONE | 1 | 1497 | B1-SWG-64302-P1010 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-01 | 16000 | 10000 | N | 40 | INCOMER FEEDER | B1-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | V1 | B0-SWG-64302 | TO 10KV SWGR COMMON - B | 1.2_LEB FOR BLOCK #1 | V1 | B064-013HT0083 → B064-013HT0272 → B064-013HT0271 → B064-013HT0231 → B064-013HT0047 → B064-013HT0048 → END | [5 empty] | Vendor |  |  | Vendor |  |  |  | 2 | EPKT-17D1XI-G58
B1-SWG-64302 | -P10 | 11 |  | PE-M1-1C240-01 | PE-M1-1C240-01 |  |  | DONE | 1 | 1498 | B1-SWG-64302-P1011 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-01 | 16000 | 10000 | N | 40 | INCOMER FEEDER | B1-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | W1 | B0-SWG-64302 | TO 10KV SWGR COMMON - B | 1.2_LEB FOR BLOCK #1 | W1 | B064-013HT0083 → B064-013HT0272 → B064-013HT0271 → B064-013HT0231 → B064-013HT0047 → B064-013HT0048 → END | [5 empty] | Vendor |  |  | Vendor |  |  |  | 2 | EPKT-17D1XI-G58
B0-SWG-64303 | -P10 | 01 |  | PE-M1-1C185-07 | PE-M1-1C185-07 | ELE-TIE-6003 |  | DONE | 1 | 1499 | B0-SWG-64303-P1001 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 185sqmm | PE-M1-1C185-07 | 5000 | 10000 | N | 40 | TIE FEEDER | B0-SWG-64303 | 10KV SWITCHGEAR FOR BACK UP - A | 1.2_LEB FOR BLOCK #1 | U1 | B1-SWG-64301 | TO 10KV SWGR #1 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1 | B064-013JT0061 → B064-013JT0060 → B064-013JT0059 → B064-013JT0058 → B064-013JT0057 → END | [12 empty] | 2 | EPKT-17C1XI-G57
B0-SWG-64303 | -P10 | 02 |  | PE-M1-1C185-07 | PE-M1-1C185-07 |  |  | DONE | 1 | 1500 | B0-SWG-64303-P1002 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 185sqmm | PE-M1-1C185-07 | 5000 | 10000 | N | 40 | TIE FEEDER | B0-SWG-64303 | 10KV SWITCHGEAR FOR BACK UP - A | 1.2_LEB FOR BLOCK #1 | V1 | B1-SWG-64301 | TO 10KV SWGR #1 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | V1 | B064-013JT0061 → B064-013JT0060 → B064-013JT0059 → B064-013JT0058 → B064-013JT0057 → END | [12 empty] | 2 | EPKT-17C1XI-G57
B0-SWG-64303 | -P10 | 03 |  | PE-M1-1C185-07 | PE-M1-1C185-07 |  |  | DONE | 1 | 1501 | B0-SWG-64303-P1003 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 185sqmm | PE-M1-1C185-07 | 5000 | 10000 | N | 40 | TIE FEEDER | B0-SWG-64303 | 10KV SWITCHGEAR FOR BACK UP - A | 1.2_LEB FOR BLOCK #1 | W1 | B1-SWG-64301 | TO 10KV SWGR #1 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | W1 | B064-013JT0061 → B064-013JT0060 → B064-013JT0059 → B064-013JT0058 → B064-013JT0057 → END | [12 empty] | 2 | EPKT-17C1XI-G57
B0-SWG-64303 | -P10 | 04 |  | PE-M1-1C185-07 | PE-M1-1C185-07 | ELE-TIE-6004 |  | DONE | 1 | 1502 | B0-SWG-64303-P1004 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 185sqmm | PE-M1-1C185-07 | 5000 | 10000 | N | 60 | TIE FEEDER | B0-SWG-64303 | 10KV SWITCHGEAR FOR BACK UP - A | 1.2_LEB FOR BLOCK #1 | U1 | B1-SWG-64302 | TO 10KV SWGR #2 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1 | B064-013JT0062 → B064-013JT0305 → B064-013JT0306 → B064-013JT0089 → B064-013JT0088 → B064-013JT0087 → B064-013JT0086 → B064-013JT0085 → B064-013JT0084 → END | [12 empty] | 2 | EPKT-17C1XI-G57
B0-SWG-64303 | -P10 | 05 |  | PE-M1-1C185-07 | PE-M1-1C185-07 |  |  | DONE | 1 | 1503 | B0-SWG-64303-P1005 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 185sqmm | PE-M1-1C185-07 | 5000 | 10000 | N | 60 | TIE FEEDER | B0-SWG-64303 | 10KV SWITCHGEAR FOR BACK UP - A | 1.2_LEB FOR BLOCK #1 | V1 | B1-SWG-64302 | TO 10KV SWGR #2 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | V1 | B064-013JT0062 → B064-013JT0305 → B064-013JT0306 → B064-013JT0089 → B064-013JT0088 → B064-013JT0087 → B064-013JT0086 → B064-013JT0085 → B064-013JT0084 → END | [12 empty] | 2 | EPKT-17C1XI-G57
B0-SWG-64303 | -P10 | 06 |  | PE-M1-1C185-07 | PE-M1-1C185-07 |  |  | DONE | 1 | 1504 | B0-SWG-64303-P1006 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 185sqmm | PE-M1-1C185-07 | 5000 | 10000 | N | 60 | TIE FEEDER | B0-SWG-64303 | 10KV SWITCHGEAR FOR BACK UP - A | 1.2_LEB FOR BLOCK #1 | W1 | B1-SWG-64302 | TO 10KV SWGR #2 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | W1 | B064-013JT0062 → B064-013JT0305 → B064-013JT0306 → B064-013JT0089 → B064-013JT0088 → B064-013JT0087 → B064-013JT0086 → B064-013JT0085 → B064-013JT0084 → END | [12 empty] | 2 | EPKT-17C1XI-G57
B0-SWG-64304 | -P10 | 01 |  | PE-M1-1C185-01 | PE-M1-1C185-01 | ELE-TIE-6005 |  | DONE | 1 | 1505 | B0-SWG-64304-P1001 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 185sqmm | PE-M1-1C185-01 | 5000 | 10000 | N | 40 | TIE FEEDER | B0-SWG-64304 | 10KV SWITCHGEAR FOR BACK UP - B | 1.2_LEB FOR BLOCK #1 | U1 | B1-SWG-64303 | TO 10KV SWGR #3 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1 | B064-013JT0089 → B064-013JT0088 → B064-013JT0301 → B064-013JT0060 → B064-013JT0059 → END | [12 empty] | 2 | EPKT-17C1XI-G57
B0-SWG-64304 | -P10 | 02 |  | PE-M1-1C185-01 | PE-M1-1C185-01 |  |  | DONE | 1 | 1506 | B0-SWG-64304-P1002 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 185sqmm | PE-M1-1C185-01 | 5000 | 10000 | N | 40 | TIE FEEDER | B0-SWG-64304 | 10KV SWITCHGEAR FOR BACK UP - B | 1.2_LEB FOR BLOCK #1 | V1 | B1-SWG-64303 | TO 10KV SWGR #3 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | V1 | B064-013JT0089 → B064-013JT0088 → B064-013JT0301 → B064-013JT0060 → B064-013JT0059 → END | [12 empty] | 2 | EPKT-17C1XI-G57
B0-SWG-64304 | -P10 | 03 |  | PE-M1-1C185-01 | PE-M1-1C185-01 |  |  | DONE | 1 | 1507 | B0-SWG-64304-P1003 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 185sqmm | PE-M1-1C185-01 | 5000 | 10000 | N | 40 | TIE FEEDER | B0-SWG-64304 | 10KV SWITCHGEAR FOR BACK UP - B | 1.2_LEB FOR BLOCK #1 | W1 | B1-SWG-64303 | TO 10KV SWGR #3 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | W1 | B064-013JT0089 → B064-013JT0088 → B064-013JT0301 → B064-013JT0060 → B064-013JT0059 → END | [12 empty] | 2 | EPKT-17C1XI-G57
B0-SWG-64304 | -P10 | 04 |  | PE-M1-1C185-01 | PE-M1-1C185-01 | ELE-TIE-6006 |  | DONE | 1 | 1508 | B0-SWG-64304-P1004 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 185sqmm | PE-M1-1C185-01 | 5000 | 10000 | N | 40 | TIE FEEDER | B0-SWG-64304 | 10KV SWITCHGEAR FOR BACK UP - B | 1.2_LEB FOR BLOCK #1 | U1 | B1-SWG-64304 | TO 10KV SWGR #4 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1 | B064-013JT0089 → B064-013JT0088 → B064-013JT0087 → B064-013JT0086 → END | [12 empty] | 2 | EPKT-17C1XI-G57
B0-SWG-64304 | -P10 | 05 |  | PE-M1-1C185-01 | PE-M1-1C185-01 |  |  | DONE | 1 | 1509 | B0-SWG-64304-P1005 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 185sqmm | PE-M1-1C185-01 | 5000 | 10000 | N | 40 | TIE FEEDER | B0-SWG-64304 | 10KV SWITCHGEAR FOR BACK UP - B | 1.2_LEB FOR BLOCK #1 | V1 | B1-SWG-64304 | TO 10KV SWGR #4 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | V1 | B064-013JT0089 → B064-013JT0088 → B064-013JT0087 → B064-013JT0086 → END | [12 empty] | 2 | EPKT-17C1XI-G57
B0-SWG-64304 | -P10 | 06 |  | PE-M1-1C185-01 | PE-M1-1C185-01 |  |  | DONE | 1 | 1510 | B0-SWG-64304-P1006 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 185sqmm | PE-M1-1C185-01 | 5000 | 10000 | N | 40 | TIE FEEDER | B0-SWG-64304 | 10KV SWITCHGEAR FOR BACK UP - B | 1.2_LEB FOR BLOCK #1 | W1 | B1-SWG-64304 | TO 10KV SWGR #4 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | W1 | B064-013JT0089 → B064-013JT0088 → B064-013JT0087 → B064-013JT0086 → END | [12 empty] | 2 | EPKT-17C1XI-G57
B2-SWG-64301 | -P10 | 06 |  | PE-M1-1C240-02 | PE-M1-1C240-02 | ELE-TIE-7002 |  |  | 1 | 1511 | B2-SWG-64301-P1006 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-02 | 16000 | 10000 | N | 500 | INCOMER FEEDER | B2-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1 | B0-SWG-64301 | TO 10KV SWGR COMMON - A | 1.2_LEB FOR BLOCK #1 | U1 | B264-013AT0004 → B264-013AT0005 → B264-013AT0233 → B264-013AT0234 → B264-013AT0235 → B264-013AT0236 → B264-013AT0249 → B025-013ET0122 → B025-013ET0121 → B025-013ET0120 → B025-013ET0119 → B025-013ET0118 → B025-013ET0117 → B025-013ET0116 → B025-013ET0115 → B025-013ET0114 → B025-013ET0113 → B025-013ET0112 → B025-013ET0111 → B025-013ET0110 → B025-013ET0109 → B064-013GT0259 → B064-013GT0115 → B064-013GT0219 → B064-013GT0216 → B064-013GT0215 → B064-013GT0214 → B064-013GT0045 → B064-013GT0046 → END | [5 empty] | Vendor |  |  | Vendor |  |  |  | 2 | EPKT-17C1XI-G57
B2-SWG-64301 | -P10 | 07 |  | PE-M1-1C240-03 | PE-M1-1C240-03 |  |  |  | 1 | 1512 | B2-SWG-64301-P1007 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-03 | 16000 | 10000 | N | 500 | INCOMER FEEDER | B2-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | V1 | B0-SWG-64301 | TO 10KV SWGR COMMON - A | 1.2_LEB FOR BLOCK #1 | V1 | B264-013AT0004 → B264-013AT0005 → B264-013AT0233 → B264-013AT0234 → B264-013AT0235 → B264-013AT0236 → B264-013AT0249 → B025-013ET0122 → B025-013ET0121 → B025-013ET0120 → B025-013ET0119 → B025-013ET0118 → B025-013ET0117 → B025-013ET0116 → B025-013ET0115 → B025-013ET0114 → B025-013ET0113 → B025-013ET0112 → B025-013ET0111 → B025-013ET0110 → B025-013ET0109 → B064-013GT0259 → B064-013GT0115 → B064-013GT0219 → B064-013GT0216 → B064-013GT0215 → B064-013GT0214 → B064-013GT0045 → B064-013GT0046 → END | [5 empty] | Vendor |  |  | Vendor |  |  |  | 2 | EPKT-17C1XI-G57
B2-SWG-64301 | -P10 | 08 |  | PE-M1-1C240-04 | PE-M1-1C240-04 |  |  |  | 1 | 1513 | B2-SWG-64301-P1008 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-04 | 16000 | 10000 | N | 500 | INCOMER FEEDER | B2-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | W1 | B0-SWG-64301 | TO 10KV SWGR COMMON - A | 1.2_LEB FOR BLOCK #1 | W1 | B264-013AT0004 → B264-013AT0005 → B264-013AT0233 → B264-013AT0234 → B264-013AT0235 → B264-013AT0236 → B264-013AT0249 → B025-013ET0122 → B025-013ET0121 → B025-013ET0120 → B025-013ET0119 → B025-013ET0118 → B025-013ET0117 → B025-013ET0116 → B025-013ET0115 → B025-013ET0114 → B025-013ET0113 → B025-013ET0112 → B025-013ET0111 → B025-013ET0110 → B025-013ET0109 → B064-013GT0259 → B064-013GT0115 → B064-013GT0219 → B064-013GT0216 → B064-013GT0215 → B064-013GT0214 → B064-013GT0045 → B064-013GT0046 → END | [5 empty] | Vendor |  |  | Vendor |  |  |  | 2 | EPKT-17C1XI-G57
B2-SWG-64301 | -P10 | 09 |  | PE-M1-1C240-05 | PE-M1-1C240-05 |  |  |  | 1 | 1514 | B2-SWG-64301-P1009 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-05 | 16000 | 10000 | N | 500 | INCOMER FEEDER | B2-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1 | B0-SWG-64301 | TO 10KV SWGR COMMON - A | 1.2_LEB FOR BLOCK #1 | U1 | B264-013AT0004 → B264-013AT0005 → B264-013AT0233 → B264-013AT0234 → B264-013AT0235 → B264-013AT0236 → B264-013AT0249 → B025-013ET0122 → B025-013ET0121 → B025-013ET0120 → B025-013ET0119 → B025-013ET0118 → B025-013ET0117 → B025-013ET0116 → B025-013ET0115 → B025-013ET0114 → B025-013ET0113 → B025-013ET0112 → B025-013ET0111 → B025-013ET0110 → B025-013ET0109 → B064-013GT0259 → B064-013GT0115 → B064-013GT0219 → B064-013GT0216 → B064-013GT0215 → B064-013GT0214 → B064-013GT0045 → B064-013GT0046 → END | [5 empty] | Vendor |  |  | Vendor |  |  |  | 2 | EPKT-17C1XI-G57
B2-SWG-64301 | -P10 | 10 |  | PE-M1-1C240-06 | PE-M1-1C240-06 |  |  |  | 1 | 1515 | B2-SWG-64301-P1010 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-06 | 16000 | 10000 | N | 500 | INCOMER FEEDER | B2-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | V1 | B0-SWG-64301 | TO 10KV SWGR COMMON - A | 1.2_LEB FOR BLOCK #1 | V1 | B264-013AT0004 → B264-013AT0005 → B264-013AT0233 → B264-013AT0234 → B264-013AT0235 → B264-013AT0236 → B264-013AT0249 → B025-013ET0122 → B025-013ET0121 → B025-013ET0120 → B025-013ET0119 → B025-013ET0118 → B025-013ET0117 → B025-013ET0116 → B025-013ET0115 → B025-013ET0114 → B025-013ET0113 → B025-013ET0112 → B025-013ET0111 → B025-013ET0110 → B025-013ET0109 → B064-013GT0259 → B064-013GT0115 → B064-013GT0219 → B064-013GT0216 → B064-013GT0215 → B064-013GT0214 → B064-013GT0045 → B064-013GT0046 → END | [5 empty] | Vendor |  |  | Vendor |  |  |  | 2 | EPKT-17C1XI-G57
B2-SWG-64301 | -P10 | 11 | ADD | PE-M1-1C240-07 | PE-M1-1C240-14 |  |  |  | 1 | 1516 | B2-SWG-64301-P1011 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-14 | 16000 | 10000 | N | 500 | INCOMER FEEDER | B2-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | W1 | B0-SWG-64301 | TO 10KV SWGR COMMON - A | 1.2_LEB FOR BLOCK #1 | W1 | B264-013AT0004 → B264-013AT0005 → B264-013AT0233 → B264-013AT0234 → B264-013AT0235 → B264-013AT0236 → B264-013AT0249 → B025-013ET0122 → B025-013ET0121 → B025-013ET0120 → B025-013ET0119 → B025-013ET0118 → B025-013ET0117 → B025-013ET0116 → B025-013ET0115 → B025-013ET0114 → B025-013ET0113 → B025-013ET0112 → B025-013ET0111 → B025-013ET0110 → B025-013ET0109 → B064-013GT0259 → B064-013GT0115 → B064-013GT0219 → B064-013GT0216 → B064-013GT0215 → B064-013GT0214 → B064-013GT0045 → B064-013GT0046 → END | [5 empty] | Vendor |  |  | Vendor |  |  |  | 2 | EPKT-17C1XI-G57
B2-SWG-64302 | -P10 | 06 | ADD | PE-M1-1C240-08 | PE-M1-1C240-15 | ELE-TIE-7004 |  |  | 1 | 1517 | B2-SWG-64302-P1006 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-15 | 16000 | 10000 | N | 510 | INCOMER FEEDER | B2-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1 | B0-SWG-64302 | TO 10KV SWGR COMMON - B | 1.2_LEB FOR BLOCK #1 | U1 | B264-013BT0019 → B264-013BT0020 → B264-013BT0234 → B264-013BT0235 → B264-013BT0236 → B264-013BT0249 → B025-013FT0122 → B025-013FT0121 → B025-013FT0120 → B025-013FT0119 → B025-013FT0118 → B025-013FT0117 → B025-013FT0116 → B025-013FT0115 → B025-013FT0114 → B025-013FT0113 → B025-013FT0112 → B025-013FT0111 → B025-013FT0110 → B025-013FT0109 → B064-013FT0259 → B064-013FT0115 → B064-013FT0219 → B064-013FT0216 → B064-013FT0215 → B064-013GT0214 → B064-013FT0039 → B064-013FT0040 → B064-013FT0041 → B064-013FT0042 → END | [5 empty] | Vendor |  |  | Vendor |  |  |  | 2 | EPKT-17C1XI-G57
B2-SWG-64302 | -P10 | 07 | ADD | PE-M1-1C240-09 | PE-M1-1C240-16 |  |  |  | 1 | 1518 | B2-SWG-64302-P1007 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-16 | 16000 | 10000 | N | 510 | INCOMER FEEDER | B2-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | V1 | B0-SWG-64302 | TO 10KV SWGR COMMON - B | 1.2_LEB FOR BLOCK #1 | V1 | B264-013BT0019 → B264-013BT0020 → B264-013BT0234 → B264-013BT0235 → B264-013BT0236 → B264-013BT0249 → B025-013FT0122 → B025-013FT0121 → B025-013FT0120 → B025-013FT0119 → B025-013FT0118 → B025-013FT0117 → B025-013FT0116 → B025-013FT0115 → B025-013FT0114 → B025-013FT0113 → B025-013FT0112 → B025-013FT0111 → B025-013FT0110 → B025-013FT0109 → B064-013FT0259 → B064-013FT0115 → B064-013FT0219 → B064-013FT0216 → B064-013FT0215 → B064-013GT0214 → B064-013FT0039 → B064-013FT0040 → B064-013FT0041 → B064-013FT0042 → END | [5 empty] | Vendor |  |  | Vendor |  |  |  | 2 | EPKT-17C1XI-G57
B2-SWG-64302 | -P10 | 08 | ADD | PE-M1-1C240-10 | PE-M1-1C240-17 |  |  |  | 1 | 1519 | B2-SWG-64302-P1008 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-17 | 16000 | 10000 | N | 510 | INCOMER FEEDER | B2-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | W1 | B0-SWG-64302 | TO 10KV SWGR COMMON - B | 1.2_LEB FOR BLOCK #1 | W1 | B264-013BT0019 → B264-013BT0020 → B264-013BT0234 → B264-013BT0235 → B264-013BT0236 → B264-013BT0249 → B025-013FT0122 → B025-013FT0121 → B025-013FT0120 → B025-013FT0119 → B025-013FT0118 → B025-013FT0117 → B025-013FT0116 → B025-013FT0115 → B025-013FT0114 → B025-013FT0113 → B025-013FT0112 → B025-013FT0111 → B025-013FT0110 → B025-013FT0109 → B064-013FT0259 → B064-013FT0115 → B064-013FT0219 → B064-013FT0216 → B064-013FT0215 → B064-013GT0214 → B064-013FT0039 → B064-013FT0040 → B064-013FT0041 → B064-013FT0042 → END | [5 empty] | Vendor |  |  | Vendor |  |  |  | 2 | EPKT-17C1XI-G57
B2-SWG-64302 | -P10 | 09 | ADD | PE-M1-1C240-11 | PE-M1-1C240-18 |  |  |  | 1 | 1520 | B2-SWG-64302-P1009 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-18 | 16000 | 10000 | N | 510 | INCOMER FEEDER | B2-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1 | B0-SWG-64302 | TO 10KV SWGR COMMON - B | 1.2_LEB FOR BLOCK #1 | U1 | B264-013BT0019 → B264-013BT0020 → B264-013BT0234 → B264-013BT0235 → B264-013BT0236 → B264-013BT0249 → B025-013FT0122 → B025-013FT0121 → B025-013FT0120 → B025-013FT0119 → B025-013FT0118 → B025-013FT0117 → B025-013FT0116 → B025-013FT0115 → B025-013FT0114 → B025-013FT0113 → B025-013FT0112 → B025-013FT0111 → B025-013FT0110 → B025-013FT0109 → B064-013FT0259 → B064-013FT0115 → B064-013FT0219 → B064-013FT0216 → B064-013FT0215 → B064-013GT0214 → B064-013FT0039 → B064-013FT0040 → B064-013FT0041 → B064-013FT0042 → END | [5 empty] | Vendor |  |  | Vendor |  |  |  | 2 | EPKT-17C1XI-G57
B2-SWG-64302 | -P10 | 10 | ADD | PE-M1-1C240-12 | PE-M1-1C240-19 |  |  |  | 1 | 1521 | B2-SWG-64302-P1010 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-19 | 16000 | 10000 | N | 510 | INCOMER FEEDER | B2-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | V1 | B0-SWG-64302 | TO 10KV SWGR COMMON - B | 1.2_LEB FOR BLOCK #1 | V1 | B264-013BT0019 → B264-013BT0020 → B264-013BT0234 → B264-013BT0235 → B264-013BT0236 → B264-013BT0249 → B025-013FT0122 → B025-013FT0121 → B025-013FT0120 → B025-013FT0119 → B025-013FT0118 → B025-013FT0117 → B025-013FT0116 → B025-013FT0115 → B025-013FT0114 → B025-013FT0113 → B025-013FT0112 → B025-013FT0111 → B025-013FT0110 → B025-013FT0109 → B064-013FT0259 → B064-013FT0115 → B064-013FT0219 → B064-013FT0216 → B064-013FT0215 → B064-013GT0214 → B064-013FT0039 → B064-013FT0040 → B064-013FT0041 → B064-013FT0042 → END | [5 empty] | Vendor |  |  | Vendor |  |  |  | 2 | EPKT-17C1XI-G57
B2-SWG-64302 | -P10 | 11 | ADD | PE-M1-1C240-13 | PE-M1-1C240-20 |  |  |  | 1 | 1522 | B2-SWG-64302-P1011 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-20 | 16000 | 10000 | N | 510 | INCOMER FEEDER | B2-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | W1 | B0-SWG-64302 | TO 10KV SWGR COMMON - B | 1.2_LEB FOR BLOCK #1 | W1 | B264-013BT0019 → B264-013BT0020 → B264-013BT0234 → B264-013BT0235 → B264-013BT0236 → B264-013BT0249 → B025-013FT0122 → B025-013FT0121 → B025-013FT0120 → B025-013FT0119 → B025-013FT0118 → B025-013FT0117 → B025-013FT0116 → B025-013FT0115 → B025-013FT0114 → B025-013FT0113 → B025-013FT0112 → B025-013FT0111 → B025-013FT0110 → B025-013FT0109 → B064-013FT0259 → B064-013FT0115 → B064-013FT0219 → B064-013FT0216 → B064-013FT0215 → B064-013GT0214 → B064-013FT0039 → B064-013FT0040 → B064-013FT0041 → B064-013FT0042 → END | [5 empty] | Vendor |  |  | Vendor |  |  |  | 2 | EPKT-17C1XI-G57
B0-SWG-64303 | -P10 | 07 |  | PE-M1-1C185-07 | PE-M1-1C185-07 | ELE-TIE-7006 |  |  | 1 | 1523 | B0-SWG-64303-P1007 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 185sqmm | PE-M1-1C185-07 | 5000 | 10000 | N | 520 | TIE FEEDER | B0-SWG-64303 | 10KV SWITCHGEAR FOR BACK UP - A | 1.2_LEB FOR BLOCK #1 | U1 | B2-SWG-64301 | TO 10KV SWGR #1 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1 | B064-013DT0061 → B064-013DT0062 → B064-013DT0305 → B064-013DT0306 → B064-013DT0307 → B064-013DT0308 → B064-013DT0121 → B064-013DT0120 → B064-013DT0119 → B064-013DT0118 → B064-013DT0117 → B064-013DT0116 → B064-013DT0263 → B025-013GT0093 → B025-013GT0094 → B025-013GT0095 → B025-013GT0096 → B025-013GT0097 → B025-013GT0098 → B025-013GT0099 → B025-013GT0100 → B025-013GT0101 → B025-013GT0102 → B025-013GT0103 → B025-013GT0104 → B025-013GT0105 → B025-013GT0106 → B264-013CT0232 → B264-013CT0231 → B264-013CT0020 → B264-013CT0019 → B264-013CT0210 → B264-013CT0003 → END | [12 empty] | 2 | EPKT-17C1XI-G57
B0-SWG-64303 | -P10 | 08 |  | PE-M1-1C185-02 | PE-M1-1C185-02 |  |  |  | 1 | 1524 | B0-SWG-64303-P1008 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 185sqmm | PE-M1-1C185-02 | 5000 | 10000 | N | 520 | TIE FEEDER | B0-SWG-64303 | 10KV SWITCHGEAR FOR BACK UP - A | 1.2_LEB FOR BLOCK #1 | V1 | B2-SWG-64301 | TO 10KV SWGR #1 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | V1 | B064-013DT0061 → B064-013DT0062 → B064-013DT0305 → B064-013DT0306 → B064-013DT0307 → B064-013DT0308 → B064-013DT0121 → B064-013DT0120 → B064-013DT0119 → B064-013DT0118 → B064-013DT0117 → B064-013DT0116 → B064-013DT0263 → B025-013GT0093 → B025-013GT0094 → B025-013GT0095 → B025-013GT0096 → B025-013GT0097 → B025-013GT0098 → B025-013GT0099 → B025-013GT0100 → B025-013GT0101 → B025-013GT0102 → B025-013GT0103 → B025-013GT0104 → B025-013GT0105 → B025-013GT0106 → B264-013CT0232 → B264-013CT0231 → B264-013CT0020 → B264-013CT0019 → B264-013CT0210 → B264-013CT0003 → END | [12 empty] | 2 | EPKT-17C1XI-G57
B0-SWG-64303 | -P10 | 09 |  | PE-M1-1C185-03 | PE-M1-1C185-03 |  |  |  | 1 | 1525 | B0-SWG-64303-P1009 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 185sqmm | PE-M1-1C185-03 | 5000 | 10000 | N | 520 | TIE FEEDER | B0-SWG-64303 | 10KV SWITCHGEAR FOR BACK UP - A | 1.2_LEB FOR BLOCK #1 | W1 | B2-SWG-64301 | TO 10KV SWGR #1 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | W1 | B064-013DT0061 → B064-013DT0062 → B064-013DT0305 → B064-013DT0306 → B064-013DT0307 → B064-013DT0308 → B064-013DT0121 → B064-013DT0120 → B064-013DT0119 → B064-013DT0118 → B064-013DT0117 → B064-013DT0116 → B064-013DT0263 → B025-013GT0093 → B025-013GT0094 → B025-013GT0095 → B025-013GT0096 → B025-013GT0097 → B025-013GT0098 → B025-013GT0099 → B025-013GT0100 → B025-013GT0101 → B025-013GT0102 → B025-013GT0103 → B025-013GT0104 → B025-013GT0105 → B025-013GT0106 → B264-013CT0232 → B264-013CT0231 → B264-013CT0020 → B264-013CT0019 → B264-013CT0210 → B264-013CT0003 → END | [12 empty] | 2 | EPKT-17C1XI-G57
B0-SWG-64303 | -P10 | 10 |  | PE-M1-1C185-04 | PE-M1-1C185-04 | ELE-TIE-7007 |  |  | 1 | 1526 | B0-SWG-64303-P1010 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 185sqmm | PE-M1-1C185-04 | 5000 | 10000 | N | 510 | TIE FEEDER | B0-SWG-64303 | 10KV SWITCHGEAR FOR BACK UP - A | 1.2_LEB FOR BLOCK #1 | U1 | B2-SWG-64302 | TO 10KV SWGR #2 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1 | B064-013DT0062 → B064-013DT0305 → B064-013DT0306 → B064-013DT0307 → B064-013DT0308 → B064-013DT0121 → B064-013DT0120 → B064-013DT0119 → B064-013DT0118 → B064-013DT0117 → B064-013DT0116 → B064-013DT0263 → B025-013GT0093 → B025-013GT0094 → B025-013GT0095 → B025-013GT0096 → B025-013GT0097 → B025-013GT0098 → B025-013GT0099 → B025-013GT0100 → B025-013GT0101 → B025-013GT0102 → B025-013GT0103 → B025-013GT0104 → B025-013GT0105 → B025-013GT0106 → B264-013CT0232 → B264-013CT0231 → B264-013CT0020 → B264-013CT0019 → B264-013CT0018 → END | [12 empty] | 2 | EPKT-17C1XI-G57
B0-SWG-64303 | -P10 | 11 |  | PE-M1-1C185-05 | PE-M1-1C185-05 |  |  |  | 1 | 1527 | B0-SWG-64303-P1011 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 185sqmm | PE-M1-1C185-05 | 5000 | 10000 | N | 510 | TIE FEEDER | B0-SWG-64303 | 10KV SWITCHGEAR FOR BACK UP - A | 1.2_LEB FOR BLOCK #1 | V1 | B2-SWG-64302 | TO 10KV SWGR #2 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | V1 | B064-013DT0062 → B064-013DT0305 → B064-013DT0306 → B064-013DT0307 → B064-013DT0308 → B064-013DT0121 → B064-013DT0120 → B064-013DT0119 → B064-013DT0118 → B064-013DT0117 → B064-013DT0116 → B064-013DT0263 → B025-013GT0093 → B025-013GT0094 → B025-013GT0095 → B025-013GT0096 → B025-013GT0097 → B025-013GT0098 → B025-013GT0099 → B025-013GT0100 → B025-013GT0101 → B025-013GT0102 → B025-013GT0103 → B025-013GT0104 → B025-013GT0105 → B025-013GT0106 → B264-013CT0232 → B264-013CT0231 → B264-013CT0020 → B264-013CT0019 → B264-013CT0018 → END | [12 empty] | 2 | EPKT-17C1XI-G57
B0-SWG-64303 | -P10 | 12 |  | PE-M1-1C185-06 | PE-M1-1C185-06 |  |  |  | 1 | 1528 | B0-SWG-64303-P1012 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 185sqmm | PE-M1-1C185-06 | 5000 | 10000 | N | 510 | TIE FEEDER | B0-SWG-64303 | 10KV SWITCHGEAR FOR BACK UP - A | 1.2_LEB FOR BLOCK #1 | W1 | B2-SWG-64302 | TO 10KV SWGR #2 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | W1 | B064-013DT0062 → B064-013DT0305 → B064-013DT0306 → B064-013DT0307 → B064-013DT0308 → B064-013DT0121 → B064-013DT0120 → B064-013DT0119 → B064-013DT0118 → B064-013DT0117 → B064-013DT0116 → B064-013DT0263 → B025-013GT0093 → B025-013GT0094 → B025-013GT0095 → B025-013GT0096 → B025-013GT0097 → B025-013GT0098 → B025-013GT0099 → B025-013GT0100 → B025-013GT0101 → B025-013GT0102 → B025-013GT0103 → B025-013GT0104 → B025-013GT0105 → B025-013GT0106 → B264-013CT0232 → B264-013CT0231 → B264-013CT0020 → B264-013CT0019 → B264-013CT0018 → END | [12 empty] | 2 | EPKT-17C1XI-G57
B0-SWG-64304 | -P10 | 07 |  | PE-M1-1C185-04 | PE-M1-1C185-04 | ELE-TIE-7008 |  |  | 1 | 1529 | B0-SWG-64304-P1007 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 185sqmm | PE-M1-1C185-04 | 5000 | 10000 | N | 500 | TIE FEEDER | B0-SWG-64304 | 10KV SWITCHGEAR FOR BACK UP - B | 1.2_LEB FOR BLOCK #1 | U1 | B2-SWG-64303 | TO 10KV SWGR #3 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1 | B064-013ET0088 → B064-013ET0089 → B064-013ET0307 → B064-013ET0308 → B064-013ET0121 → B064-013ET0120 → B064-013ET0119 → B064-013ET0118 → B064-013ET0117 → B064-013ET0116 → B064-013ET0263 → B025-013HT0093 → B025-013HT0094 → B025-013HT0095 → B025-013HT0096 → B025-013HT0097 → B025-013HT0098 → B025-013HT0099 → B025-013HT0100 → B025-013HT0101 → B025-013HT0102 → B025-013HT0103 → B025-013HT0104 → B025-013HT0105 → B025-013HT0106 → B264-013DT0232 → B264-013DT0231 → B264-013DT0230 → B264-013DT0005 → END | [12 empty] | 2 | EPKT-17C1XI-G57
B0-SWG-64304 | -P10 | 08 |  | PE-M1-1C185-05 | PE-M1-1C185-05 |  |  |  | 1 | 1530 | B0-SWG-64304-P1008 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 185sqmm | PE-M1-1C185-05 | 5000 | 10000 | N | 500 | TIE FEEDER | B0-SWG-64304 | 10KV SWITCHGEAR FOR BACK UP - B | 1.2_LEB FOR BLOCK #1 | V1 | B2-SWG-64303 | TO 10KV SWGR #3 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | V1 | B064-013ET0088 → B064-013ET0089 → B064-013ET0307 → B064-013ET0308 → B064-013ET0121 → B064-013ET0120 → B064-013ET0119 → B064-013ET0118 → B064-013ET0117 → B064-013ET0116 → B064-013ET0263 → B025-013HT0093 → B025-013HT0094 → B025-013HT0095 → B025-013HT0096 → B025-013HT0097 → B025-013HT0098 → B025-013HT0099 → B025-013HT0100 → B025-013HT0101 → B025-013HT0102 → B025-013HT0103 → B025-013HT0104 → B025-013HT0105 → B025-013HT0106 → B264-013DT0232 → B264-013DT0231 → B264-013DT0230 → B264-013DT0005 → END | [12 empty] | 2 | EPKT-17C1XI-G57
B0-SWG-64304 | -P10 | 09 |  | PE-M1-1C185-06 | PE-M1-1C185-06 |  |  |  | 1 | 1531 | B0-SWG-64304-P1009 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 185sqmm | PE-M1-1C185-06 | 5000 | 10000 | N | 500 | TIE FEEDER | B0-SWG-64304 | 10KV SWITCHGEAR FOR BACK UP - B | 1.2_LEB FOR BLOCK #1 | W1 | B2-SWG-64303 | TO 10KV SWGR #3 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | W1 | B064-013ET0088 → B064-013ET0089 → B064-013ET0307 → B064-013ET0308 → B064-013ET0121 → B064-013ET0120 → B064-013ET0119 → B064-013ET0118 → B064-013ET0117 → B064-013ET0116 → B064-013ET0263 → B025-013HT0093 → B025-013HT0094 → B025-013HT0095 → B025-013HT0096 → B025-013HT0097 → B025-013HT0098 → B025-013HT0099 → B025-013HT0100 → B025-013HT0101 → B025-013HT0102 → B025-013HT0103 → B025-013HT0104 → B025-013HT0105 → B025-013HT0106 → B264-013DT0232 → B264-013DT0231 → B264-013DT0230 → B264-013DT0005 → END | [12 empty] | 2 | EPKT-17C1XI-G57
B0-SWG-64304 | -P10 | 10 |  | PE-M1-1C185-01 | PE-M1-1C185-01 | ELE-TIE-7009 |  |  | 1 | 1532 | B0-SWG-64304-P1010 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 185sqmm | PE-M1-1C185-01 | 5000 | 10000 | N | 490 | TIE FEEDER | B0-SWG-64304 | 10KV SWITCHGEAR FOR BACK UP - B | 1.2_LEB FOR BLOCK #1 | U1 | B2-SWG-64304 | TO 10KV SWGR #4 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1 | B064-013ET0089 → B064-013ET0307 → B064-013ET0308 → B064-013ET0121 → B064-013ET0120 → B064-013ET0119 → B064-013ET0118 → B064-013ET0117 → B064-013ET0116 → B064-013ET0263 → B025-013HT0093 → B025-013HT0094 → B025-013HT0095 → B025-013HT0096 → B025-013HT0097 → B025-013HT0098 → B025-013HT0099 → B025-013HT0100 → B025-013HT0101 → B025-013HT0102 → B025-013HT0103 → B025-013HT0104 → B025-013HT0105 → B025-013HT0106 → B264-013DT0232 → B264-013DT0231 → B264-013DT0020 → END | [12 empty] | 2 | EPKT-17C1XI-G57
B0-SWG-64304 | -P10 | 11 |  | PE-M1-1C185-02 | PE-M1-1C185-02 |  |  |  | 1 | 1533 | B0-SWG-64304-P1011 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 185sqmm | PE-M1-1C185-02 | 5000 | 10000 | N | 490 | TIE FEEDER | B0-SWG-64304 | 10KV SWITCHGEAR FOR BACK UP - B | 1.2_LEB FOR BLOCK #1 | V1 | B2-SWG-64304 | TO 10KV SWGR #4 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | V1 | B064-013ET0089 → B064-013ET0307 → B064-013ET0308 → B064-013ET0121 → B064-013ET0120 → B064-013ET0119 → B064-013ET0118 → B064-013ET0117 → B064-013ET0116 → B064-013ET0263 → B025-013HT0093 → B025-013HT0094 → B025-013HT0095 → B025-013HT0096 → B025-013HT0097 → B025-013HT0098 → B025-013HT0099 → B025-013HT0100 → B025-013HT0101 → B025-013HT0102 → B025-013HT0103 → B025-013HT0104 → B025-013HT0105 → B025-013HT0106 → B264-013DT0232 → B264-013DT0231 → B264-013DT0020 → END | [12 empty] | 2 | EPKT-17C1XI-G57
B0-SWG-64304 | -P10 | 12 |  | PE-M1-1C185-03 | PE-M1-1C185-03 |  |  |  | 1 | 1534 | B0-SWG-64304-P1012 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 185sqmm | PE-M1-1C185-03 | 5000 | 10000 | N | 490 | TIE FEEDER | B0-SWG-64304 | 10KV SWITCHGEAR FOR BACK UP - B | 1.2_LEB FOR BLOCK #1 | W1 | B2-SWG-64304 | TO 10KV SWGR #4 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | W1 | B064-013ET0089 → B064-013ET0307 → B064-013ET0308 → B064-013ET0121 → B064-013ET0120 → B064-013ET0119 → B064-013ET0118 → B064-013ET0117 → B064-013ET0116 → B064-013ET0263 → B025-013HT0093 → B025-013HT0094 → B025-013HT0095 → B025-013HT0096 → B025-013HT0097 → B025-013HT0098 → B025-013HT0099 → B025-013HT0100 → B025-013HT0101 → B025-013HT0102 → B025-013HT0103 → B025-013HT0104 → B025-013HT0105 → B025-013HT0106 → B264-013DT0232 → B264-013DT0231 → B264-013DT0020 → END | [12 empty] | 2 | EPKT-17C1XI-G57
B1-XFR-20301 | -P10 | 01 |  | PE-M1-1C300-01 | PE-M1-1C300-01 | ELE-INT-6001 |  |  | 1 | 1535 | B1-XFR-20301-P1001 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-01 | 16000 | 10000 | N | 150 | INCOMER FEEDER | B1-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-1 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | U1 | B1-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1 | PSP/INTEGRA TRAY → B025-013LT0129 → B025-013LT0072 → B025-013LT0071 → B025-013LT0070 → B025-013LT0090 → B164-013ET0285 → B164-013ET0284 → B164-013ET0283 → B164-013ET0077 → B164-013ET0280 → B164-013ET0066 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-20301 | -P10 | 02 |  | PE-M1-1C300-01 | PE-M1-1C300-01 |  |  |  | 1 | 1536 | B1-XFR-20301-P1002 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-01 | 16000 | 10000 | N | 150 | INCOMER FEEDER | B1-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-1 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | V1 | B1-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | V1 | PSP/INTEGRA TRAY → B025-013LT0129 → B025-013LT0072 → B025-013LT0071 → B025-013LT0070 → B025-013LT0090 → B164-013ET0285 → B164-013ET0284 → B164-013ET0283 → B164-013ET0077 → B164-013ET0280 → B164-013ET0066 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-20301 | -P10 | 03 |  | PE-M1-1C300-01 | PE-M1-1C300-01 |  |  |  | 1 | 1537 | B1-XFR-20301-P1003 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-01 | 16000 | 10000 | N | 150 | INCOMER FEEDER | B1-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-1 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | W1 | B1-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | W1 | PSP/INTEGRA TRAY → B025-013LT0129 → B025-013LT0072 → B025-013LT0071 → B025-013LT0070 → B025-013LT0090 → B164-013ET0285 → B164-013ET0284 → B164-013ET0283 → B164-013ET0077 → B164-013ET0280 → B164-013ET0066 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-20301 | -P10 | 04 |  | PE-M1-1C300-01 | PE-M1-1C300-01 |  |  |  | 1 | 1538 | B1-XFR-20301-P1004 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-01 | 16000 | 10000 | N | 150 | INCOMER FEEDER | B1-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-1 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | U1 | B1-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1 | PSP/INTEGRA TRAY → B025-013LT0129 → B025-013LT0072 → B025-013LT0071 → B025-013LT0070 → B025-013LT0090 → B164-013ET0285 → B164-013ET0284 → B164-013ET0283 → B164-013ET0077 → B164-013ET0280 → B164-013ET0066 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-20301 | -P10 | 05 |  | PE-M1-1C300-07 | PE-M1-1C300-07 |  |  |  | 1 | 1539 | B1-XFR-20301-P1005 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-07 | 16000 | 10000 | N | 150 | INCOMER FEEDER | B1-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-1 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | V1 | B1-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | V1 | PSP/INTEGRA TRAY → B025-013LT0129 → B025-013LT0072 → B025-013LT0071 → B025-013LT0070 → B025-013LT0090 → B164-013ET0285 → B164-013ET0284 → B164-013ET0283 → B164-013ET0077 → B164-013ET0280 → B164-013ET0066 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-20301 | -P10 | 06 |  | PE-M1-1C300-07 | PE-M1-1C300-07 |  |  |  | 1 | 1540 | B1-XFR-20301-P1006 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-07 | 16000 | 10000 | N | 150 | INCOMER FEEDER | B1-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-1 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | W1 | B1-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | W1 | PSP/INTEGRA TRAY → B025-013LT0129 → B025-013LT0072 → B025-013LT0071 → B025-013LT0070 → B025-013LT0090 → B164-013ET0285 → B164-013ET0284 → B164-013ET0283 → B164-013ET0077 → B164-013ET0280 → B164-013ET0066 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-20301 | -P10 | 07 |  | PE-M1-1C300-07 | PE-M1-1C300-07 |  |  |  | 1 | 1541 | B1-XFR-20301-P1007 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-07 | 16000 | 10000 | N | 150 | INCOMER FEEDER | B1-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-1 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | U1 | B1-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1 | PSP/INTEGRA TRAY → B025-013LT0129 → B025-013LT0072 → B025-013LT0071 → B025-013LT0070 → B025-013LT0090 → B164-013ET0285 → B164-013ET0284 → B164-013ET0283 → B164-013ET0077 → B164-013ET0280 → B164-013ET0066 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-20301 | -P10 | 08 |  | PE-M1-1C300-02 | PE-M1-1C300-02 |  |  |  | 1 | 1542 | B1-XFR-20301-P1008 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-02 | 16000 | 10000 | N | 150 | INCOMER FEEDER | B1-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-1 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | V1 | B1-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | V1 | PSP/INTEGRA TRAY → B025-013LT0129 → B025-013LT0072 → B025-013LT0071 → B025-013LT0070 → B025-013LT0090 → B164-013ET0285 → B164-013ET0284 → B164-013ET0283 → B164-013ET0077 → B164-013ET0280 → B164-013ET0066 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-20301 | -P10 | 09 |  | PE-M1-1C300-02 | PE-M1-1C300-02 |  |  |  | 1 | 1543 | B1-XFR-20301-P1009 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-02 | 16000 | 10000 | N | 150 | INCOMER FEEDER | B1-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-1 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | W1 | B1-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | W1 | PSP/INTEGRA TRAY → B025-013LT0129 → B025-013LT0072 → B025-013LT0071 → B025-013LT0070 → B025-013LT0090 → B164-013ET0285 → B164-013ET0284 → B164-013ET0283 → B164-013ET0077 → B164-013ET0280 → B164-013ET0066 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-20301 | -P10 | 10 |  | PE-M1-1C300-02 | PE-M1-1C300-02 | ELE-INT-6001-001 |  |  | 1 | 1544 | B1-XFR-20301-P1010 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-02 | 16000 | 10000 | N | 140 | INCOMER FEEDER | B1-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-2 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | U1 | B1-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1 | PSP/INTEGRA TRAY → B025-013MT0073 → B025-013MT0072 → B025-013MT0071 → B025-013MT0070 → B025-013MT0090 → B164-013DT0285 → B164-013DT0284 → B164-013DT0283 → B164-013DT0282 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-20301 | -P10 | 11 |  | PE-M1-1C300-03 | PE-M1-1C300-03 |  |  |  | 1 | 1545 | B1-XFR-20301-P1011 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-03 | 16000 | 10000 | N | 140 | INCOMER FEEDER | B1-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-2 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | V1 | B1-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | V1 | PSP/INTEGRA TRAY → B025-013MT0073 → B025-013MT0072 → B025-013MT0071 → B025-013MT0070 → B025-013MT0090 → B164-013DT0285 → B164-013DT0284 → B164-013DT0283 → B164-013DT0282 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-20301 | -P10 | 12 |  | PE-M1-1C300-03 | PE-M1-1C300-03 |  |  |  | 1 | 1546 | B1-XFR-20301-P1012 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-03 | 16000 | 10000 | N | 140 | INCOMER FEEDER | B1-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-2 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | W1 | B1-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | W1 | PSP/INTEGRA TRAY → B025-013MT0073 → B025-013MT0072 → B025-013MT0071 → B025-013MT0070 → B025-013MT0090 → B164-013DT0285 → B164-013DT0284 → B164-013DT0283 → B164-013DT0282 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-20301 | -P10 | 13 |  | PE-M1-1C300-03 | PE-M1-1C300-03 |  |  |  | 1 | 1547 | B1-XFR-20301-P1013 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-03 | 16000 | 10000 | N | 140 | INCOMER FEEDER | B1-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-2 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | U1 | B1-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1 | PSP/INTEGRA TRAY → B025-013MT0073 → B025-013MT0072 → B025-013MT0071 → B025-013MT0070 → B025-013MT0090 → B164-013DT0285 → B164-013DT0284 → B164-013DT0283 → B164-013DT0282 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-20301 | -P10 | 14 |  | PE-M1-1C300-04 | PE-M1-1C300-04 |  |  |  | 1 | 1548 | B1-XFR-20301-P1014 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-04 | 16000 | 10000 | N | 140 | INCOMER FEEDER | B1-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-2 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | V1 | B1-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | V1 | PSP/INTEGRA TRAY → B025-013MT0073 → B025-013MT0072 → B025-013MT0071 → B025-013MT0070 → B025-013MT0090 → B164-013DT0285 → B164-013DT0284 → B164-013DT0283 → B164-013DT0282 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-20301 | -P10 | 15 |  | PE-M1-1C300-04 | PE-M1-1C300-04 |  |  |  | 1 | 1549 | B1-XFR-20301-P1015 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-04 | 16000 | 10000 | N | 140 | INCOMER FEEDER | B1-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-2 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | W1 | B1-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | W1 | PSP/INTEGRA TRAY → B025-013MT0073 → B025-013MT0072 → B025-013MT0071 → B025-013MT0070 → B025-013MT0090 → B164-013DT0285 → B164-013DT0284 → B164-013DT0283 → B164-013DT0282 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-20301 | -P10 | 16 |  | PE-M1-1C300-04 | PE-M1-1C300-04 |  |  |  | 1 | 1550 | B1-XFR-20301-P1016 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-04 | 16000 | 10000 | N | 140 | INCOMER FEEDER | B1-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-2 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | U1 | B1-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1 | PSP/INTEGRA TRAY → B025-013MT0073 → B025-013MT0072 → B025-013MT0071 → B025-013MT0070 → B025-013MT0090 → B164-013DT0285 → B164-013DT0284 → B164-013DT0283 → B164-013DT0282 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-20301 | -P10 | 17 |  | PE-M1-1C300-05 | PE-M1-1C300-05 |  |  |  | 1 | 1551 | B1-XFR-20301-P1017 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-05 | 16000 | 10000 | N | 140 | INCOMER FEEDER | B1-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-2 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | V1 | B1-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | V1 | PSP/INTEGRA TRAY → B025-013MT0073 → B025-013MT0072 → B025-013MT0071 → B025-013MT0070 → B025-013MT0090 → B164-013DT0285 → B164-013DT0284 → B164-013DT0283 → B164-013DT0282 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-20301 | -P10 | 18 |  | PE-M1-1C300-05 | PE-M1-1C300-05 |  |  |  | 1 | 1552 | B1-XFR-20301-P1018 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-05 | 16000 | 10000 | N | 140 | INCOMER FEEDER | B1-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-2 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | W1 | B1-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | W1 | PSP/INTEGRA TRAY → B025-013MT0073 → B025-013MT0072 → B025-013MT0071 → B025-013MT0070 → B025-013MT0090 → B164-013DT0285 → B164-013DT0284 → B164-013DT0283 → B164-013DT0282 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-21301 | -P10 | 01 |  | PE-M1-1C300-06 | PE-M1-1C300-06 | ELE-INT-6002 |  |  | 1 | 1553 | B1-XFR-21301-P1001 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-06 | 16000 | 10000 | N | 200 | INCOMER FEEDER | B1-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-1 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | U1 | B1-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1 | PSP/INTEGRA TRAY → B025-013KT0075 → B025-013KT0096 → B025-013KT0095 → B025-013KT0094 → B025-013KT0092 → B025-013KT0091 → B164-013CT0288 → B164-013CT0287 → B164-013CT0286 → B164-013CT0084 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-21301 | -P10 | 02 |  | PE-M1-1C300-06 | PE-M1-1C300-06 |  |  |  | 1 | 1554 | B1-XFR-21301-P1002 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-06 | 16000 | 10000 | N | 200 | INCOMER FEEDER | B1-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-1 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | V1 | B1-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | V1 | PSP/INTEGRA TRAY → B025-013KT0075 → B025-013KT0096 → B025-013KT0095 → B025-013KT0094 → B025-013KT0092 → B025-013KT0091 → B164-013CT0288 → B164-013CT0287 → B164-013CT0286 → B164-013CT0084 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-21301 | -P10 | 3 |  | PE-M1-1C300-17 | PE-M1-1C300-17 |  |  |  | 1 | 1555 | B1-XFR-21301-P103 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-17 | 16000 | 10000 | N | 200 | INCOMER FEEDER | B1-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-1 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | W1 | B1-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | W1 | PSP/INTEGRA TRAY → B025-013KT0075 → B025-013KT0096 → B025-013KT0095 → B025-013KT0094 → B025-013KT0092 → B025-013KT0091 → B164-013CT0288 → B164-013CT0287 → B164-013CT0286 → B164-013CT0084 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-21301 | -P10 | 4 |  | PE-M1-1C300-17 | PE-M1-1C300-17 |  |  |  | 1 | 1556 | B1-XFR-21301-P104 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-17 | 16000 | 10000 | N | 200 | INCOMER FEEDER | B1-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-1 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | U1 | B1-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1 | PSP/INTEGRA TRAY → B025-013KT0075 → B025-013KT0096 → B025-013KT0095 → B025-013KT0094 → B025-013KT0092 → B025-013KT0091 → B164-013CT0288 → B164-013CT0287 → B164-013CT0286 → B164-013CT0084 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-21301 | -P10 | 5 |  | PE-M1-1C300-16 | PE-M1-1C300-16 |  |  |  | 1 | 1557 | B1-XFR-21301-P105 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-16 | 16000 | 10000 | N | 200 | INCOMER FEEDER | B1-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-1 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | V1 | B1-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | V1 | PSP/INTEGRA TRAY → B025-013KT0075 → B025-013KT0096 → B025-013KT0095 → B025-013KT0094 → B025-013KT0092 → B025-013KT0091 → B164-013CT0288 → B164-013CT0287 → B164-013CT0286 → B164-013CT0084 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-21301 | -P10 | 6 |  | PE-M1-1C300-16 | PE-M1-1C300-16 |  |  |  | 1 | 1558 | B1-XFR-21301-P106 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-16 | 16000 | 10000 | N | 200 | INCOMER FEEDER | B1-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-1 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | W1 | B1-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | W1 | PSP/INTEGRA TRAY → B025-013KT0075 → B025-013KT0096 → B025-013KT0095 → B025-013KT0094 → B025-013KT0092 → B025-013KT0091 → B164-013CT0288 → B164-013CT0287 → B164-013CT0286 → B164-013CT0084 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-21301 | -P10 | 7 |  | PE-M1-1C300-22 | PE-M1-1C300-22 |  |  |  | 1 | 1559 | B1-XFR-21301-P107 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-22 | 16000 | 10000 | N | 200 | INCOMER FEEDER | B1-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-1 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | U1 | B1-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1 | PSP/INTEGRA TRAY → B025-013KT0075 → B025-013KT0096 → B025-013KT0095 → B025-013KT0094 → B025-013KT0092 → B025-013KT0091 → B164-013CT0288 → B164-013CT0287 → B164-013CT0286 → B164-013CT0084 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-21301 | -P10 | 8 |  | PE-M1-1C300-22 | PE-M1-1C300-22 |  |  |  | 1 | 1560 | B1-XFR-21301-P108 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-22 | 16000 | 10000 | N | 200 | INCOMER FEEDER | B1-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-1 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | V1 | B1-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | V1 | PSP/INTEGRA TRAY → B025-013KT0075 → B025-013KT0096 → B025-013KT0095 → B025-013KT0094 → B025-013KT0092 → B025-013KT0091 → B164-013CT0288 → B164-013CT0287 → B164-013CT0286 → B164-013CT0084 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-21301 | -P10 | 9 |  | PE-M1-1C300-23 | PE-M1-1C300-23 |  |  |  | 1 | 1561 | B1-XFR-21301-P109 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-23 | 16000 | 10000 | N | 200 | INCOMER FEEDER | B1-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-1 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | W1 | B1-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | W1 | PSP/INTEGRA TRAY → B025-013KT0075 → B025-013KT0096 → B025-013KT0095 → B025-013KT0094 → B025-013KT0092 → B025-013KT0091 → B164-013CT0288 → B164-013CT0287 → B164-013CT0286 → B164-013CT0084 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-21301 | -P10 | 10 |  | PE-M1-1C300-25 | PE-M1-1C300-25 | ELE-INT-6002-001 |  |  | 1 | 1562 | B1-XFR-21301-P1010 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-25 | 16000 | 10000 | N | 185 | INCOMER FEEDER | B1-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-2 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | U1 | B1-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1 | PSP/INTEGRA TRAY → B025-013JT0130 → B025-013JT0096 → B025-013JT0095 → B025-013JT0094 → B025-013JT0092 → B025-013JT0091 → B164-013BT0288 → B164-013BT0287 → B164-013BT0286 → B164-013BT0085 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-21301 | -P10 | 11 |  | PE-M1-1C300-25 | PE-M1-1C300-25 |  |  |  | 1 | 1563 | B1-XFR-21301-P1011 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-25 | 16000 | 10000 | N | 185 | INCOMER FEEDER | B1-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-2 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | V1 | B1-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | V1 | PSP/INTEGRA TRAY → B025-013JT0130 → B025-013JT0096 → B025-013JT0095 → B025-013JT0094 → B025-013JT0092 → B025-013JT0091 → B164-013BT0288 → B164-013BT0287 → B164-013BT0286 → B164-013BT0085 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-21301 | -P10 | 12 |  | PE-M1-1C300-25 | PE-M1-1C300-25 |  |  |  | 1 | 1564 | B1-XFR-21301-P1012 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-25 | 16000 | 10000 | N | 185 | INCOMER FEEDER | B1-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-2 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | W1 | B1-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | W1 | PSP/INTEGRA TRAY → B025-013JT0130 → B025-013JT0096 → B025-013JT0095 → B025-013JT0094 → B025-013JT0092 → B025-013JT0091 → B164-013BT0288 → B164-013BT0287 → B164-013BT0286 → B164-013BT0085 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-21301 | -P10 | 13 |  | PE-M1-1C300-26 | PE-M1-1C300-26 |  |  |  | 1 | 1565 | B1-XFR-21301-P1013 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-26 | 16000 | 10000 | N | 185 | INCOMER FEEDER | B1-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-2 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | U1 | B1-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1 | PSP/INTEGRA TRAY → B025-013JT0130 → B025-013JT0096 → B025-013JT0095 → B025-013JT0094 → B025-013JT0092 → B025-013JT0091 → B164-013BT0288 → B164-013BT0287 → B164-013BT0286 → B164-013BT0085 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-21301 | -P10 | 14 |  | PE-M1-1C300-26 | PE-M1-1C300-26 |  |  |  | 1 | 1566 | B1-XFR-21301-P1014 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-26 | 16000 | 10000 | N | 185 | INCOMER FEEDER | B1-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-2 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | V1 | B1-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | V1 | PSP/INTEGRA TRAY → B025-013JT0130 → B025-013JT0096 → B025-013JT0095 → B025-013JT0094 → B025-013JT0092 → B025-013JT0091 → B164-013BT0288 → B164-013BT0287 → B164-013BT0286 → B164-013BT0085 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-21301 | -P10 | 15 |  | PE-M1-1C300-26 | PE-M1-1C300-26 |  |  |  | 1 | 1567 | B1-XFR-21301-P1015 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-26 | 16000 | 10000 | N | 185 | INCOMER FEEDER | B1-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-2 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | W1 | B1-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | W1 | PSP/INTEGRA TRAY → B025-013JT0130 → B025-013JT0096 → B025-013JT0095 → B025-013JT0094 → B025-013JT0092 → B025-013JT0091 → B164-013BT0288 → B164-013BT0287 → B164-013BT0286 → B164-013BT0085 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-21301 | -P10 | 16 |  | PE-M1-1C300-27 | PE-M1-1C300-27 |  |  |  | 1 | 1568 | B1-XFR-21301-P1016 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-27 | 16000 | 10000 | N | 185 | INCOMER FEEDER | B1-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-2 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | U1 | B1-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | U1 | PSP/INTEGRA TRAY → B025-013JT0130 → B025-013JT0096 → B025-013JT0095 → B025-013JT0094 → B025-013JT0092 → B025-013JT0091 → B164-013BT0288 → B164-013BT0287 → B164-013BT0286 → B164-013BT0085 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-21301 | -P10 | 17 |  | PE-M1-1C300-27 | PE-M1-1C300-27 |  |  |  | 1 | 1569 | B1-XFR-21301-P1017 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-27 | 16000 | 10000 | N | 185 | INCOMER FEEDER | B1-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-2 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | V1 | B1-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | V1 | PSP/INTEGRA TRAY → B025-013JT0130 → B025-013JT0096 → B025-013JT0095 → B025-013JT0094 → B025-013JT0092 → B025-013JT0091 → B164-013BT0288 → B164-013BT0287 → B164-013BT0286 → B164-013BT0085 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B1-XFR-21301 | -P10 | 18 |  | PE-M1-1C300-27 | PE-M1-1C300-27 |  |  |  | 1 | 1570 | B1-XFR-21301-P1018 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-27 | 16000 | 10000 | N | 185 | INCOMER FEEDER | B1-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-2 FOR BLOCK#1 | 6_UNIT AUXILIARY TRANSFORMER | W1 | B1-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #1 | 1.2_LEB FOR BLOCK #1 | W1 | PSP/INTEGRA TRAY → B025-013JT0130 → B025-013JT0096 → B025-013JT0095 → B025-013JT0094 → B025-013JT0092 → B025-013JT0091 → B164-013BT0288 → B164-013BT0287 → B164-013BT0286 → B164-013BT0085 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-20301 | -P10 | 01 |  | PE-M1-1C300-05 | PE-M1-1C300-05 | ELE-INT-7001 |  |  | 1 | 1571 | B2-XFR-20301-P1001 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-05 | 16000 | 10000 | N | 260 | INCOMER FEEDER | B2-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-1 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | U1 | B2-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1 | PSP/INTEGRA TRAY → B025-013NT0131 → B025-013NT0102 → B025-013NT0103 → B025-013NT0104 → B025-013NT0105 → B025-013NT0107 → B025-013NT0108 → B264-013GT0214 → B264-013GT0052 → B264-013GT0251 → B264-013GT0201 → B264-013GT0250 → B264-013GT0001 → B264-013GT0002 → B264-013GT0003 → B264-013GT0004 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-20301 | -P10 | 02 |  | PE-M1-1C300-34 | PE-M1-1C300-34 |  |  |  | 1 | 1572 | B2-XFR-20301-P1002 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-34 | 16000 | 10000 | N | 260 | INCOMER FEEDER | B2-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-1 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | V1 | B2-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | V1 | PSP/INTEGRA TRAY → B025-013NT0131 → B025-013NT0102 → B025-013NT0103 → B025-013NT0104 → B025-013NT0105 → B025-013NT0107 → B025-013NT0108 → B264-013GT0214 → B264-013GT0052 → B264-013GT0251 → B264-013GT0201 → B264-013GT0250 → B264-013GT0001 → B264-013GT0002 → B264-013GT0003 → B264-013GT0004 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-20301 | -P10 | 03 |  | PE-M1-1C300-34 | PE-M1-1C300-34 |  |  |  | 1 | 1573 | B2-XFR-20301-P1003 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-34 | 16000 | 10000 | N | 260 | INCOMER FEEDER | B2-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-1 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | W1 | B2-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | W1 | PSP/INTEGRA TRAY → B025-013NT0131 → B025-013NT0102 → B025-013NT0103 → B025-013NT0104 → B025-013NT0105 → B025-013NT0107 → B025-013NT0108 → B264-013GT0214 → B264-013GT0052 → B264-013GT0251 → B264-013GT0201 → B264-013GT0250 → B264-013GT0001 → B264-013GT0002 → B264-013GT0003 → B264-013GT0004 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-20301 | -P10 | 04 |  | PE-M1-1C300-35 | PE-M1-1C300-35 |  |  |  | 1 | 1574 | B2-XFR-20301-P1004 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-35 | 16000 | 10000 | N | 260 | INCOMER FEEDER | B2-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-1 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | U1 | B2-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1 | PSP/INTEGRA TRAY → B025-013NT0131 → B025-013NT0102 → B025-013NT0103 → B025-013NT0104 → B025-013NT0105 → B025-013NT0107 → B025-013NT0108 → B264-013GT0214 → B264-013GT0052 → B264-013GT0251 → B264-013GT0201 → B264-013GT0250 → B264-013GT0001 → B264-013GT0002 → B264-013GT0003 → B264-013GT0004 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-20301 | -P10 | 05 |  | PE-M1-1C300-35 | PE-M1-1C300-35 |  |  |  | 1 | 1575 | B2-XFR-20301-P1005 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-35 | 16000 | 10000 | N | 260 | INCOMER FEEDER | B2-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-1 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | V1 | B2-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | V1 | PSP/INTEGRA TRAY → B025-013NT0131 → B025-013NT0102 → B025-013NT0103 → B025-013NT0104 → B025-013NT0105 → B025-013NT0107 → B025-013NT0108 → B264-013GT0214 → B264-013GT0052 → B264-013GT0251 → B264-013GT0201 → B264-013GT0250 → B264-013GT0001 → B264-013GT0002 → B264-013GT0003 → B264-013GT0004 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-20301 | -P10 | 06 |  | PE-M1-1C300-36 | PE-M1-1C300-36 |  |  |  | 1 | 1576 | B2-XFR-20301-P1006 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-36 | 16000 | 10000 | N | 260 | INCOMER FEEDER | B2-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-1 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | W1 | B2-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | W1 | PSP/INTEGRA TRAY → B025-013NT0131 → B025-013NT0102 → B025-013NT0103 → B025-013NT0104 → B025-013NT0105 → B025-013NT0107 → B025-013NT0108 → B264-013GT0214 → B264-013GT0052 → B264-013GT0251 → B264-013GT0201 → B264-013GT0250 → B264-013GT0001 → B264-013GT0002 → B264-013GT0003 → B264-013GT0004 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-20301 | -P10 | 07 |  | PE-M1-1C300-36 | PE-M1-1C300-36 |  |  |  | 1 | 1577 | B2-XFR-20301-P1007 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-36 | 16000 | 10000 | N | 260 | INCOMER FEEDER | B2-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-1 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | U1 | B2-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1 | PSP/INTEGRA TRAY → B025-013NT0131 → B025-013NT0102 → B025-013NT0103 → B025-013NT0104 → B025-013NT0105 → B025-013NT0107 → B025-013NT0108 → B264-013GT0214 → B264-013GT0052 → B264-013GT0251 → B264-013GT0201 → B264-013GT0250 → B264-013GT0001 → B264-013GT0002 → B264-013GT0003 → B264-013GT0004 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-20301 | -P10 | 08 |  | PE-M1-1C300-37 | PE-M1-1C300-37 |  |  |  | 1 | 1578 | B2-XFR-20301-P1008 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-37 | 16000 | 10000 | N | 260 | INCOMER FEEDER | B2-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-1 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | V1 | B2-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | V1 | PSP/INTEGRA TRAY → B025-013NT0131 → B025-013NT0102 → B025-013NT0103 → B025-013NT0104 → B025-013NT0105 → B025-013NT0107 → B025-013NT0108 → B264-013GT0214 → B264-013GT0052 → B264-013GT0251 → B264-013GT0201 → B264-013GT0250 → B264-013GT0001 → B264-013GT0002 → B264-013GT0003 → B264-013GT0004 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-20301 | -P10 | 09 |  | PE-M1-1C300-37 | PE-M1-1C300-37 |  |  |  | 1 | 1579 | B2-XFR-20301-P1009 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-37 | 16000 | 10000 | N | 260 | INCOMER FEEDER | B2-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-1 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | W1 | B2-SWG-64301 | 10KV SWITCHGEAR #1 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | W1 | PSP/INTEGRA TRAY → B025-013NT0131 → B025-013NT0102 → B025-013NT0103 → B025-013NT0104 → B025-013NT0105 → B025-013NT0107 → B025-013NT0108 → B264-013GT0214 → B264-013GT0052 → B264-013GT0251 → B264-013GT0201 → B264-013GT0250 → B264-013GT0001 → B264-013GT0002 → B264-013GT0003 → B264-013GT0004 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-20301 | -P10 | 10 |  | PE-M1-1C300-38 | PE-M1-1C300-38 | ELE-INT-7001-001 |  |  | 1 | 1580 | B2-XFR-20301-P1010 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-38 | 16000 | 10000 | N | 260 | INCOMER FEEDER | B2-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-2 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | U1 | B2-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1 | PSP/INTEGRA TRAY → B025-013PT0081 → B025-013PT0102 → B025-013PT0103 → B025-013PT0104 → B025-013PT0105 → B025-013PT0107 → B025-013PT0108 → B264-013HT0214 → B264-013HT0052 → B264-013HT0251 → B264-013HT0201 → B264-013HT0250 → B264-013HT0001 → B264-013HT0002 → B264-013HT0003 → B264-013HT0004 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-20301 | -P10 | 11 |  | PE-M1-1C300-38 | PE-M1-1C300-38 |  |  |  | 1 | 1581 | B2-XFR-20301-P1011 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-38 | 16000 | 10000 | N | 260 | INCOMER FEEDER | B2-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-2 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | V1 | B2-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | V1 | PSP/INTEGRA TRAY → B025-013PT0081 → B025-013PT0102 → B025-013PT0103 → B025-013PT0104 → B025-013PT0105 → B025-013PT0107 → B025-013PT0108 → B264-013HT0214 → B264-013HT0052 → B264-013HT0251 → B264-013HT0201 → B264-013HT0250 → B264-013HT0001 → B264-013HT0002 → B264-013HT0003 → B264-013HT0004 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-20301 | -P10 | 12 |  | PE-M1-1C300-39 | PE-M1-1C300-39 |  |  |  | 1 | 1582 | B2-XFR-20301-P1012 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-39 | 16000 | 10000 | N | 260 | INCOMER FEEDER | B2-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-2 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | W1 | B2-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | W1 | PSP/INTEGRA TRAY → B025-013PT0081 → B025-013PT0102 → B025-013PT0103 → B025-013PT0104 → B025-013PT0105 → B025-013PT0107 → B025-013PT0108 → B264-013HT0214 → B264-013HT0052 → B264-013HT0251 → B264-013HT0201 → B264-013HT0250 → B264-013HT0001 → B264-013HT0002 → B264-013HT0003 → B264-013HT0004 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-20301 | -P10 | 13 |  | PE-M1-1C300-39 | PE-M1-1C300-39 |  |  |  | 1 | 1583 | B2-XFR-20301-P1013 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-39 | 16000 | 10000 | N | 260 | INCOMER FEEDER | B2-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-2 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | U1 | B2-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1 | PSP/INTEGRA TRAY → B025-013PT0081 → B025-013PT0102 → B025-013PT0103 → B025-013PT0104 → B025-013PT0105 → B025-013PT0107 → B025-013PT0108 → B264-013HT0214 → B264-013HT0052 → B264-013HT0251 → B264-013HT0201 → B264-013HT0250 → B264-013HT0001 → B264-013HT0002 → B264-013HT0003 → B264-013HT0004 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-20301 | -P10 | 14 |  | PE-M1-1C300-40 | PE-M1-1C300-40 |  |  |  | 1 | 1584 | B2-XFR-20301-P1014 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-40 | 16000 | 10000 | N | 260 | INCOMER FEEDER | B2-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-2 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | V1 | B2-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | V1 | PSP/INTEGRA TRAY → B025-013PT0081 → B025-013PT0102 → B025-013PT0103 → B025-013PT0104 → B025-013PT0105 → B025-013PT0107 → B025-013PT0108 → B264-013HT0214 → B264-013HT0052 → B264-013HT0251 → B264-013HT0201 → B264-013HT0250 → B264-013HT0001 → B264-013HT0002 → B264-013HT0003 → B264-013HT0004 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-20301 | -P10 | 15 |  | PE-M1-1C300-40 | PE-M1-1C300-40 |  |  |  | 1 | 1585 | B2-XFR-20301-P1015 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-40 | 16000 | 10000 | N | 260 | INCOMER FEEDER | B2-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-2 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | W1 | B2-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | W1 | PSP/INTEGRA TRAY → B025-013PT0081 → B025-013PT0102 → B025-013PT0103 → B025-013PT0104 → B025-013PT0105 → B025-013PT0107 → B025-013PT0108 → B264-013HT0214 → B264-013HT0052 → B264-013HT0251 → B264-013HT0201 → B264-013HT0250 → B264-013HT0001 → B264-013HT0002 → B264-013HT0003 → B264-013HT0004 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-20301 | -P10 | 16 |  | PE-M1-1C300-41 | PE-M1-1C300-41 |  |  |  | 1 | 1586 | B2-XFR-20301-P1016 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-41 | 16000 | 10000 | N | 260 | INCOMER FEEDER | B2-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-2 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | U1 | B2-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1 | PSP/INTEGRA TRAY → B025-013PT0081 → B025-013PT0102 → B025-013PT0103 → B025-013PT0104 → B025-013PT0105 → B025-013PT0107 → B025-013PT0108 → B264-013HT0214 → B264-013HT0052 → B264-013HT0251 → B264-013HT0201 → B264-013HT0250 → B264-013HT0001 → B264-013HT0002 → B264-013HT0003 → B264-013HT0004 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-20301 | -P10 | 17 |  | PE-M1-1C300-41 | PE-M1-1C300-41 |  |  |  | 1 | 1587 | B2-XFR-20301-P1017 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-41 | 16000 | 10000 | N | 260 | INCOMER FEEDER | B2-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-2 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | V1 | B2-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | V1 | PSP/INTEGRA TRAY → B025-013PT0081 → B025-013PT0102 → B025-013PT0103 → B025-013PT0104 → B025-013PT0105 → B025-013PT0107 → B025-013PT0108 → B264-013HT0214 → B264-013HT0052 → B264-013HT0251 → B264-013HT0201 → B264-013HT0250 → B264-013HT0001 → B264-013HT0002 → B264-013HT0003 → B264-013HT0004 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-20301 | -P10 | 18 |  | PE-M1-1C300-42 | PE-M1-1C300-42 |  |  |  | 1 | 1588 | B2-XFR-20301-P1018 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-42 | 16000 | 10000 | N | 260 | INCOMER FEEDER | B2-XFR-20301 | UNIT AUXILIARY TRANSFORMER #1-2 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | W1 | B2-SWG-64303 | 10KV SWITCHGEAR #3 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | W1 | PSP/INTEGRA TRAY → B025-013PT0081 → B025-013PT0102 → B025-013PT0103 → B025-013PT0104 → B025-013PT0105 → B025-013PT0107 → B025-013PT0108 → B264-013HT0214 → B264-013HT0052 → B264-013HT0251 → B264-013HT0201 → B264-013HT0250 → B264-013HT0001 → B264-013HT0002 → B264-013HT0003 → B264-013HT0004 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-21301 | -P10 | 01 |  | PE-M1-1C300-24 | PE-M1-1C300-24 | ELE-INT-7002 |  |  | 1 | 1589 | B2-XFR-21301-P1001 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-24 | 16000 | 10000 | N | 200 | INCOMER FEEDER | B2-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-1 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | U1 | B2-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1 | PSP/INTEGRA TRAY → B025-013QT0132 → B025-013QT0085 → B025-013QT0086 → B025-013QT0087 → B025-013QT0088 → B264-013ET0217 → B264-013ET0051 → B264-013ET0202 → B264-013ET0016 → B264-013ET0017 → B264-013ET0018 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-21301 | -P10 | 02 |  | PE-M1-1C300-19 | PE-M1-1C300-19 |  |  |  | 1 | 1590 | B2-XFR-21301-P1002 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-19 | 16000 | 10000 | N | 200 | INCOMER FEEDER | B2-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-1 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | V1 | B2-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | V1 | PSP/INTEGRA TRAY → B025-013QT0132 → B025-013QT0085 → B025-013QT0086 → B025-013QT0087 → B025-013QT0088 → B264-013ET0217 → B264-013ET0051 → B264-013ET0202 → B264-013ET0016 → B264-013ET0017 → B264-013ET0018 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-21301 | -P10 | 03 |  | PE-M1-1C300-20 | PE-M1-1C300-20 |  |  |  | 1 | 1591 | B2-XFR-21301-P1003 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-20 | 16000 | 10000 | N | 200 | INCOMER FEEDER | B2-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-1 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | W1 | B2-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | W1 | PSP/INTEGRA TRAY → B025-013QT0132 → B025-013QT0085 → B025-013QT0086 → B025-013QT0087 → B025-013QT0088 → B264-013ET0217 → B264-013ET0051 → B264-013ET0202 → B264-013ET0016 → B264-013ET0017 → B264-013ET0018 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-21301 | -P10 | 04 |  | PE-M1-1C300-21 | PE-M1-1C300-21 |  |  |  | 1 | 1592 | B2-XFR-21301-P1004 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-21 | 16000 | 10000 | N | 200 | INCOMER FEEDER | B2-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-1 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | U1 | B2-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1 | PSP/INTEGRA TRAY → B025-013QT0132 → B025-013QT0085 → B025-013QT0086 → B025-013QT0087 → B025-013QT0088 → B264-013ET0217 → B264-013ET0051 → B264-013ET0202 → B264-013ET0016 → B264-013ET0017 → B264-013ET0018 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-21301 | -P10 | 05 |  | PE-M1-1C300-31 | PE-M1-1C300-31 |  |  |  | 1 | 1593 | B2-XFR-21301-P1005 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-31 | 16000 | 10000 | N | 200 | INCOMER FEEDER | B2-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-1 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | V1 | B2-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | V1 | PSP/INTEGRA TRAY → B025-013QT0132 → B025-013QT0085 → B025-013QT0086 → B025-013QT0087 → B025-013QT0088 → B264-013ET0217 → B264-013ET0051 → B264-013ET0202 → B264-013ET0016 → B264-013ET0017 → B264-013ET0018 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-21301 | -P10 | 06 |  | PE-M1-1C300-32 | PE-M1-1C300-32 |  |  |  | 1 | 1594 | B2-XFR-21301-P1006 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-32 | 16000 | 10000 | N | 200 | INCOMER FEEDER | B2-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-1 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | W1 | B2-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | W1 | PSP/INTEGRA TRAY → B025-013QT0132 → B025-013QT0085 → B025-013QT0086 → B025-013QT0087 → B025-013QT0088 → B264-013ET0217 → B264-013ET0051 → B264-013ET0202 → B264-013ET0016 → B264-013ET0017 → B264-013ET0018 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-21301 | -P10 | 07 |  | PE-M1-1C300-33 | PE-M1-1C300-33 |  |  |  | 1 | 1595 | B2-XFR-21301-P1007 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-33 | 16000 | 10000 | N | 200 | INCOMER FEEDER | B2-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-1 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | U1 | B2-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1 | PSP/INTEGRA TRAY → B025-013QT0132 → B025-013QT0085 → B025-013QT0086 → B025-013QT0087 → B025-013QT0088 → B264-013ET0217 → B264-013ET0051 → B264-013ET0202 → B264-013ET0016 → B264-013ET0017 → B264-013ET0018 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-21301 | -P10 | 08 |  | PE-M1-1C300-28 | PE-M1-1C300-28 |  |  |  | 1 | 1596 | B2-XFR-21301-P1008 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-28 | 16000 | 10000 | N | 200 | INCOMER FEEDER | B2-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-1 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | V1 | B2-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | V1 | PSP/INTEGRA TRAY → B025-013QT0132 → B025-013QT0085 → B025-013QT0086 → B025-013QT0087 → B025-013QT0088 → B264-013ET0217 → B264-013ET0051 → B264-013ET0202 → B264-013ET0016 → B264-013ET0017 → B264-013ET0018 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-21301 | -P10 | 09 |  | PE-M1-1C300-42 | PE-M1-1C300-42 |  |  |  | 1 | 1597 | B2-XFR-21301-P1009 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-42 | 16000 | 10000 | N | 200 | INCOMER FEEDER | B2-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-1 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | W1 | B2-SWG-64302 | 10KV SWITCHGEAR #2 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | W1 | PSP/INTEGRA TRAY → B025-013QT0132 → B025-013QT0085 → B025-013QT0086 → B025-013QT0087 → B025-013QT0088 → B264-013ET0217 → B264-013ET0051 → B264-013ET0202 → B264-013ET0016 → B264-013ET0017 → B264-013ET0018 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-21301 | -P10 | 10 |  | PE-M1-1C300-08 | PE-M1-1C300-08 | ELE-INT-7002-001 |  |  | 1 | 1598 | B2-XFR-21301-P1010 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-08 | 16000 | 10000 | N | 210 | INCOMER FEEDER | B2-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-2 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | U1 | B2-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1 | PSP/INTEGRA TRAY → B025-013RT0084 → B025-013RT0085 → B025-013RT0086 → B025-013RT0087 → B025-013RT0088 → B264-013FT0217 → B264-013FT0051 → B264-013FT0202 → B264-013FT0016 → B264-013FT0017 → B264-013FT0018 → B264-013FT0019 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-21301 | -P10 | 11 |  | PE-M1-1C300-09 | PE-M1-1C300-09 |  |  |  | 1 | 1599 | B2-XFR-21301-P1011 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-09 | 16000 | 10000 | N | 210 | INCOMER FEEDER | B2-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-2 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | V1 | B2-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | V1 | PSP/INTEGRA TRAY → B025-013RT0084 → B025-013RT0085 → B025-013RT0086 → B025-013RT0087 → B025-013RT0088 → B264-013FT0217 → B264-013FT0051 → B264-013FT0202 → B264-013FT0016 → B264-013FT0017 → B264-013FT0018 → B264-013FT0019 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-21301 | -P10 | 12 |  | PE-M1-1C300-10 | PE-M1-1C300-10 |  |  |  | 1 | 1600 | B2-XFR-21301-P1012 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-10 | 16000 | 10000 | N | 210 | INCOMER FEEDER | B2-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-2 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | W1 | B2-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | W1 | PSP/INTEGRA TRAY → B025-013RT0084 → B025-013RT0085 → B025-013RT0086 → B025-013RT0087 → B025-013RT0088 → B264-013FT0217 → B264-013FT0051 → B264-013FT0202 → B264-013FT0016 → B264-013FT0017 → B264-013FT0018 → B264-013FT0019 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-21301 | -P10 | 13 |  | PE-M1-1C300-11 | PE-M1-1C300-11 |  |  |  | 1 | 1601 | B2-XFR-21301-P1013 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-11 | 16000 | 10000 | N | 210 | INCOMER FEEDER | B2-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-2 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | U1 | B2-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1 | PSP/INTEGRA TRAY → B025-013RT0084 → B025-013RT0085 → B025-013RT0086 → B025-013RT0087 → B025-013RT0088 → B264-013FT0217 → B264-013FT0051 → B264-013FT0202 → B264-013FT0016 → B264-013FT0017 → B264-013FT0018 → B264-013FT0019 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-21301 | -P10 | 14 |  | PE-M1-1C300-12 | PE-M1-1C300-12 |  |  |  | 1 | 1602 | B2-XFR-21301-P1014 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-12 | 16000 | 10000 | N | 210 | INCOMER FEEDER | B2-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-2 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | V1 | B2-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | V1 | PSP/INTEGRA TRAY → B025-013RT0084 → B025-013RT0085 → B025-013RT0086 → B025-013RT0087 → B025-013RT0088 → B264-013FT0217 → B264-013FT0051 → B264-013FT0202 → B264-013FT0016 → B264-013FT0017 → B264-013FT0018 → B264-013FT0019 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-21301 | -P10 | 15 |  | PE-M1-1C300-13 | PE-M1-1C300-13 |  |  |  | 1 | 1603 | B2-XFR-21301-P1015 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-13 | 16000 | 10000 | N | 210 | INCOMER FEEDER | B2-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-2 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | W1 | B2-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | W1 | PSP/INTEGRA TRAY → B025-013RT0084 → B025-013RT0085 → B025-013RT0086 → B025-013RT0087 → B025-013RT0088 → B264-013FT0217 → B264-013FT0051 → B264-013FT0202 → B264-013FT0016 → B264-013FT0017 → B264-013FT0018 → B264-013FT0019 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-21301 | -P10 | 16 |  | PE-M1-1C300-14 | PE-M1-1C300-14 |  |  |  | 1 | 1604 | B2-XFR-21301-P1016 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-14 | 16000 | 10000 | N | 210 | INCOMER FEEDER | B2-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-2 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | U1 | B2-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | U1 | PSP/INTEGRA TRAY → B025-013RT0084 → B025-013RT0085 → B025-013RT0086 → B025-013RT0087 → B025-013RT0088 → B264-013FT0217 → B264-013FT0051 → B264-013FT0202 → B264-013FT0016 → B264-013FT0017 → B264-013FT0018 → B264-013FT0019 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-21301 | -P10 | 17 |  | PE-M1-1C300-15 | PE-M1-1C300-15 |  |  |  | 1 | 1605 | B2-XFR-21301-P1017 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-15 | 16000 | 10000 | N | 210 | INCOMER FEEDER | B2-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-2 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | V1 | B2-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | V1 | PSP/INTEGRA TRAY → B025-013RT0084 → B025-013RT0085 → B025-013RT0086 → B025-013RT0087 → B025-013RT0088 → B264-013FT0217 → B264-013FT0051 → B264-013FT0202 → B264-013FT0016 → B264-013FT0017 → B264-013FT0018 → B264-013FT0019 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B2-XFR-21301 | -P10 | 18 |  | PE-M1-1C300-18 | PE-M1-1C300-18 |  |  |  | 1 | 1606 | B2-XFR-21301-P1018 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-18 | 16000 | 10000 | N | 210 | INCOMER FEEDER | B2-XFR-21301 | UNIT AUXILIARY TRANSFORMER #2-2 FOR BLOCK#2 | 6_UNIT AUXILIARY TRANSFORMER | W1 | B2-SWG-64304 | 10KV SWITCHGEAR #4 FOR BLOCK #2 | 1.3_LEB FOR BLOCK #2 | W1 | PSP/INTEGRA TRAY → B025-013RT0084 → B025-013RT0085 → B025-013RT0086 → B025-013RT0087 → B025-013RT0088 → B264-013FT0217 → B264-013FT0051 → B264-013FT0202 → B264-013FT0016 → B264-013FT0017 → B264-013FT0018 → B264-013FT0019 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B0-MCC-64601 | -P20 | 31 |  | PE-L1-4C150/95-01 | PE-L1-4C150/95-01 | ELE-INT-8001 |  |  | 1 | 1607 | B0-MCC-64601-P2031 | 0.6/1kV CU/XLPE/LSZH | 3C x 150sqmm + 1C X 95sqmm | PE-L1-4C150/95-01 | 110 | 400 | N | 520 | INCOMER FEEDER | B0-MCC-64601 | 400V MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B0-MCC-72601 | 400V MCC FOR WORKSHOP - A | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, L2, L3, PE | B064-016AT0012 → B064-996AT0020 → M0501 → D0503-L44 → M0502 → D0504-L44 → M0503 → D0501-L44 → M0328 → D0324-L44 → M0329 → B114-996BT0046 → B114-016BT0045 → B114-016BT0044 → B114-016BT0043 → B114-016BT0042 → B114-016BT0041 → B114-016BT0040 → B114-016BT0039 → B114-016BT0038 → B215-016BT0037 → B215-016BT0036 → B215-016BT0035 → B215-016BT0034 → B215-016BT0033 → B215-016BT0032 → B215-016BT0022 → B025-016AT0001 → B025-016AT0002 → B025-016AT0003 → B025-996AT0001 → M0102 → D0101-L11 → B071-006AT0001 → END
B0-MCC-64601 | -P20 | 01 |  | PE-L1-4C150/95-02 | PE-L1-4C150/95-02 |  |  |  | 1 | 1608 | B0-MCC-64601-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 150sqmm + 1C X 95sqmm | PE-L1-4C150/95-02 | 110 | 400 | N | 520 | INCOMER FEEDER | B0-MCC-64601 | 400V MCC FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B0-MCC-72601 | 400V MCC FOR WORKSHOP - A | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, L2, L3, PE | B064-016AT0012 → B064-996AT0020 → M0501 → D0503-L43 → M0502 → D0504-L43 → M0503 → D0501-L43 → M0328 → D0324-L43 → M0329 → B114-996BT0046 → B114-016BT0045 → B114-016BT0044 → B114-016BT0043 → B114-016BT0042 → B114-016BT0041 → B114-016BT0040 → B114-016BT0039 → B114-016BT0038 → B215-016BT0037 → B215-016BT0036 → B215-016BT0035 → B215-016BT0034 → B215-016BT0033 → B215-016BT0032 → B215-016BT0022 → B025-016AT0001 → B025-016AT0002 → B025-016AT0003 → B025-996AT0001 → M0102 → D0101-L11 → B071-006AT0001 → END
B0-MCC-64602 | -P20 | 01 |  | PE-L1-4C150/95-03 | PE-L1-4C150/95-03 | ELE-INT-8003 |  |  | 1 | 1609 | B0-MCC-64602-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 150sqmm + 1C X 95sqmm | PE-L1-4C150/95-03 | 110 | 400 | N | 530 | INCOMER FEEDER | B0-MCC-64602 | 400V MCC FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B0-MCC-72602 | 400V MCC FOR WORKSHOP - B | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, L2, L3, PE | B064-016BT0034 → B064-016BT0033 → B064-996BT0020 → M0501 → D0503-L35 → M0502 → D0504-L35 → M0503 → D0501-L35 → M0328 → D0324-L35 → M0329 → B114-997AT0021 → B114-017AT0020 → B114-017AT0019 → B114-017AT0018 → B114-017AT0017 → B114-017AT0016 → B114-017AT0015 → B114-017AT0014 → B114-017AT0013 → B215-017AT0012 → B215-017AT0011 → B215-017AT0010 → B215-017AT0009 → B215-017AT0008 → B215-017AT0007 → B215-017AT0022 → B025-017AT0001 → B025-017AT0002 → B025-017AT0003 → B025-997AT0001 → M0102 → D0101-L12 → B071-007AT0001 → END
B0-MCC-64602 | -P20 | 02 |  | PE-L1-4C150/95-04 | PE-L1-4C150/95-04 |  |  |  | 1 | 1610 | B0-MCC-64602-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 150sqmm + 1C X 95sqmm | PE-L1-4C150/95-04 | 110 | 400 | N | 530 | INCOMER FEEDER | B0-MCC-64602 | 400V MCC FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | L1, L2, L3, PE | B0-MCC-72602 | 400V MCC FOR WORKSHOP - B | 24_WORKSHOP AND STORAGE RADIATION SHELTER | L1, L2, L3, PE | B064-016BT0034 → B064-016BT0033 → B064-996BT0020 → M0501 → D0503-L46 → M0502 → D0504-L46 → M0503 → D0501-L45 → M0328 → D0324-L45 → M0329 → B114-997AT0021 → B114-017AT0020 → B114-017AT0019 → B114-017AT0018 → B114-017AT0017 → B114-017AT0016 → B114-017AT0015 → B114-017AT0014 → B114-017AT0013 → B215-017AT0012 → B215-017AT0011 → B215-017AT0010 → B215-017AT0009 → B215-017AT0008 → B215-017AT0007 → B215-017AT0022 → B025-017AT0001 → B025-017AT0002 → B025-017AT0003 → B025-997AT0001 → M0102 → D0101-L12 → B071-007AT0001 → END
B0-SWG-64301 | -P10 | 07 |  | PE-M1-1C300-23 | PE-M1-1C300-23 | BAZIS-C-001 |  |  | 1 | 1611 | B0-SWG-64301-P1007 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-23 | 10789 | 10000 | N | 330 | TRANSFORMER | B0-SWG-64301 | 10KV SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | U1 | BUS-1900-A | 10KV SWGR TO DIST. POINT 10KV WITH TP 10/0.4KV - A | 19_DISTRIBUTION POINT 10KV WITH TP 10/0.4KV | U1 | B064-013AT0040 → B064-013AT0226 → B064-993AT0019 → M0501 → D0503-M25 → M0502 → D0504-M25 → M0503 → D0501-M25 → M0328 → D0324-M25 → M0329 → B114-993AT0021 → B114-013AT0020 → B114-013AT0025 → B025-013TT0042 → B025-013TT0041 → B025-013TT0040 → B025-993TT0016 → B025-013TT0039 → B025-013TT0038 → B025-013TT0037 → B025-993TT0007 → PSP/INTEGRA TRAY | [12 empty] | 2 | EPKT-17D1XI-G58
B0-SWG-64301 | -P10 | 08 |  | PE-M1-1C300-24 | PE-M1-1C300-24 |  |  |  | 1 | 1612 | B0-SWG-64301-P1008 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-24 | 10789 | 10000 | N | 330 | TRANSFORMER | B0-SWG-64301 | 10KV SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | V1 | BUS-1900-A | 10KV SWGR TO DIST. POINT 10KV WITH TP 10/0.4KV - A | 19_DISTRIBUTION POINT 10KV WITH TP 10/0.4KV | V1 | B064-013AT0040 → B064-013AT0226 → B064-993AT0019 → M0501 → D0503-M25 → M0502 → D0504-M25 → M0503 → D0501-M25 → M0328 → D0324-M25 → M0329 → B114-993AT0021 → B114-013AT0020 → B114-013AT0025 → B025-013TT0042 → B025-013TT0041 → B025-013TT0040 → B025-993TT0016 → B025-013TT0039 → B025-013TT0038 → B025-013TT0037 → B025-993TT0007 → PSP/INTEGRA TRAY | [12 empty] | 2 | EPKT-17D1XI-G58
B0-SWG-64301 | -P10 | 09 |  | PE-M1-1C300-19 | PE-M1-1C300-19 |  |  |  | 1 | 1613 | B0-SWG-64301-P1009 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-19 | 10789 | 10000 | N | 330 | TRANSFORMER | B0-SWG-64301 | 10KV SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | W1 | BUS-1900-A | 10KV SWGR TO DIST. POINT 10KV WITH TP 10/0.4KV - A | 19_DISTRIBUTION POINT 10KV WITH TP 10/0.4KV | W1 | B064-013AT0040 → B064-013AT0226 → B064-993AT0019 → M0501 → D0503-M25 → M0502 → D0504-M25 → M0503 → D0501-M25 → M0328 → D0324-M25 → M0329 → B114-993AT0021 → B114-013AT0020 → B114-013AT0025 → B025-013TT0042 → B025-013TT0041 → B025-013TT0040 → B025-993TT0016 → B025-013TT0039 → B025-013TT0038 → B025-013TT0037 → B025-993TT0007 → PSP/INTEGRA TRAY | [12 empty] | 2 | EPKT-17D1XI-G58
B0-SWG-64301 | -P10 | 10 |  | PE-M1-1C300-20 | PE-M1-1C300-20 |  |  |  | 1 | 1614 | B0-SWG-64301-P1010 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-20 | 10789 | 10000 | N | 330 | TRANSFORMER | B0-SWG-64301 | 10KV SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | U1 | BUS-1900-A | 10KV SWGR TO DIST. POINT 10KV WITH TP 10/0.4KV - A | 19_DISTRIBUTION POINT 10KV WITH TP 10/0.4KV | U1 | B064-013AT0040 → B064-013AT0226 → B064-993AT0019 → M0501 → D0503-M26 → M0502 → D0504-M26 → M0503 → D0501-M26 → M0328 → D0324-M26 → M0329 → B114-993AT0021 → B114-013AT0020 → B114-013AT0025 → B025-013TT0042 → B025-013TT0041 → B025-013TT0040 → B025-993TT0016 → B025-013TT0039 → B025-013TT0038 → B025-013TT0037 → B025-993TT0007 → PSP/INTEGRA TRAY | [12 empty] | 2 | EPKT-17D1XI-G58
B0-SWG-64301 | -P10 | 11 |  | PE-M1-1C300-21 | PE-M1-1C300-21 |  |  |  | 1 | 1615 | B0-SWG-64301-P1011 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-21 | 10789 | 10000 | N | 330 | TRANSFORMER | B0-SWG-64301 | 10KV SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | V1 | BUS-1900-A | 10KV SWGR TO DIST. POINT 10KV WITH TP 10/0.4KV - A | 19_DISTRIBUTION POINT 10KV WITH TP 10/0.4KV | V1 | B064-013AT0040 → B064-013AT0226 → B064-993AT0019 → M0501 → D0503-M26 → M0502 → D0504-M26 → M0503 → D0501-M26 → M0328 → D0324-M26 → M0329 → B114-993AT0021 → B114-013AT0020 → B114-013AT0025 → B025-013TT0042 → B025-013TT0041 → B025-013TT0040 → B025-993TT0016 → B025-013TT0039 → B025-013TT0038 → B025-013TT0037 → B025-993TT0007 → PSP/INTEGRA TRAY | [12 empty] | 2 | EPKT-17D1XI-G58
B0-SWG-64301 | -P10 | 12 |  | PE-M1-1C300-31 | PE-M1-1C300-31 |  |  |  | 1 | 1616 | B0-SWG-64301-P1012 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-31 | 10789 | 10000 | N | 330 | TRANSFORMER | B0-SWG-64301 | 10KV SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | W1 | BUS-1900-A | 10KV SWGR TO DIST. POINT 10KV WITH TP 10/0.4KV - A | 19_DISTRIBUTION POINT 10KV WITH TP 10/0.4KV | W1 | B064-013AT0040 → B064-013AT0226 → B064-993AT0019 → M0501 → D0503-M26 → M0502 → D0504-M26 → M0503 → D0501-M26 → M0328 → D0324-M26 → M0329 → B114-993AT0021 → B114-013AT0020 → B114-013AT0025 → B025-013TT0042 → B025-013TT0041 → B025-013TT0040 → B025-993TT0016 → B025-013TT0039 → B025-013TT0038 → B025-013TT0037 → B025-993TT0007 → PSP/INTEGRA TRAY | [12 empty] | 2 | EPKT-17D1XI-G58
B0-SWG-64301 | -P10 | 13 |  | PE-M1-1C300-32 | PE-M1-1C300-32 |  |  |  | 1 | 1617 | B0-SWG-64301-P1013 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-32 | 10789 | 10000 | N | 330 | TRANSFORMER | B0-SWG-64301 | 10KV SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | U1 | BUS-1900-A | 10KV SWGR TO DIST. POINT 10KV WITH TP 10/0.4KV - A | 19_DISTRIBUTION POINT 10KV WITH TP 10/0.4KV | U1 | B064-013AT0040 → B064-013AT0226 → B064-993AT0019 → M0501 → D0503-M27 → M0502 → D0504-M27 → M0503 → D0501-M27 → M0328 → D0324-M27 → M0329 → B114-993AT0021 → B114-013AT0020 → B114-013AT0025 → B025-013TT0042 → B025-013TT0041 → B025-013TT0040 → B025-993TT0016 → B025-013TT0039 → B025-013TT0038 → B025-013TT0037 → B025-993TT0007 → PSP/INTEGRA TRAY | [12 empty] | 2 | EPKT-17D1XI-G58
B0-SWG-64301 | -P10 | 14 |  | PE-M1-1C300-33 | PE-M1-1C300-33 |  |  |  | 1 | 1618 | B0-SWG-64301-P1014 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-33 | 10789 | 10000 | N | 330 | TRANSFORMER | B0-SWG-64301 | 10KV SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | V1 | BUS-1900-A | 10KV SWGR TO DIST. POINT 10KV WITH TP 10/0.4KV - A | 19_DISTRIBUTION POINT 10KV WITH TP 10/0.4KV | V1 | B064-013AT0040 → B064-013AT0226 → B064-993AT0019 → M0501 → D0503-M27 → M0502 → D0504-M27 → M0503 → D0501-M27 → M0328 → D0324-M27 → M0329 → B114-993AT0021 → B114-013AT0020 → B114-013AT0025 → B025-013TT0042 → B025-013TT0041 → B025-013TT0040 → B025-993TT0016 → B025-013TT0039 → B025-013TT0038 → B025-013TT0037 → B025-993TT0007 → PSP/INTEGRA TRAY | [12 empty] | 2 | EPKT-17D1XI-G58
B0-SWG-64301 | -P10 | 15 |  | PE-M1-1C300-28 | PE-M1-1C300-28 |  |  |  | 1 | 1619 | B0-SWG-64301-P1015 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-28 | 10789 | 10000 | N | 330 | TRANSFORMER | B0-SWG-64301 | 10KV SWITCHGEAR FOR COMMON - A | 1.2_LEB FOR BLOCK #1 | W1 | BUS-1900-A | 10KV SWGR TO DIST. POINT 10KV WITH TP 10/0.4KV - A | 19_DISTRIBUTION POINT 10KV WITH TP 10/0.4KV | W1 | B064-013AT0040 → B064-013AT0226 → B064-993AT0019 → M0501 → D0503-M27 → M0502 → D0504-M27 → M0503 → D0501-M27 → M0328 → D0324-M27 → M0329 → B114-993AT0021 → B114-013AT0020 → B114-013AT0025 → B025-013TT0042 → B025-013TT0041 → B025-013TT0040 → B025-993TT0016 → B025-013TT0039 → B025-013TT0038 → B025-013TT0037 → B025-993TT0007 → PSP/INTEGRA TRAY | [12 empty] | 2 | EPKT-17D1XI-G58
B0-SWG-64302 | -P10 | 07 |  | PE-M1-1C300-08 | PE-M1-1C300-08 | BAZIS-C-002 |  |  | 1 | 1620 | B0-SWG-64302-P1007 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-08 | 10789 | 10000 | N | 340 | TRANSFORMER | B0-SWG-64302 | 10KV SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | U1 | BUS-1900-B | 10KV SWGR TO DIST. POINT 10KV WITH TP 10/0.4KV - B | 19_DISTRIBUTION POINT 10KV WITH TP 10/0.4KV | U1 | B064-013BT0043 → B064-013BT0043 → B064-013BT0042 → B064-013BT0233 → B064-013BT0034 → B064-013BT0033 → B064-993BT0019 → M0501 → D0503-M28 → M0502 → D0504-M28 → M0503 → D0501-M28 → M0328 → D0324-M28 → M0329 → B114-993BT0021 → B114-013BT0020 → B114-013BT0025 → B025-013ST0042 → B025-013ST0041 → B025-013ST0040 → B025-993ST0016 → B025-013ST0039 → B025-013ST0038 → B025-993ST0007 → PSP/INTEGRA TRAY | [12 empty] | 2 | EPKT-17D1XI-G58
B0-SWG-64302 | -P10 | 08 |  | PE-M1-1C300-09 | PE-M1-1C300-09 |  |  |  | 1 | 1621 | B0-SWG-64302-P1008 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-09 | 10789 | 10000 | N | 340 | TRANSFORMER | B0-SWG-64302 | 10KV SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | V1 | BUS-1900-B | 10KV SWGR TO DIST. POINT 10KV WITH TP 10/0.4KV - B | 19_DISTRIBUTION POINT 10KV WITH TP 10/0.4KV | V1 | B064-013BT0043 → B064-013BT0043 → B064-013BT0042 → B064-013BT0233 → B064-013BT0034 → B064-013BT0033 → B064-993BT0019 → M0501 → D0503-M28 → M0502 → D0504-M28 → M0503 → D0501-M28 → M0328 → D0324-M28 → M0329 → B114-993BT0021 → B114-013BT0020 → B114-013BT0025 → B025-013ST0042 → B025-013ST0041 → B025-013ST0040 → B025-993ST0016 → B025-013ST0039 → B025-013ST0038 → B025-993ST0007 → PSP/INTEGRA TRAY | [12 empty] | 2 | EPKT-17D1XI-G58
B0-SWG-64302 | -P10 | 09 |  | PE-M1-1C300-10 | PE-M1-1C300-10 |  |  |  | 1 | 1622 | B0-SWG-64302-P1009 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-10 | 10789 | 10000 | N | 340 | TRANSFORMER | B0-SWG-64302 | 10KV SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | W1 | BUS-1900-B | 10KV SWGR TO DIST. POINT 10KV WITH TP 10/0.4KV - B | 19_DISTRIBUTION POINT 10KV WITH TP 10/0.4KV | W1 | B064-013BT0043 → B064-013BT0043 → B064-013BT0042 → B064-013BT0233 → B064-013BT0034 → B064-013BT0033 → B064-993BT0019 → M0501 → D0503-M28 → M0502 → D0504-M28 → M0503 → D0501-M28 → M0328 → D0324-M28 → M0329 → B114-993BT0021 → B114-013BT0020 → B114-013BT0025 → B025-013ST0042 → B025-013ST0041 → B025-013ST0040 → B025-993ST0016 → B025-013ST0039 → B025-013ST0038 → B025-993ST0007 → PSP/INTEGRA TRAY | [12 empty] | 2 | EPKT-17D1XI-G58
B0-SWG-64302 | -P10 | 10 |  | PE-M1-1C300-11 | PE-M1-1C300-11 |  |  |  | 1 | 1623 | B0-SWG-64302-P1010 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-11 | 10789 | 10000 | N | 340 | TRANSFORMER | B0-SWG-64302 | 10KV SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | U1 | BUS-1900-B | 10KV SWGR TO DIST. POINT 10KV WITH TP 10/0.4KV - B | 19_DISTRIBUTION POINT 10KV WITH TP 10/0.4KV | U1 | B064-013BT0043 → B064-013BT0043 → B064-013BT0042 → B064-013BT0233 → B064-013BT0034 → B064-013BT0033 → B064-993BT0019 → M0501 → D0503-M31 → M0502 → D0504-M31 → M0503 → D0501-M31 → M0328 → D0324-M31 → M0329 → B114-993BT0021 → B114-013BT0020 → B114-013BT0025 → B025-013ST0042 → B025-013ST0041 → B025-013ST0040 → B025-993ST0016 → B025-013ST0039 → B025-013ST0038 → B025-993ST0007 → PSP/INTEGRA TRAY | [12 empty] | 2 | EPKT-17D1XI-G58
B0-SWG-64302 | -P10 | 11 |  | PE-M1-1C300-12 | PE-M1-1C300-12 |  |  |  | 1 | 1624 | B0-SWG-64302-P1011 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-12 | 10789 | 10000 | N | 340 | TRANSFORMER | B0-SWG-64302 | 10KV SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | V1 | BUS-1900-B | 10KV SWGR TO DIST. POINT 10KV WITH TP 10/0.4KV - B | 19_DISTRIBUTION POINT 10KV WITH TP 10/0.4KV | V1 | B064-013BT0043 → B064-013BT0043 → B064-013BT0042 → B064-013BT0233 → B064-013BT0034 → B064-013BT0033 → B064-993BT0019 → M0501 → D0503-M31 → M0502 → D0504-M31 → M0503 → D0501-M31 → M0328 → D0324-M31 → M0329 → B114-993BT0021 → B114-013BT0020 → B114-013BT0025 → B025-013ST0042 → B025-013ST0041 → B025-013ST0040 → B025-993ST0016 → B025-013ST0039 → B025-013ST0038 → B025-993ST0007 → PSP/INTEGRA TRAY | [12 empty] | 2 | EPKT-17D1XI-G58
B0-SWG-64302 | -P10 | 12 |  | PE-M1-1C300-13 | PE-M1-1C300-13 |  |  |  | 1 | 1625 | B0-SWG-64302-P1012 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-13 | 10789 | 10000 | N | 340 | TRANSFORMER | B0-SWG-64302 | 10KV SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | W1 | BUS-1900-B | 10KV SWGR TO DIST. POINT 10KV WITH TP 10/0.4KV - B | 19_DISTRIBUTION POINT 10KV WITH TP 10/0.4KV | W1 | B064-013BT0043 → B064-013BT0043 → B064-013BT0042 → B064-013BT0233 → B064-013BT0034 → B064-013BT0033 → B064-993BT0019 → M0501 → D0503-M31 → M0502 → D0504-M31 → M0503 → D0501-M31 → M0328 → D0324-M31 → M0329 → B114-993BT0021 → B114-013BT0020 → B114-013BT0025 → B025-013ST0042 → B025-013ST0041 → B025-013ST0040 → B025-993ST0016 → B025-013ST0039 → B025-013ST0038 → B025-993ST0007 → PSP/INTEGRA TRAY | [12 empty] | 2 | EPKT-17D1XI-G58
B0-SWG-64302 | -P10 | 13 |  | PE-M1-1C300-14 | PE-M1-1C300-14 |  |  |  | 1 | 1626 | B0-SWG-64302-P1013 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-14 | 10789 | 10000 | N | 340 | TRANSFORMER | B0-SWG-64302 | 10KV SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | U1 | BUS-1900-B | 10KV SWGR TO DIST. POINT 10KV WITH TP 10/0.4KV - B | 19_DISTRIBUTION POINT 10KV WITH TP 10/0.4KV | U1 | B064-013BT0043 → B064-013BT0043 → B064-013BT0042 → B064-013BT0233 → B064-013BT0034 → B064-013BT0033 → B064-993BT0019 → M0501 → D0503-M32 → M0502 → D0504-M32 → M0503 → D0501-M32 → M0328 → D0324-M32 → M0329 → B114-993BT0021 → B114-013BT0020 → B114-013BT0025 → B025-013ST0042 → B025-013ST0041 → B025-013ST0040 → B025-993ST0016 → B025-013ST0039 → B025-013ST0038 → B025-993ST0007 → PSP/INTEGRA TRAY | [12 empty] | 2 | EPKT-17D1XI-G58
B0-SWG-64302 | -P10 | 14 |  | PE-M1-1C300-15 | PE-M1-1C300-15 |  |  |  | 1 | 1627 | B0-SWG-64302-P1014 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-15 | 10789 | 10000 | N | 340 | TRANSFORMER | B0-SWG-64302 | 10KV SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | V1 | BUS-1900-B | 10KV SWGR TO DIST. POINT 10KV WITH TP 10/0.4KV - B | 19_DISTRIBUTION POINT 10KV WITH TP 10/0.4KV | V1 | B064-013BT0043 → B064-013BT0043 → B064-013BT0042 → B064-013BT0233 → B064-013BT0034 → B064-013BT0033 → B064-993BT0019 → M0501 → D0503-M32 → M0502 → D0504-M32 → M0503 → D0501-M32 → M0328 → D0324-M32 → M0329 → B114-993BT0021 → B114-013BT0020 → B114-013BT0025 → B025-013ST0042 → B025-013ST0041 → B025-013ST0040 → B025-993ST0016 → B025-013ST0039 → B025-013ST0038 → B025-993ST0007 → PSP/INTEGRA TRAY | [12 empty] | 2 | EPKT-17D1XI-G58
B0-SWG-64302 | -P10 | 15 |  | PE-M1-1C300-18 | PE-M1-1C300-18 |  |  |  | 1 | 1628 | B0-SWG-64302-P1015 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-18 | 10789 | 10000 | N | 340 | TRANSFORMER | B0-SWG-64302 | 10KV SWITCHGEAR FOR COMMON - B | 1.2_LEB FOR BLOCK #1 | W1 | BUS-1900-B | 10KV SWGR TO DIST. POINT 10KV WITH TP 10/0.4KV - B | 19_DISTRIBUTION POINT 10KV WITH TP 10/0.4KV | W1 | B064-013BT0043 → B064-013BT0043 → B064-013BT0042 → B064-013BT0233 → B064-013BT0034 → B064-013BT0033 → B064-993BT0019 → M0501 → D0503-M32 → M0502 → D0504-M32 → M0503 → D0501-M32 → M0328 → D0324-M32 → M0329 → B114-993BT0021 → B114-013BT0020 → B114-013BT0025 → B025-013ST0042 → B025-013ST0041 → B025-013ST0040 → B025-993ST0016 → B025-013ST0039 → B025-013ST0038 → B025-993ST0007 → PSP/INTEGRA TRAY | [12 empty] | 2 | EPKT-17D1XI-G58
B0-XFR-20301 | -P10 | 01 |  | PE-M1-1C300-03 | PE-M1-1C300-03 | ELE-INT-0011 |  |  | 1 | 1629 | B0-XFR-20301-P1001 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-03 | 16000 | 10000 | N | 110 | INCOMER FEEDER | B0-XFR-20301 | BACK UP TRANSFORMER #1 (X WINDING) | 34_BACK UP TRANSFORMER | U1 | B0-SWG-64303 | 10KV SWITCHGEAR FOR BACK UP - A | 1.2_LEB FOR BLOCK #1 | U1 | PSP/INTEGRA TRAY → M0524 → D0507-M11 → M0509 → B064-993DT0025 → B064-013DT0302 → B064-013DT0301 → B064-013DT0061 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B0-XFR-20301 | -P10 | 02 |  | PE-M1-1C300-04 | PE-M1-1C300-04 |  |  |  | 1 | 1630 | B0-XFR-20301-P1002 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-04 | 16000 | 10000 | N | 110 | INCOMER FEEDER | B0-XFR-20301 | BACK UP TRANSFORMER #1 (X WINDING) | 34_BACK UP TRANSFORMER | V1 | B0-SWG-64303 | 10KV SWITCHGEAR FOR BACK UP - A | 1.2_LEB FOR BLOCK #1 | V1 | PSP/INTEGRA TRAY → M0524 → D0507-M11 → M0509 → B064-993DT0025 → B064-013DT0302 → B064-013DT0301 → B064-013DT0061 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B0-XFR-20301 | -P10 | 03 |  | PE-M1-1C300-06 | PE-M1-1C300-06 |  |  |  | 1 | 1631 | B0-XFR-20301-P1003 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-06 | 16000 | 10000 | N | 110 | INCOMER FEEDER | B0-XFR-20301 | BACK UP TRANSFORMER #1 (X WINDING) | 34_BACK UP TRANSFORMER | W1 | B0-SWG-64303 | 10KV SWITCHGEAR FOR BACK UP - A | 1.2_LEB FOR BLOCK #1 | W1 | PSP/INTEGRA TRAY → M0524 → D0507-M11 → M0509 → B064-993DT0025 → B064-013DT0302 → B064-013DT0301 → B064-013DT0061 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B0-XFR-20301 | -P10 | 04 |  | PE-M1-1C300-07 | PE-M1-1C300-07 |  |  |  | 1 | 1632 | B0-XFR-20301-P1004 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-07 | 16000 | 10000 | N | 110 | INCOMER FEEDER | B0-XFR-20301 | BACK UP TRANSFORMER #1 (X WINDING) | 34_BACK UP TRANSFORMER | U1 | B0-SWG-64303 | 10KV SWITCHGEAR FOR BACK UP - A | 1.2_LEB FOR BLOCK #1 | U1 | PSP/INTEGRA TRAY → M0524 → D0507-M12 → M0509 → B064-993DT0025 → B064-013DT0302 → B064-013DT0301 → B064-013DT0061 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B0-XFR-20301 | -P10 | 05 |  | PE-M1-1C300-17 | PE-M1-1C300-17 |  |  |  | 1 | 1633 | B0-XFR-20301-P1005 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-17 | 16000 | 10000 | N | 110 | INCOMER FEEDER | B0-XFR-20301 | BACK UP TRANSFORMER #1 (X WINDING) | 34_BACK UP TRANSFORMER | V1 | B0-SWG-64303 | 10KV SWITCHGEAR FOR BACK UP - A | 1.2_LEB FOR BLOCK #1 | V1 | PSP/INTEGRA TRAY → M0524 → D0507-M12 → M0509 → B064-993DT0025 → B064-013DT0302 → B064-013DT0301 → B064-013DT0061 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B0-XFR-20301 | -P10 | 06 |  | PE-M1-1C300-16 | PE-M1-1C300-16 |  |  |  | 1 | 1634 | B0-XFR-20301-P1006 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-16 | 16000 | 10000 | N | 110 | INCOMER FEEDER | B0-XFR-20301 | BACK UP TRANSFORMER #1 (X WINDING) | 34_BACK UP TRANSFORMER | W1 | B0-SWG-64303 | 10KV SWITCHGEAR FOR BACK UP - A | 1.2_LEB FOR BLOCK #1 | W1 | PSP/INTEGRA TRAY → M0524 → D0507-M12 → M0509 → B064-993DT0025 → B064-013DT0302 → B064-013DT0301 → B064-013DT0061 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B0-XFR-20301 | -P10 | 07 |  | PE-M1-1C300-22 | PE-M1-1C300-22 |  |  |  | 1 | 1635 | B0-XFR-20301-P1007 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-22 | 16000 | 10000 | N | 110 | INCOMER FEEDER | B0-XFR-20301 | BACK UP TRANSFORMER #1 (X WINDING) | 34_BACK UP TRANSFORMER | U1 | B0-SWG-64303 | 10KV SWITCHGEAR FOR BACK UP - A | 1.2_LEB FOR BLOCK #1 | U1 | PSP/INTEGRA TRAY → M0524 → D0507-M13 → M0509 → B064-993DT0025 → B064-013DT0302 → B064-013DT0301 → B064-013DT0061 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B0-XFR-20301 | -P10 | 08 |  | PE-M1-1C300-29 | PE-M1-1C300-29 |  |  |  | 1 | 1636 | B0-XFR-20301-P1008 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-29 | 16000 | 10000 | N | 110 | INCOMER FEEDER | B0-XFR-20301 | BACK UP TRANSFORMER #1 (X WINDING) | 34_BACK UP TRANSFORMER | V1 | B0-SWG-64303 | 10KV SWITCHGEAR FOR BACK UP - A | 1.2_LEB FOR BLOCK #1 | V1 | PSP/INTEGRA TRAY → M0524 → D0507-M13 → M0509 → B064-993DT0025 → B064-013DT0302 → B064-013DT0301 → B064-013DT0061 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B0-XFR-20301 | -P10 | 09 |  | PE-M1-1C300-30 | PE-M1-1C300-30 |  |  |  | 1 | 1637 | B0-XFR-20301-P1009 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-30 | 16000 | 10000 | N | 110 | INCOMER FEEDER | B0-XFR-20301 | BACK UP TRANSFORMER #1 (X WINDING) | 34_BACK UP TRANSFORMER | W1 | B0-SWG-64303 | 10KV SWITCHGEAR FOR BACK UP - A | 1.2_LEB FOR BLOCK #1 | W1 | PSP/INTEGRA TRAY → M0524 → D0507-M13 → M0509 → B064-993DT0025 → B064-013DT0302 → B064-013DT0301 → B064-013DT0061 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B0-XFR-20301 | -P10 | 10 |  | PE-M1-1C300-02 | PE-M1-1C300-02 | ELE-INT-0012 |  |  | 1 | 1638 | B0-XFR-20301-P1010 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-02 | 16000 | 10000 | N | 100 | INCOMER FEEDER | B0-XFR-20301 | BACK UP TRANSFORMER #1 (Y WINDING) | 34_BACK UP TRANSFORMER | U1 | B0-SWG-64304 | 10KV SWITCHGEAR FOR BACK UP - B | 1.2_LEB FOR BLOCK #1 | U1 | PSP/INTEGRA TRAY → M0524 → D0507-M21 → M0509 → B064-993ET0026 → B064-013ET0304 → B064-013ET0088 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B0-XFR-20301 | -P10 | 11 |  | PE-M1-1C300-29 | PE-M1-1C300-29 |  |  |  | 1 | 1639 | B0-XFR-20301-P1011 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-29 | 16000 | 10000 | N | 100 | INCOMER FEEDER | B0-XFR-20301 | BACK UP TRANSFORMER #1 (Y WINDING) | 34_BACK UP TRANSFORMER | V1 | B0-SWG-64304 | 10KV SWITCHGEAR FOR BACK UP - B | 1.2_LEB FOR BLOCK #1 | V1 | PSP/INTEGRA TRAY → M0524 → D0507-M21 → M0509 → B064-993ET0026 → B064-013ET0304 → B064-013ET0088 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B0-XFR-20301 | -P10 | 12 |  | PE-M1-1C300-29 | PE-M1-1C300-29 |  |  |  | 1 | 1640 | B0-XFR-20301-P1012 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-29 | 16000 | 10000 | N | 100 | INCOMER FEEDER | B0-XFR-20301 | BACK UP TRANSFORMER #1 (Y WINDING) | 34_BACK UP TRANSFORMER | W1 | B0-SWG-64304 | 10KV SWITCHGEAR FOR BACK UP - B | 1.2_LEB FOR BLOCK #1 | W1 | PSP/INTEGRA TRAY → M0524 → D0507-M21 → M0509 → B064-993ET0026 → B064-013ET0304 → B064-013ET0088 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B0-XFR-20301 | -P10 | 13 |  | PE-M1-1C300-29 | PE-M1-1C300-29 |  |  |  | 1 | 1641 | B0-XFR-20301-P1013 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-29 | 16000 | 10000 | N | 100 | INCOMER FEEDER | B0-XFR-20301 | BACK UP TRANSFORMER #1 (Y WINDING) | 34_BACK UP TRANSFORMER | U1 | B0-SWG-64304 | 10KV SWITCHGEAR FOR BACK UP - B | 1.2_LEB FOR BLOCK #1 | U1 | PSP/INTEGRA TRAY → M0524 → D0507-M22 → M0509 → B064-993ET0026 → B064-013ET0304 → B064-013ET0088 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B0-XFR-20301 | -P10 | 14 |  | PE-M1-1C300-29 | PE-M1-1C300-29 |  |  |  | 1 | 1642 | B0-XFR-20301-P1014 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-29 | 16000 | 10000 | N | 100 | INCOMER FEEDER | B0-XFR-20301 | BACK UP TRANSFORMER #1 (Y WINDING) | 34_BACK UP TRANSFORMER | V1 | B0-SWG-64304 | 10KV SWITCHGEAR FOR BACK UP - B | 1.2_LEB FOR BLOCK #1 | V1 | PSP/INTEGRA TRAY → M0524 → D0507-M22 → M0509 → B064-993ET0026 → B064-013ET0304 → B064-013ET0088 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B0-XFR-20301 | -P10 | 15 |  | PE-M1-1C300-30 | PE-M1-1C300-30 |  |  |  | 1 | 1643 | B0-XFR-20301-P1015 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-30 | 16000 | 10000 | N | 100 | INCOMER FEEDER | B0-XFR-20301 | BACK UP TRANSFORMER #1 (Y WINDING) | 34_BACK UP TRANSFORMER | W1 | B0-SWG-64304 | 10KV SWITCHGEAR FOR BACK UP - B | 1.2_LEB FOR BLOCK #1 | W1 | PSP/INTEGRA TRAY → M0524 → D0507-M22 → M0509 → B064-993ET0026 → B064-013ET0304 → B064-013ET0088 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B0-XFR-20301 | -P10 | 16 |  | PE-M1-1C300-30 | PE-M1-1C300-30 |  |  |  | 1 | 1644 | B0-XFR-20301-P1016 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-30 | 16000 | 10000 | N | 100 | INCOMER FEEDER | B0-XFR-20301 | BACK UP TRANSFORMER #1 (Y WINDING) | 34_BACK UP TRANSFORMER | U1 | B0-SWG-64304 | 10KV SWITCHGEAR FOR BACK UP - B | 1.2_LEB FOR BLOCK #1 | U1 | PSP/INTEGRA TRAY → M0524 → D0507-M23 → M0509 → B064-993ET0026 → B064-013ET0304 → B064-013ET0088 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B0-XFR-20301 | -P10 | 17 |  | PE-M1-1C300-30 | PE-M1-1C300-30 |  |  |  | 1 | 1645 | B0-XFR-20301-P1017 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-30 | 16000 | 10000 | N | 100 | INCOMER FEEDER | B0-XFR-20301 | BACK UP TRANSFORMER #1 (Y WINDING) | 34_BACK UP TRANSFORMER | V1 | B0-SWG-64304 | 10KV SWITCHGEAR FOR BACK UP - B | 1.2_LEB FOR BLOCK #1 | V1 | PSP/INTEGRA TRAY → M0524 → D0507-M23 → M0509 → B064-993ET0026 → B064-013ET0304 → B064-013ET0088 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B0-XFR-20301 | -P10 | 18 |  | PE-M1-1C300-30 | PE-M1-1C300-30 |  |  |  | 1 | 1646 | B0-XFR-20301-P1018 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 300sqmm | PE-M1-1C300-30 | 16000 | 10000 | N | 100 | INCOMER FEEDER | B0-XFR-20301 | BACK UP TRANSFORMER #1 (Y WINDING) | 34_BACK UP TRANSFORMER | W1 | B0-SWG-64304 | 10KV SWITCHGEAR FOR BACK UP - B | 1.2_LEB FOR BLOCK #1 | W1 | PSP/INTEGRA TRAY → M0524 → D0507-M23 → M0509 → B064-993ET0026 → B064-013ET0304 → B064-013ET0088 → END | [12 empty] | 2 | EPKT-17D1XI-G58
B0-XFR-24101 | -P10 | 01 |  | PE-M2-1C630-01 | PE-M2-1C630-01 | AUTO TR-001 |  | DONE | 1 | 1647 | B0-XFR-24101-P1001 | 12/20kV CU/XLPE/CTS/LSZH | 1C x 630sqmm | PE-M2-1C630-01 | 32000 | 15750 | N | 490 | INCOMER FEEDER | B0-XFR-24101 | AUTO TRANSFORMER | 39_500 MVA AUTO TRANSFORMER | U1 | B0-XFR-20301 | BACK UP TRANSFORMER #1 | 34_BACK UP TRANSFORMER | U1 | M0417 → D0413-M11 → M0416 → D0412-M11 → M0415 → D0411-M11 → M0414 → D0419-M14 → M0421 → D0418-M11 → M0422 → D0415-M11 → M0420 → D0416-M11 → M0423 → D0420-M13 → M0425 → D0527-M15 → M0519 → D0516-M15 → M0518 → D0515-M15 → M0517 → D0523-M15 → M0516 → D0514-M11 → M0520 → PSP/INTEGRA TRAY | [12 empty] | 2 | EPKT-24E1XO-G59
B0-XFR-24101 | -P10 | 02 |  | PE-M2-1C630-02 | PE-M2-1C630-02 |  |  | DONE | 1 | 1648 | B0-XFR-24101-P1002 | 12/20kV CU/XLPE/CTS/LSZH | 1C x 630sqmm | PE-M2-1C630-02 | 32000 | 15750 | N | 490 | INCOMER FEEDER | B0-XFR-24101 | AUTO TRANSFORMER | 39_500 MVA AUTO TRANSFORMER | V1 | B0-XFR-20301 | BACK UP TRANSFORMER #1 | 34_BACK UP TRANSFORMER | V1 | M0417 → D0413-M11 → M0416 → D0412-M11 → M0415 → D0411-M11 → M0414 → D0419-M14 → M0421 → D0418-M11 → M0422 → D0415-M11 → M0420 → D0416-M11 → M0423 → D0420-M13 → M0425 → D0527-M15 → M0519 → D0516-M15 → M0518 → D0515-M15 → M0517 → D0523-M15 → M0516 → D0514-M11 → M0520 → PSP/INTEGRA TRAY | [12 empty] | 2 | EPKT-24E1XO-G59
B0-XFR-24101 | -P10 | 03 |  | PE-M2-1C630-03 | PE-M2-1C630-03 |  |  | DONE | 1 | 1649 | B0-XFR-24101-P1003 | 12/20kV CU/XLPE/CTS/LSZH | 1C x 630sqmm | PE-M2-1C630-03 | 32000 | 15750 | N | 490 | INCOMER FEEDER | B0-XFR-24101 | AUTO TRANSFORMER | 39_500 MVA AUTO TRANSFORMER | W1 | B0-XFR-20301 | BACK UP TRANSFORMER #1 | 34_BACK UP TRANSFORMER | W1 | M0417 → D0413-M11 → M0416 → D0412-M11 → M0415 → D0411-M11 → M0414 → D0419-M14 → M0421 → D0418-M11 → M0422 → D0415-M11 → M0420 → D0416-M11 → M0423 → D0420-M13 → M0425 → D0527-M15 → M0519 → D0516-M15 → M0518 → D0515-M15 → M0517 → D0523-M15 → M0516 → D0514-M11 → M0520 → PSP/INTEGRA TRAY | [12 empty] | 2 | EPKT-24E1XO-G59
B0-XFR-24101 | -P10 | 04 |  | PE-M2-1C630-04 | PE-M2-1C630-04 |  |  | DONE | 1 | 1650 | B0-XFR-24101-P1004 | 12/20kV CU/XLPE/CTS/LSZH | 1C x 630sqmm | PE-M2-1C630-04 | 32000 | 15750 | N | 490 | INCOMER FEEDER | B0-XFR-24101 | AUTO TRANSFORMER | 39_500 MVA AUTO TRANSFORMER | U1 | B0-XFR-20301 | BACK UP TRANSFORMER #1 | 34_BACK UP TRANSFORMER | U1 | M0417 → D0413-M12 → M0416 → D0412-M12 → M0415 → D0411-M12 → M0414 → D0419-M13 → M0421 → D0418-M12 → M0422 → D0415-M12 → M0420 → D0416-M12 → M0423 → D0420-M14 → M0425 → D0527-M14 → M0519 → D0516-M14 → M0518 → D0515-M14 → M0517 → D0523-M14 → M0516 → D0514-M12 → M0520 → PSP/INTEGRA TRAY | [12 empty] | 2 | EPKT-24E1XO-G59
B0-XFR-24101 | -P10 | 05 |  | PE-M2-1C630-05 | PE-M2-1C630-05 |  | DONE(9/28) | DONE | 1 | 1651 | B0-XFR-24101-P1005 | 12/20kV CU/XLPE/CTS/LSZH | 1C x 630sqmm | PE-M2-1C630-05 | 32000 | 15750 | N | 490 | INCOMER FEEDER | B0-XFR-24101 | AUTO TRANSFORMER | 39_500 MVA AUTO TRANSFORMER | V1 | B0-XFR-20301 | BACK UP TRANSFORMER #1 | 34_BACK UP TRANSFORMER | V1 | M0417 → D0413-M12 → M0416 → D0412-M12 → M0415 → D0411-M12 → M0414 → D0419-M13 → M0421 → D0418-M12 → M0422 → D0415-M12 → M0420 → D0416-M12 → M0423 → D0420-M14 → M0425 → D0527-M14 → M0519 → D0516-M14 → M0518 → D0515-M14 → M0517 → D0523-M14 → M0516 → D0514-M12 → M0520 → PSP/INTEGRA TRAY | [12 empty] | 2 | EPKT-24E1XO-G59
B0-XFR-24101 | -P10 | 06 |  | PE-M2-1C630-06 | PE-M2-1C630-06 |  |  |  | 1 | 1652 | B0-XFR-24101-P1006 | 12/20kV CU/XLPE/CTS/LSZH | 1C x 630sqmm | PE-M2-1C630-06 | 32000 | 15750 | N | 490 | INCOMER FEEDER | B0-XFR-24101 | AUTO TRANSFORMER | 39_500 MVA AUTO TRANSFORMER | W1 | B0-XFR-20301 | BACK UP TRANSFORMER #1 | 34_BACK UP TRANSFORMER | W1 | M0417 → D0413-M12 → M0416 → D0412-M12 → M0415 → D0411-M12 → M0414 → D0419-M13 → M0421 → D0418-M12 → M0422 → D0415-M12 → M0420 → D0416-M12 → M0423 → D0420-M14 → M0425 → D0527-M14 → M0519 → D0516-M14 → M0518 → D0515-M14 → M0517 → D0523-M14 → M0516 → D0514-M12 → M0520 → PSP/INTEGRA TRAY | [12 empty] | 2 | EPKT-24E1XO-G59
11BFA51.DA001 | -P20 | 01 | 미배정Drum 사용(10/6) | PE-L1-3C4-03 | PE-L1-3C4-03 | GT#1-1-11BAB11GW023 -E01 | DONE(10/6) | DONE | 1 | 1653 | 11BFA51.DA001-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-03 | 0.15 | 230 | N | 30 | GT PKG | 11BFA51.DA001 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, N, PE | 11BAB11GW023 -E01 | GEN NEUT GND CAB | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, N, PE | B111-016AT0011 → B111-016AT0010 → B111-016AT0009 → B111-016AT0015 → B111-016AT0016 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
11BFA03.CB001 | -P20 | 02 |  | PE-L1-3C4-18 | PE-L1-3C4-18 | GT#1-1-11MBA18AA001 -Y01 |  | DONE | 1 | 1654 | 11BFA03.CB001-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-18 | 0.073 | 230 | N | 120 | GT PKG | 11BFA03.CB001 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, N, PE | 11MBA18AA001 -Y01 | DRN-VLV 1 FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, N, PE | B111-016AT0011 → B111-996AT0023 → M0327 → D0329-L31 → M0326 → D0320-L31 → M0325 → D0319-L26 → M0324 → B161-006BC0002 → B161-006BC0023 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MYB17GF010 -X01 (701, 702, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 13
11BFA03.CB002 | -P20 | 03 |  | PE-L1-3C4-18 | PE-L1-3C4-18 | GT#1-1-11MBA18AA002 -Y01 |  | DONE | 1 | 1655 | 11BFA03.CB002-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-18 | 0.073 | 230 | N | 120 | GT PKG | 11BFA03.CB002 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, N, PE | 11MBA18AA002 -Y01 | DRN-VLV 2 FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, N, PE | B111-016AT0011 → B111-996AT0023 → M0327 → D0329-L31 → M0326 → D0320-L31 → M0325 → D0319-L26 → M0324 → B161-006BC0002 → B161-006BC0023 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MYB17GF010 -X01 (703, 704, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 13
11BFA03.CB003 | -P20 | 04 |  | PE-L1-3C4-18 | PE-L1-3C4-18 | GT#1-1-11MBA18AA003 -Y01 |  | DONE | 1 | 1656 | 11BFA03.CB003-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-18 | 0.073 | 230 | N | 120 | GT PKG | 11BFA03.CB003 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, N, PE | 11MBA18AA003 -Y01 | DRN-VLV 3 FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, N, PE | B111-016AT0011 → B111-996AT0023 → M0327 → D0329-L31 → M0326 → D0320-L31 → M0325 → D0319-L26 → M0324 → B161-006BC0002 → B161-006BC0023 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MYB17GF010 -X01 (705, 706, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 13
11BFA02.CB001 | -P20 | 05 |  | PE-L1-4C4-02 | PE-L1-4C4-02 | GT#1-1-11MBA30AP001 -M01 |  | DONE | 1 | 1657 | 11BFA02.CB001-P2005 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-02 | 4.9 | 400 | N | 120 | GT PKG | 11BFA02.CB001 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, L2, L3, PE | 11MBA30AP001 -M01 | MXG-PP | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, L2, L3, PE | B111-016AT0011 → B111-996AT0023 → M0327 → D0329-L31 → M0326 → D0320-L31 → M0325 → D0319-L26 → M0324 → B161-006BC0002 → B161-017BC0112 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
11BFA02.EA003 | -P20 | 06 |  | PE-L1-3C4-18 | PE-L1-3C4-18 | GT#1-1-11MBA32AP001 -M01 |  | DONE | 1 | 1658 | 11BFA02.EA003-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-18 | 0.5 | 230 | N | 120 | GT PKG | 11BFA02.EA003 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, N, PE | 11MBA32AP001 -M01 | CLNG-AGT-PP | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, N, PE | B111-016AT0011 → B111-996AT0023 → M0327 → D0329-L31 → M0326 → D0320-L31 → M0325 → D0319-L26 → M0324 → B161-006BC0002 → B161-017BC0113 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
11BFA53.DA002 | -P20 | 07 |  | PE-L1-3C4-18 | PE-L1-3C4-18 | GT#1-1-11MBA32GQ012 -X01 |  | DONE | 1 | 1659 | 11BFA53.DA002-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-18 | 0.5 | 230 | N | 120 | GT PKG | 11BFA53.DA002 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, N, PE | 11MBA32GQ012 -X01 | EL-SCKT JUNCT-BOX | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, N, PE | B111-016AT0011 → B111-996AT0023 → M0327 → D0329-L31 → M0326 → D0320-L31 → M0325 → D0319-L26 → M0324 → B161-006BC0002 → B161-017BC0114 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
11BFA02.EA004 | -P20 | 08 |  | PE-L1-3C4-18 | PE-L1-3C4-18 | GT#1-1-11MBA33AP001 -M01 |  | DONE | 1 | 1660 | 11BFA02.EA004-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-18 | 0.5 | 230 | N | 120 | GT PKG | 11BFA02.EA004 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, N, PE | 11MBA33AP001 -M01 | ANTIFRZ-AGT-PP | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, N, PE | B111-016AT0011 → B111-996AT0023 → M0327 → D0329-L31 → M0326 → D0320-L31 → M0325 → D0319-L26 → M0324 → B161-006BC0002 → B161-017BC0115 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
11BFA02.CB002 | -P20 | 09 |  | PE-L1-4C4-01 | PE-L1-4C4-01 | GT#1-1-11MBA51AP001 -M01 |  |  | 1 | 1661 | 11BFA02.CB002-P2009 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-01 | 2.2 | 400 | N | 50 | GT PKG | 11BFA02.CB002 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, L2, L3, PE | 11MBA51AP001 -M01 | HYDRC-PP 1 HCO | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, L2, L3, PE | B111-016BT0001 → B111-016BT0002 → B111-016BT0012 → B111-996BT0026 → B161-016BC0117 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
11BFA02.CB003 | -P20 | 10 |  | PE-L1-4C4-01 | PE-L1-4C4-01 | GT#1-1-11MBA51AP002 -M01 |  |  | 1 | 1662 | 11BFA02.CB003-P2010 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-01 | 2.2 | 400 | N | 50 | GT PKG | 11BFA02.CB003 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, L2, L3, PE | 11MBA51AP002 -M01 | HYDRC-PP 2 HCO | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, L2, L3, PE | B111-016BT0001 → B111-016BT0002 → B111-016BT0012 → B111-996BT0026 → B161-016BC0118 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
11CJT91 (11MBJ01GS091 -E01) | -P10 | 01 | Drum 재배정(9/30) | PE-M3-1C240-01 | PE-M1-1C240-07 | GT#1-1-11MBJ01GS091 -E01 |  |  | 1 | 1663 | 11CJT0001 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-07 |  | 1400 | N | 60 | GT PKG | 11CJT91 (11MBJ01GS091 -E01) | GTG #11 SFC CABINET (GTG #11 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | U1 | B1-CB-11301 | BLOCK #1 GENERATOR CIRCUIT BREAKER FOR GT#1 | 1.1_MAIN BUILDING COMPLEX / GT #11 | U1 | B161-013BC0001 → B161-003BC0007 → M0325 → D0320-M11 → M0326 → D0329-M11 → M0327 → B111-993AT0022 → B111-013AT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
11CJT91 (11MBJ01GS091 -E01) | -P10 | 02 | Drum 재배정(9/30) | PE-M3-1C240-01 | PE-M1-1C240-07 | GT#1-1 |  |  | 1 | 1664 | 11CJT0004 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-07 |  | 1400 | N | 60 | GT PKG | 11CJT91 (11MBJ01GS091 -E01) | GTG #11 SFC CABINET (GTG #11 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | V1 | B1-CB-11301 | BLOCK #1 GENERATOR CIRCUIT BREAKER FOR GT#1 | 1.1_MAIN BUILDING COMPLEX / GT #11 | V1 | B161-013BC0001 → B161-003BC0007 → M0325 → D0320-M11 → M0326 → D0329-M11 → M0327 → B111-993AT0022 → B111-013AT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
11CJT91 (11MBJ01GS091 -E01) | -P10 | 03 | Drum 재배정(9/30) | PE-M3-1C240-01 | PE-M1-1C240-07 | GT#1-1 |  |  | 1 | 1665 | 11CJT0007 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-07 |  | 1400 | N | 60 | GT PKG | 11CJT91 (11MBJ01GS091 -E01) | GTG #11 SFC CABINET (GTG #11 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | W1 | B1-CB-11301 | BLOCK #1 GENERATOR CIRCUIT BREAKER FOR GT#1 | 1.1_MAIN BUILDING COMPLEX / GT #11 | W1 | B161-013BC0001 → B161-003BC0007 → M0325 → D0320-M11 → M0326 → D0329-M11 → M0327 → B111-993AT0022 → B111-013AT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
11CJT91 (11MBJ01GS091 -E01) | -P10 | 04 | Drum 재배정(9/30) | PE-M3-1C240-01 | PE-M1-1C240-07 | GT#1-1 |  |  | 1 | 1666 | 11CJT0002 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-07 |  | 1400 | N | 60 | GT PKG | 11CJT91 (11MBJ01GS091 -E01) | GTG #11 SFC CABINET (GTG #11 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | U1 | B1-CB-11301 | BLOCK #1 GENERATOR CIRCUIT BREAKER FOR GT#1 | 1.1_MAIN BUILDING COMPLEX / GT #11 | U1 | B161-013BC0002 → B161-003BC0008 → M0325 → D0320-M12 → M0326 → D0329-M12 → M0327 → B111-993AT0022 → B111-013AT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
11CJT91 (11MBJ01GS091 -E01) | -P10 | 05 | Drum 재배정(9/30) | PE-M3-1C240-01 | PE-M1-1C240-07 | GT#1-1 |  |  | 1 | 1667 | 11CJT0005 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-07 |  | 1400 | N | 60 | GT PKG | 11CJT91 (11MBJ01GS091 -E01) | GTG #11 SFC CABINET (GTG #11 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | V1 | B1-CB-11301 | BLOCK #1 GENERATOR CIRCUIT BREAKER FOR GT#1 | 1.1_MAIN BUILDING COMPLEX / GT #11 | V1 | B161-013BC0002 → B161-003BC0008 → M0325 → D0320-M12 → M0326 → D0329-M12 → M0327 → B111-993AT0022 → B111-013AT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
11CJT91 (11MBJ01GS091 -E01) | -P10 | 06 | Drum 재배정(9/30) | PE-M3-1C240-01 | PE-M1-1C240-07 | GT#1-1 |  |  | 1 | 1668 | 11CJT0008 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-07 |  | 1400 | N | 60 | GT PKG | 11CJT91 (11MBJ01GS091 -E01) | GTG #11 SFC CABINET (GTG #11 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | W1 | B1-CB-11301 | BLOCK #1 GENERATOR CIRCUIT BREAKER FOR GT#1 | 1.1_MAIN BUILDING COMPLEX / GT #11 | W1 | B161-013BC0002 → B161-003BC0008 → M0325 → D0320-M12 → M0326 → D0329-M12 → M0327 → B111-993AT0022 → B111-013AT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
11CJT91 (11MBJ01GS091 -E01) | -P10 | 07 | Drum 재배정(9/30) | PE-M3-1C240-01 | PE-M1-1C240-07 | GT#1-1 |  |  | 1 | 1669 | 11CJT0003 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-07 |  | 1400 | N | 60 | GT PKG | 11CJT91 (11MBJ01GS091 -E01) | GTG #11 SFC CABINET (GTG #11 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | U1 | B1-CB-11301 | BLOCK #1 GENERATOR CIRCUIT BREAKER FOR GT#1 | 1.1_MAIN BUILDING COMPLEX / GT #11 | U1 | B161-013BC0003 → B161-003BC0009 → M0325 → D0320-M13 → M0326 → D0329-M13 → M0327 → B111-993AT0022 → B111-013AT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
11CJT91 (11MBJ01GS091 -E01) | -P10 | 08 | Drum 재배정(9/30) | PE-M3-1C240-01 | PE-M1-1C240-08 | GT#1-1 |  |  | 1 | 1670 | 11CJT0006 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-08 |  | 1400 | N | 60 | GT PKG | 11CJT91 (11MBJ01GS091 -E01) | GTG #11 SFC CABINET (GTG #11 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | V1 | B1-CB-11301 | BLOCK #1 GENERATOR CIRCUIT BREAKER FOR GT#1 | 1.1_MAIN BUILDING COMPLEX / GT #11 | V1 | B161-013BC0003 → B161-003BC0009 → M0325 → D0320-M13 → M0326 → D0329-M13 → M0327 → B111-993AT0022 → B111-013AT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
11CJT91 (11MBJ01GS091 -E01) | -P10 | 09 | Drum 재배정(9/30) | PE-M3-1C240-01 | PE-M1-1C240-08 | GT#1-1 |  |  | 1 | 1671 | 11CJT0009 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-08 |  | 1400 | N | 60 | GT PKG | 11CJT91 (11MBJ01GS091 -E01) | GTG #11 SFC CABINET (GTG #11 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | W1 | B1-CB-11301 | BLOCK #1 GENERATOR CIRCUIT BREAKER FOR GT#1 | 1.1_MAIN BUILDING COMPLEX / GT #11 | W1 | B161-013BC0003 → B161-003BC0009 → M0325 → D0320-M13 → M0326 → D0329-M13 → M0327 → B111-993AT0022 → B111-013AT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
11MBJ01GT002 -E01 | -P10 | 01 | Drum 재배정(9/30) SE의견에 때른 재포설필요 | PE-M3-1C240-01 | PE-M1-1C240-07 | GT#1-1-11MBJ01GT002 -E01 | 재포설 완료 | DONE | 1 | 1672 | 11MBJ0001 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-07 |  | 1400 | N | 35 | GT PKG | 11MBJ01GT002 -E01 | GTG #11 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #11 | U1 | 11CJT91 | GTG #11 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | U1 | B161-003BC0003 → M0326 → B111-993AT0021 → B111-013AT0004 → B111-013AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
11MBJ01GT002 -E01 | -P10 | 02 | Drum 재배정(9/30) SE의견에 때른 재포설필요 | PE-M3-1C240-01 | PE-M1-1C240-07 | GT#1-1 | 재포설 완료 | DONE | 1 | 1673 | 11MBJ0004 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-07 |  | 1400 | N | 35 | GT PKG | 11MBJ01GT002 -E01 | GTG #11 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #11 | V1 | 11CJT91 | GTG #11 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | V1 | B161-003BC0003 → M0326 → B111-993AT0021 → B111-013AT0004 → B111-013AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
11MBJ01GT002 -E01 | -P10 | 03 | Drum 재배정(9/30) SE의견에 때른 재포설필요 | PE-M3-1C240-01 | PE-M1-1C240-08 | GT#1-1 | 재포설 완료 | DONE | 1 | 1674 | 11MBJ0007 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-08 |  | 1400 | N | 35 | GT PKG | 11MBJ01GT002 -E01 | GTG #11 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #11 | W1 | 11CJT91 | GTG #11 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | W1 | B161-003BC0003 → M0326 → B111-993AT0021 → B111-013AT0004 → B111-013AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
11MBJ01GT002 -E01 | -P10 | 04 | Drum 재배정(9/30) SE의견에 때른 재포설필요 | PE-M3-1C240-01 | PE-M1-1C240-08 | GT#1-1 | 재포설 완료 | DONE | 1 | 1675 | 11MBJ0002 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-08 |  | 1400 | N | 35 | GT PKG | 11MBJ01GT002 -E01 | GTG #11 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #11 | U1 | 11CJT91 | GTG #11 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | U1 | B161-003BC0004 → M0326 → B111-993AT0021 → B111-013AT0004 → B111-013AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
11MBJ01GT002 -E01 | -P10 | 05 | Drum 재배정(9/30) SE의견에 때른 재포설필요 | PE-M3-1C240-01 | PE-M1-1C240-09 | GT#1-1 | 재포설 완료 | DONE | 1 | 1676 | 11MBJ0005 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-09 |  | 1400 | N | 35 | GT PKG | 11MBJ01GT002 -E01 | GTG #11 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #11 | V1 | 11CJT91 | GTG #11 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | V1 | B161-003BC0004 → M0326 → B111-993AT0021 → B111-013AT0004 → B111-013AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
11MBJ01GT002 -E01 | -P10 | 06 | Drum 재배정(9/30) SE의견에 때른 재포설필요 | PE-M3-1C240-01 | PE-M1-1C240-09 | GT#1-1 | 재포설 완료 | DONE | 1 | 1677 | 11MBJ0008 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-09 |  | 1400 | N | 35 | GT PKG | 11MBJ01GT002 -E01 | GTG #11 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #11 | W1 | 11CJT91 | GTG #11 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | W1 | B161-003BC0004 → M0326 → B111-993AT0021 → B111-013AT0004 → B111-013AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
11MBJ01GT002 -E01 | -P10 | 07 | Drum 재배정(9/30) SE의견에 때른 재포설필요 | PE-M3-1C240-02 | PE-M1-1C240-09 | GT#1-1 | 재포설 완료 | DONE | 1 | 1678 | 11MBJ0003 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-09 |  | 1400 | N | 35 | GT PKG | 11MBJ01GT002 -E01 | GTG #11 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #11 | U1 | 11CJT91 | GTG #11 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | U1 | B161-003BC0005 → M0326 → B111-993AT0021 → B111-013AT0004 → B111-013AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
11MBJ01GT002 -E01 | -P10 | 08 | Drum 재배정(9/30) SE의견에 때른 재포설필요 | PE-M3-1C240-02 | PE-M1-1C240-09 | GT#1-1 | 재포설 완료 | DONE | 1 | 1679 | 11MBJ0006 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-09 |  | 1400 | N | 35 | GT PKG | 11MBJ01GT002 -E01 | GTG #11 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #11 | V1 | 11CJT91 | GTG #11 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | V1 | B161-003BC0005 → M0326 → B111-993AT0021 → B111-013AT0004 → B111-013AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
11MBJ01GT002 -E01 | -P10 | 09 | Drum 재배정(9/30) SE의견에 때른 재포설필요 | PE-M3-1C240-02 | PE-M1-1C240-09 | GT#1-1 | 재포설 완료 | DONE | 1 | 1680 | 11MBJ0009 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-09 |  | 1400 | N | 35 | GT PKG | 11MBJ01GT002 -E01 | GTG #11 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #11 | W1 | 11CJT91 | GTG #11 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | W1 | B161-003BC0005 → M0326 → B111-993AT0021 → B111-013AT0004 → B111-013AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
11BFA52.DA001 | -P20 | 11 |  | PE-L1-3C4-18 | PE-L1-3C4-18 | GT#1-1-11MBJ01GW035 -E01 | DONE(9/28) | DONE | 1 | 1681 | 11BFA52.DA001-P2011 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-18 | 1.2 | 230 | N | 40 | GT PKG | 11BFA52.DA001 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, N, PE | 11MBJ01GW035 -E01 | MBJ 1AC AUX-VOLT SUP | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, N, PE | B111-016AT0011 → B111-996AT0023 → M0327 → D0329-L23 → M0326 → B161-007BC0010 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
11BFA53.HA002 | -P20 | 12 |  | PE-L1-5C6-01 | PE-L1-5C6-01 | GT#1-1-11MBL10GH001 -E01 |  | DONE | 1 | 1682 | 11BFA53.HA002-P2012 | 0.6/1kV CU/XLPE/LSZH | 5C x 6sqmm | PE-L1-5C6-01 | 15 | 400 | N | 195 | GT PKG | 11BFA53.HA002 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, L2, L3, N, PE | 11MBL10GH001 -E01 | CABINET AIR INTAKE | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, L2, L3, N, PE | B111-016AT0011 → B111-996AT0023 → M0327 → D0329-L25 → M0326 → D0320-L25 → M0325 → D0319-L23 → M0324 → D0327-L22 → M0321 → B161-006DC0025 → B161-026EC0006 → B161-026EC0005 → B161-026EC0002 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MBL10GH001 -X01 (001, 002, 003, 004, 005) | 1 | A2F-S-25a-N34 | 16 - 20.5 | 17
11BFA53.HA003 | -P20 | 13 |  | PE-L1-5C6-01 | PE-L1-5C6-01 | GT#1-1-11MBL20GH001 -E01 |  | DONE | 1 | 1683 | 11BFA53.HA003-P2013 | 0.6/1kV CU/XLPE/LSZH | 5C x 6sqmm | PE-L1-5C6-01 | 11 | 400 | N | 115 | GT PKG | 11BFA53.HA003 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, L2, L3, N, PE | 11MBL20GH001 -E01 | CAB AIR-INTK-FLP | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, L2, L3, N, PE | B111-016AT0011 → B111-996AT0023 → M0327 → D0329-L25 → M0326 → D0320-L25 → M0325 → D0319-L23 → M0324 → B161-006BC0004 → B161-016BC0101 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MBL20GH001 -X01 (001, 002, 003, 004, 005) | 1 | A2F-S-25a-N34 | 16 - 20.5 | 17
11BFA51.HA001 | -P20 | 14 |  | PE-L1-5C4-02 | PE-L1-5C4-02 | GT#1-1-11MBL25AT001 -E01 |  | DONE | 1 | 1684 | 11BFA51.HA001-P2014 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-02 | 5.2 | 400 | N | 110 | GT PKG | 11BFA51.HA001 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, L2, L3, N, PE | 11MBL25AT001 -E01 | STANDSTL AIR DEHUMI | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, L2, L3, N, PE | B111-016AT0011 → B111-996AT0023 → M0327 → D0329-L25 → M0326 → D0320-L25 → M0325 → D0319-L23 → M0324 → B161-006BC0005 → B161-007BC0001 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 15
11BFA03.JB001 | -P20 | 15 |  | PE-L1-5C25/16-02 | PE-L1-5C25/16-02 | GT#1-1-11MBL30GH001 -E01 |  | DONE | 1 | 1685 | 11BFA03.JB001-P2015 | 0.6/1kV CU/XLPE/LSZH | 4C x 25sqmm + 1C X 16sqmm | PE-L1-5C25/16-02 | 40 | 400 | N | 85 | GT PKG | 11BFA03.JB001 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, L2, L3, N, PE | 11MBL30GH001 -E01 | CAB PULS-AIR | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, L2, L3, N, PE | B111-016AT0011 → B111-996AT0023 → M0327 → D0329-L31 → M0326 → D0320-L31 → M0325 → D0319-L26 → M0324 → B161-006BC0007 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MBL30GH001 -X01 (001, 002, 003, 004, 005) | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5
11BFA53.HA004 | -P20 | 16 |  | PE-L1-5C6-01 | PE-L1-5C6-01 | GT#1-1-11MBL40GH001 -E01 |  | DONE | 1 | 1686 | 11BFA53.HA004-P2016 | 0.6/1kV CU/XLPE/LSZH | 5C x 6sqmm | PE-L1-5C6-01 | 18 | 400 | N | 105 | GT PKG | 11BFA53.HA004 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, L2, L3, N, PE | 11MBL40GH001 -E01 | CAB EVAP COOL | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, L2, L3, N, PE | B111-016AT0011 → B111-996AT0023 → M0327 → D0329-L25 → M0326 → D0320-L25 → M0325 → D0319-L23 → M0324 → B161-006BC0006 → B161-016BC0103 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MBL40GH001 -X01 (001, 002, 003, 004, 005) | 1 | A2F-S-25a-N34 | 16 - 20.5 | 17
11BFA03.CB004 | -P20 | 17 |  | PE-L1-3C4-18 | PE-L1-3C4-18 | GT#1-1-11MBM12GT100 -E01 |  | DONE | 1 | 1687 | 11BFA03.CB004-P2017 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-18 | 1.6 | 230 | N | 120 | GT PKG | 11BFA03.CB004 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, N, PE | 11MBM12GT100 -E01 | IGNITION TRANSFORMERS | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, N, PE | B111-016AT0011 → B111-996AT0023 → M0327 → D0329-L24 → M0326 → D0320-L24 → M0325 → D0319-L22 → M0324 → B161-006BC0005 → B161-006BC0003 → B161-017BC0103 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MYB30GF202 -X03 | 1 | A2F-S-25-N34 | 12 - 18 | 13
11BUA01.EA001 | -P20 | 18 | 재배정 | PE-L1-2C4-04 | PE-L1-2C4-06 | GT#1-1-11MBN12AA505 -Y01 |  | DONE | 1 | 1688 | 11BUA01.EA001-P2018 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-06 | 0.055 | 220 | D | 70 | GT PKG | 11BUA01.EA001 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L+, L- | 11MBN12AA505 -Y01 | RL-VLV FEED FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #11 | L+, L- | B111-016AT0011 → B111-996AT0023 → M0327 → B161-006BC0014 → B161-017BC0132 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MBY08GF001 -X04 (401, 402) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
11BUA01.EA002 | -P20 | 19 | 재배정 | PE-L1-2C4-04 | PE-L1-2C4-06 | GT#1-1-11MBN13AA501 -Y01 |  | DONE | 1 | 1689 | 11BUA01.EA002-P2019 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-06 | 0.048 | 220 | D | 60 | GT PKG | 11BUA01.EA002 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L+, L- | 11MBN13AA501 -Y01 | STOP-VLV FUEL OIL SUPPLY | 1.1_MAIN BUILDING COMPLEX / GT #11 | L+, L- | B111-016AT0011 → B111-996AT0023 → M0327 → B161-006BC0013 → B161-017BC0133 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MYB30GF010 -X03 (403, 404) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
11BUA01.EA003 | -P20 | 20 | 재배정 | PE-L1-2C4-04 | PE-L1-2C4-06 | GT#1-1-11MBN13AA502 -Y01 |  | DONE | 1 | 1690 | 11BUA01.EA003-P2020 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-06 | 0.048 | 220 | D | 60 | GT PKG | 11BUA01.EA003 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L+, L- | 11MBN13AA502 -Y01 | RL-VLV RETN DIFFU FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #11 | L+, L- | B111-016AT0011 → B111-996AT0023 → M0327 → B161-006BC0013 → B161-017BC0134 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MYB30GF010 -X03 (401, 402) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
11BUA51.JA001 | -P20 | 21 | 미배정Drum사용 5C4로 재포설필요 | PE-L1-5C4-02 | PE-L1-5C4-02 | GT#1-1-11MBN21AA001 -Y02 |  | DONE 재포설 | 1 | 1691 | 11BUA51.JA001-P2021 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-02 | 0.13 | 220 | D | 120 | GT PKG | 11BUA51.JA001 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 11MBN21AA001 -Y02 | BLL-VLV ASSY LFT FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #11 | RL, LL, L-, BR, PE | B111-016AT0011 → B111-996AT0023 → M0327 → D0329-L24 → M0326 → D0320-L24 → M0325 → D0319-L22 → M0324 → B161-006BC0005 → B161-006BC0003 → B161-017BC0104 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 15
11BUA01.EA004 | -P20 | 22 |  | PE-L1-2C4-04 | PE-L1-2C4-04 | GT#1-1-11MBN21AA002 -Y01 |  | DONE | 1 | 1692 | 11BUA01.EA004-P2022 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-04 | 0.048 | 220 | D | 120 | GT PKG | 11BUA01.EA004 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L+, L- | 11MBN21AA002 -Y01 | BYP-VLV LFT FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #11 | L+, L- | B111-016AT0011 → B111-996AT0023 → M0327 → D0329-L24 → M0326 → D0320-L24 → M0325 → D0319-L22 → M0324 → B161-006BC0005 → B161-006BC0003 → B161-017BC0105 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MYB30GF102 -X03 (429, 430) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
11BUA51.KB001 | -P20 | 23 | 미배정Drum사용 5C4로 재포설필요 | PE-L1-5C4-02 | PE-L1-5C4-02 | GT#1-1-11MBN22AA001 -Y02 |  | DONE 재포설 | 1 | 1693 | 11BUA51.KB001-P2023 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-02 | 0.13 | 220 | D | 120 | GT PKG | 11BUA51.KB001 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 11MBN22AA001 -Y02 | BLL-VLV ASSY RGHT FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #11 | RL, LL, L-, BR, PE | B111-016AT0011 → B111-996AT0023 → M0327 → D0329-L24 → M0326 → D0320-L24 → M0325 → D0319-L22 → M0324 → B161-006BC0005 → B161-006BC0003 → B161-017BC0106 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 15
11BUA01.FB001 | -P20 | 24 |  | PE-L1-2C4-05 | PE-L1-2C4-05 | GT#1-1-11MBN22AA002 -Y01 |  | DONE | 1 | 1694 | 11BUA01.FB001-P2024 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-05 | 0.048 | 220 | D | 120 | GT PKG | 11BUA01.FB001 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L+, L- | 11MBN22AA002 -Y01 | BYP-VLV RGHT FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #11 | L+, L- | B111-016AT0011 → B111-996AT0023 → M0327 → D0329-L24 → M0326 → D0320-L24 → M0325 → D0319-L22 → M0324 → B161-006BC0005 → B161-006BC0003 → B161-017BC0107 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MYB30GF202 -X03 (429, 430) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
11BUA01.FB002 | -P20 | 25 |  | PE-L1-2C4-05 | PE-L1-2C4-05 | GT#1-1-11MBN23AA501 -Y01 |  | DONE | 1 | 1695 | 11BUA01.FB002-P2025 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-05 | 0.048 | 220 | D | 120 | GT PKG | 11BUA01.FB002 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L+, L- | 11MBN23AA501 -Y01 | DRN-VLV FEED PREM FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #11 | L+, L- | B111-016AT0011 → B111-996AT0023 → M0327 → D0329-L24 → M0326 → D0320-L24 → M0325 → D0319-L22 → M0324 → B161-006BC0005 → B161-006BC0003 → B161-017BC0108 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MYB30GF010 -X03 (405, 406) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
11BUA51.MA001 | -P20 | 26 | 미배정Drum사용 5C4로 재포설필요 | PE-L1-5C4-02 | PE-L1-5C4-02 | GT#1-1-11MBN25AA001 -Y02 |  | DONE 재포설 | 1 | 1696 | 11BUA51.MA001-P2026 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-02 | 0.13 | 220 | D | 120 | GT PKG | 11BUA51.MA001 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 11MBN25AA001 -Y02 | BLL-VLV PREM LFT FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #11 | RL, LL, L-, BR, PE | B111-016AT0011 → B111-996AT0023 → M0327 → D0329-L24 → M0326 → D0320-L24 → M0325 → D0319-L22 → M0324 → B161-006BC0005 → B161-006BC0003 → B161-017BC0109 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MYB30GF102 -X03 (401, 402, 403, 404, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
11BUA01.FB003 | -P20 | 27 |  | PE-L1-2C4-05 | PE-L1-2C4-05 | GT#1-1-11MBN25AA501 -Y01 |  | DONE | 1 | 1697 | 11BUA01.FB003-P2027 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-05 | 0.053 | 220 | D | 120 | GT PKG | 11BUA01.FB003 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L+, L- | 11MBN25AA501 -Y01 | FIL-VLV PREM LFT FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #11 | L+, L- | B111-016AT0011 → B111-996AT0023 → M0327 → D0329-L24 → M0326 → D0320-L24 → M0325 → D0319-L22 → M0324 → B161-006BC0005 → B161-006BC0003 → B161-017BC0110 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MYB30GF102 -X03 (701, 702) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
11BUA51.NB001 | -P20 | 28 | 미배정Drum사용 5C4로 재포설필요 | PE-L1-5C4-02 | PE-L1-5C4-02 | GT#1-1-11MBN26AA001 -Y02 |  | DONE 재포설 | 1 | 1698 | 11BUA51.NB001-P2028 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-02 | 0.13 | 220 | D | 120 | GT PKG | 11BUA51.NB001 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 11MBN26AA001 -Y02 | BLL-VLV PREM RGHT FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #11 | RL, LL, L-, BR, PE | B111-016AT0011 → B111-996AT0023 → M0327 → D0329-L24 → M0326 → D0320-L24 → M0325 → D0319-L22 → M0324 → B161-006BC0005 → B161-006BC0003 → B161-017BC0111 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MYB30GF202 -X03 (401, 402, 403, 404, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
11BUA01.FB004 | -P20 | 29 |  | PE-L1-2C4-05 | PE-L1-2C4-05 | GT#1-1-11MBN26AA501 -Y01 | DONE(10/6) | DONE | 1 | 1699 | 11BUA01.FB004-P2029 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-05 | 0.053 | 220 | D | 70 | GT PKG | 11BUA01.FB004 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L+, L- | 11MBN26AA501 -Y01 | FIL-VLV PREM RGHT FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #11 | L+, L- | B111-016AT0011 → B111-016AT0010 → B111-016AT0009 → B111-016AT0015 → B111-016AT0016 → B161-017BC0006 → B161-017BC0116 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MYB30GF202 -X03 (701, 702) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
11BUA01.HA001 | -P20 | 30 |  | PE-L1-2C4-05 | PE-L1-2C4-05 | GT#1-1-11MBN27AA501 -Y01 | DONE(10/6) | DONE | 1 | 1700 | 11BUA01.HA001-P2030 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-05 | 0.048 | 220 | D | 70 | GT PKG | 11BUA01.HA001 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L+, L- | 11MBN27AA501 -Y01 | LKG VLV PREM FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #11 | L+, L- | B111-016AT0011 → B111-016AT0010 → B111-016AT0009 → B111-016AT0015 → B111-016AT0016 → B161-017BC0006 → B161-017BC0117 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MYB30GF010 -X03 (407, 408) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
11BFA02.CB004 | -P20 | 31 | 재배정 | PE-L1-4C4-01 | PE-L1-4C4-02 | GT#1-1-11MBN60AP001 -M01 |  | DONE | 1 | 1701 | 11BFA02.CB004-P2031 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-02 | 1.1 | 400 | N | 60 | GT PKG | 11BFA02.CB004 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, L2, L3, PE | 11MBN60AP001 -M01 | DRNG PP AUX-TNK 1 FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, L2, L3, PE | B111-016AT0011 → B111-996AT0023 → M0327 → B161-006BC0014 → B161-016BC0105 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
11BFA03.EA003 | -P20 | 32 |  | PE-L1-4C6-01 | PE-L1-4C6-01 | GT#1-1-11MBN81AP001 -M01 |  | DONE | 1 | 1702 | 11BFA03.EA003-P2032 | 0.6/1kV CU/XLPE/LSZH | 4C x 6sqmm | PE-L1-4C6-01 | 11 | 400 | N | 60 | GT PKG | 11BFA03.EA003 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, L2, L3, PE | 11MBN81AP001 -M01 | PP FLUSH-WTR FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, L2, L3, PE | B111-016AT0011 → B111-996AT0023 → M0327 → B161-006BC0014 → B161-016BC0106 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 15.5
11BUA01.HA002 | -P20 | 33 | 재배정 | PE-L1-2C4-05 | PE-L1-2C4-06 | GT#1-1-11MBN82AA001 -Y01 |  | DONE | 1 | 1703 | 11BUA01.HA002-P2033 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-06 | 0.078 | 220 | D | 70 | GT PKG | 11BUA01.HA002 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L+, L- | 11MBN82AA001 -Y01 | FLUSHING WATER VALVE 1 | 1.1_MAIN BUILDING COMPLEX / GT #11 | L+, L- | B111-016AT0011 → B111-996AT0023 → M0327 → B161-006BC0014 → B161-017BC0135 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MBY11GF001 -X01 (401, 402) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
11BUA01.HA003 | -P20 | 34 | 재배정 | PE-L1-2C4-05 | PE-L1-2C4-06 | GT#1-1-11MBN82AA002 -Y01 |  | DONE | 1 | 1704 | 11BUA01.HA003-P2034 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-06 | 0.078 | 220 | D | 70 | GT PKG | 11BUA01.HA003 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L+, L- | 11MBN82AA002 -Y01 | FLUSHING WATER VALVE 2 | 1.1_MAIN BUILDING COMPLEX / GT #11 | L+, L- | B111-016AT0011 → B111-996AT0023 → M0327 → B161-006BC0014 → B161-017BC0136 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MBY11GF001 -X01 (403, 404) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
11BUB01.EA001 | -P20 | 35 |  | PE-L1-2C4-05 | PE-L1-2C4-05 | GT#1-1-11MBP13AA501 -Y01 | DONE(10/6) | DONE | 1 | 1705 | 11BUB01.EA001-P2035 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-05 | 0.205 | 220 | D | 50 | GT PKG | 11BUB01.EA001 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L+, L- | 11MBP13AA501 -Y01 | VENT-VLV MN SUP NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #11 | L+, L- | B111-016BT0001 → B111-016BT0002 → B111-016BT0012 → B111-996BT0026 → B161-017BC0137 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MBY09GF001 -X02 (401, 402) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
11BUB01.EA002 | -P20 | 36 |  | PE-L1-2C4-05 | PE-L1-2C4-05 | GT#1-1-11MBP14AA501 -Y01 | DONE(10/6) | DONE | 1 | 1706 | 11BUB01.EA002-P2036 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-05 | 0.205 | 220 | D | 50 | GT PKG | 11BUB01.EA002 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L+, L- | 11MBP14AA501 -Y01 | SOL-VLV VENTG NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #11 | L+, L- | B111-016BT0001 → B111-016BT0002 → B111-016BT0012 → B111-996BT0026 → B161-017BC0138 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MBY09GF001 -X02 (403, 404) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
11BUB01.EA003 | -P20 | 37 |  | PE-L1-2C4-05 | PE-L1-2C4-05 | GT#1-1-11MBP15AA501 -Y01 | DONE(10/6) | DONE | 1 | 1707 | 11BUB01.EA003-P2037 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-05 | 0.205 | 220 | D | 50 | GT PKG | 11BUB01.EA003 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L+, L- | 11MBP15AA501 -Y01 | VENT-VLV CLD SUP NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #11 | L+, L- | B111-016BT0001 → B111-016BT0002 → B111-016BT0012 → B111-996BT0026 → B161-017BC0139 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MBY09GF001 -X02 (405, 406) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
11BUB51.JA001 | -P20 | 38 |  | PE-L1-3C4-01 | PE-L1-3C4-01 | GT#1-1-11MBP21AA001 -E01 |  |  | 1 | 1708 | 11BUB51.JA001-P2038 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-01 | 0.008 | 220 | D | 60 | GT PKG | 11BUB51.JA001 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | X19(D3, D4), PE | 11MBP21AA001 -E01 | SO-VLV LFT DIFFU NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #11 | L, N, PE | B111-016AT0011 → B111-016AT0010 → B111-016AT0009 → B111-016AT0015 → B111-016AT0016 → B161-017BC0006 → B161-017BC0118 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MYB30GF102 -X03 (412, 413, 414) | 1 | A2F-S-25-N34 | 12 - 18 | 13
11BUB51.JA001 | -P20 | 39 |  | PE-L1-5C4-01 | PE-L1-5C4-01 | GT#1-1-11MBP21AA001 -Y02 |  |  | 1 | 1709 | 11BUB51.JA001-P2039 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-01 | 0.13 | 220 | D | 60 | GT PKG | 11BUB51.JA001 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 11MBP21AA001 -Y02 | SO-VLV LFT DIFFU NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #11 | RL, LL, L-, BR, PE | B111-016AT0011 → B111-016AT0010 → B111-016AT0009 → B111-016AT0015 → B111-016AT0016 → B161-017BC0006 → B161-017BC0119 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MYB30GF102 -X03 (408, 409, 410, 411, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
11BUB51.KB001 | -P20 | 40 |  | PE-L1-3C4-01 | PE-L1-3C4-01 | GT#1-1-11MBP21AA002 -E01 |  |  | 1 | 1710 | 11BUB51.KB001-P2040 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-01 | 0.008 | 220 | D | 60 | GT PKG | 11BUB51.KB001 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | X19(D3, D4), PE | 11MBP21AA002 -E01 | SO-VLV LFT PREM NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #11 | L, N, PE | B111-016AT0011 → B111-016AT0010 → B111-016AT0009 → B111-016AT0015 → B111-016AT0016 → B161-017BC0006 → B161-017BC0120 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MYB30GF102 -X03 (419, 420, 421) | 1 | A2F-S-25-N34 | 12 - 18 | 13
11BUB51.KB001 | -P20 | 41 |  | PE-L1-5C4-01 | PE-L1-5C4-01 | GT#1-1-11MBP21AA002 -Y02 |  |  | 1 | 1711 | 11BUB51.KB001-P2041 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-01 | 0.13 | 220 | D | 60 | GT PKG | 11BUB51.KB001 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 11MBP21AA002 -Y02 | SO-VLV LFT PREM NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #11 | RL, LL, L-, BR, PE | B111-016AT0011 → B111-016AT0010 → B111-016AT0009 → B111-016AT0015 → B111-016AT0016 → B161-017BC0006 → B161-017BC0121 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MYB30GF102 -X03 (415, 416, 417, 418, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
11BUB51.MA001 | -P20 | 42 |  | PE-L1-3C4-01 | PE-L1-3C4-01 | GT#1-1-11MBP21AA003 -E01 |  |  | 1 | 1712 | 11BUB51.MA001-P2042 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-01 | 0.008 | 220 | D | 60 | GT PKG | 11BUB51.MA001 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | X19(D3, D4), PE | 11MBP21AA003 -E01 | SO-VLV LFT PILOT NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #11 | L, N, PE | B111-016AT0011 → B111-016AT0010 → B111-016AT0009 → B111-016AT0015 → B111-016AT0016 → B161-017BC0006 → B161-017BC0122 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MYB30GF102 -X03 (426, 427, 428) | 1 | A2F-S-25-N34 | 12 - 18 | 13
11BUB51.MA001 | -P20 | 43 |  | PE-L1-5C4-01 | PE-L1-5C4-01 | GT#1-1-11MBP21AA003 -Y02 |  |  | 1 | 1713 | 11BUB51.MA001-P2043 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-01 | 0.13 | 220 | D | 60 | GT PKG | 11BUB51.MA001 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 11MBP21AA003 -Y02 | SO-VLV LFT PILOT NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #11 | RL, LL, L-, BR, PE | B111-016AT0011 → B111-016AT0010 → B111-016AT0009 → B111-016AT0015 → B111-016AT0016 → B161-017BC0006 → B161-017BC0123 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MYB30GF102 -X03 (422, 423, 424, 425, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
11BUB51.NB001 | -P20 | 44 |  | PE-L1-3C4-01 | PE-L1-3C4-01 | GT#1-1-11MBP22AA001 -E01 |  |  | 1 | 1714 | 11BUB51.NB001-P2044 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-01 | 0.008 | 220 | D | 60 | GT PKG | 11BUB51.NB001 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | X19(D3, D4), PE | 11MBP22AA001 -E01 | SO-VLV RGHT DIFFU NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #11 | L, N, PE | B111-016AT0011 → B111-016AT0010 → B111-016AT0009 → B111-016AT0015 → B111-016AT0016 → B161-017BC0006 → B161-017BC0124 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MYB30GF202 -X03 (412, 413, 414) | 1 | A2F-S-25-N34 | 12 - 18 | 13
11BUB51.NB001 | -P20 | 45 |  | PE-L1-5C4-01 | PE-L1-5C4-01 | GT#1-1-11MBP22AA001 -Y02 |  |  | 1 | 1715 | 11BUB51.NB001-P2045 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-01 | 0.13 | 220 | D | 60 | GT PKG | 11BUB51.NB001 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 11MBP22AA001 -Y02 | SO-VLV RGHT DIFFU NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #11 | RL, LL, L-, BR, PE | B111-016AT0011 → B111-016AT0010 → B111-016AT0009 → B111-016AT0015 → B111-016AT0016 → B161-017BC0006 → B161-017BC0125 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MYB30GF202 -X03 (408, 409, 410, 411, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
11BUB51.QA001 | -P20 | 46 |  | PE-L1-3C4-01 | PE-L1-3C4-01 | GT#1-1-11MBP22AA002 -E01 |  |  | 1 | 1716 | 11BUB51.QA001-P2046 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-01 | 0.008 | 220 | D | 60 | GT PKG | 11BUB51.QA001 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | X19(D3, D4), PE | 11MBP22AA002 -E01 | SO-VLV RGHT PREM NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #11 | L, N, PE | B111-016AT0011 → B111-016AT0010 → B111-016AT0009 → B111-016AT0015 → B111-016AT0016 → B161-017BC0006 → B161-017BC0126 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MYB30GF202 -X03 (419, 420, 421) | 1 | A2F-S-25-N34 | 12 - 18 | 13
11BUB51.QA001 | -P20 | 47 |  | PE-L1-5C4-01 | PE-L1-5C4-01 | GT#1-1-11MBP22AA002 -Y02 |  |  | 1 | 1717 | 11BUB51.QA001-P2047 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-01 | 0.13 | 220 | D | 60 | GT PKG | 11BUB51.QA001 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 11MBP22AA002 -Y02 | SO-VLV RGHT PREM NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #11 | RL, LL, L-, BR, PE | B111-016AT0011 → B111-016AT0010 → B111-016AT0009 → B111-016AT0015 → B111-016AT0016 → B161-017BC0006 → B161-017BC0127 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MYB30GF202 -X03 (415, 416, 417, 418, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
11BUB51.RB001 | -P20 | 48 |  | PE-L1-3C4-01 | PE-L1-3C4-01 | GT#1-1-11MBP22AA003 -E01 |  |  | 1 | 1718 | 11BUB51.RB001-P2048 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-01 | 0.008 | 220 | D | 60 | GT PKG | 11BUB51.RB001 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | X19(D3, D4), PE | 11MBP22AA003 -E01 | SO-VLV RGHT PILOT NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #11 | L, N, PE | B111-016AT0011 → B111-016AT0010 → B111-016AT0009 → B111-016AT0015 → B111-016AT0016 → B161-017BC0006 → B161-017BC0128 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MYB30GF202 -X03 (426, 427, 428) | 1 | A2F-S-25-N34 | 12 - 18 | 13
11BUB51.RB001 | -P20 | 49 |  | PE-L1-5C4-01 | PE-L1-5C4-01 | GT#1-1-11MBP22AA003 -Y02 |  |  | 1 | 1719 | 11BUB51.RB001-P2049 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-01 | 0.13 | 220 | D | 60 | GT PKG | 11BUB51.RB001 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 11MBP22AA003 -Y02 | SO-VLV RGHT PILOT NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #11 | RL, LL, L-, BR, PE | B111-016AT0011 → B111-016AT0010 → B111-016AT0009 → B111-016AT0015 → B111-016AT0016 → B161-017BC0006 → B161-017BC0129 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MYB30GF202 -X03 (422, 423, 424, 425, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
11BFA03.EA001 | -P20 | 50 | 미배정Drum 사용(10/6) | PE-L1-3C4-03 | PE-L1-3C4-03 | GT#1-1-11MBQ11AA001 -Y01 | DONE(10/6) | DONE | 1 | 1720 | 11BFA03.EA001-P2050 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-03 | 0.16 | 230 | N | 50 | GT PKG | 11BFA03.EA001 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, N, PE | 11MBQ11AA001 -Y01 | SOL-VLV 1 IGN-GAS | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, N, PE | B111-016AT0011 → B111-016AT0010 → B111-016AT0009 → B111-016AT0015 → B111-016AT0016 → B161-017BC0006 → B161-017BC0130 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MYB30GF021 -X01 (701, 702, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 13
11BFA03.EA002 | -P20 | 51 | 미배정Drum 사용(10/6) | PE-L1-3C4-03 | PE-L1-3C4-03 | GT#1-1-11MBQ11AA002 -Y01 | DONE(10/6) | DONE | 1 | 1721 | 11BFA03.EA002-P2051 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-03 | 0.125 | 230 | N | 60 | GT PKG | 11BFA03.EA002 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, N, PE | 11MBQ11AA002 -Y01 | SOL-VLV 2 IGN-GAS | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, N, PE | B111-016AT0011 → B111-016AT0010 → B111-016AT0009 → B111-016AT0015 → B111-016AT0016 → B161-017BC0006 → B161-017BC0131 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MYB30GF021 -X01 (703, 704, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 13
11BMA52.PB001 | -P20 | 54 |  | PE-L1-4C10-01 | PE-L1-4C10-01 | GT#1-1-11MBV21AP001 -M01 | DONE(10/6) | DONE | 1 | 1722 | 11BMA52.PB001-P2054 | 0.6/1kV CU/XLPE/LSZH | 4C x 10sqmm | PE-L1-4C10-01 | 22 | 400 | E | 60 | GT PKG | 11BMA52.PB001 | GTG #11 400V AC EMERGENCY SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, L2, L3, PE | 11MBV21AP001 -M01 | LUBRICATING OIL PUMP 1 | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, L2, L3, PE | B111-016BT0025 → B111-016BT0007 → B111-016BT0008 → B111-016BT0009 → B111-016BT0010 → B111-016BT0002 → B111-016BT0012 → B111-996BT0026 → B161-016BC0107 → END |  | 1 | A2F-S-25a-N34 | 16 - 20.5 | 18
11BFA02.PB001 | -P20 | 55 |  | PE-L1-4C10-01 | PE-L1-4C10-01 | GT#1-1-11MBV21AP002 -M01 | DONE(10/6) | DONE | 1 | 1723 | 11BFA02.PB001-P2055 | 0.6/1kV CU/XLPE/LSZH | 4C x 10sqmm | PE-L1-4C10-01 | 22 | 400 | N | 60 | GT PKG | 11BFA02.PB001 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, L2, L3, PE | 11MBV21AP002 -M01 | LUBRICATING OIL PUMP 2 | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, L2, L3, PE | B111-016BT0025 → B111-016BT0007 → B111-016BT0008 → B111-016BT0009 → B111-016BT0010 → B111-016BT0002 → B111-016BT0012 → B111-996BT0026 → B161-016BC0108 → END |  | 1 | A2F-S-25a-N34 | 16 - 20.5 | 18
11BUA51.RA001 | -P20 | 56 |  | PE-L1-3C4-01 | PE-L1-3C4-01 | GT#1-1-11MBV21AP003 -E01 |  |  | 1 | 1724 | 11BUA51.RA001-P2056 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-01 | 0.1 | 220 | D | 40 | GT PKG | 11BUA51.RA001 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | X19(D03(L), D04(N)), PE | 11MBV21AP003 -E01 | EMERGENCY LUB-OIL-PP | 1.1_MAIN BUILDING COMPLEX / GT #11 | L, N, PE | B111-016BT0001 → B111-016BT0002 → B111-016BT0012 → B111-996BT0026 → B161-017BC0142 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
11BUA51.RA001 | -P20 | 57 |  | PE-L1-4C6-01 | PE-L1-4C6-01 | GT#1-1-11MBV21AP003 -M01 |  |  | 1 | 1725 | 11BUA51.RA001-P2057 | 0.6/1kV CU/XLPE/LSZH | 4C x 6sqmm | PE-L1-4C6-01 | 3.7 | 220 | D | 40 | GT PKG | 11BUA51.RA001 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | X2(1, 2, 3), PE | 11MBV21AP003 -M01 | EMERGENCY LUB-OIL-PP | 1.1_MAIN BUILDING COMPLEX / GT #11 | F1, A2, D2, PE | B111-016BT0001 → B111-016BT0002 → B111-016BT0012 → B111-996BT0026 → B161-017BC0143 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 15.5
11BUA51.RA001 | -P20 | 58 |  | PE-L1-3C95/50-01 | PE-L1-3C95/50-01 | GT#1-1-11MBV21AP003 -R01 |  |  | 1 | 1726 | 11BUA51.RA001-P2058 | 0.6/1kV CU/XLPE/LSZH | 2C x 95sqmm + 1C x 50sqmm | PE-L1-3C95/50-01 | 3.7 | 220 | D | 40 | GT PKG | 11BUA51.RA001 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | X2(1, 2), PE | 11MBV21AP003 -R01 | EMERGENCY LUB-OIL-PP | 1.1_MAIN BUILDING COMPLEX / GT #11 | 1, 2, PE | B111-016BT0001 → B111-016BT0002 → B111-016BT0012 → B111-996BT0026 → B161-017BC0144 → END |  | 1 | A2F-S-50-N1-12 | 32.1 - 40 | 34.5
11BMA51.SA001 | -P20 | 59 |  | PE-L1-4C35/25-01 | PE-L1-4C35/25-01 | GT#1-1-11MBV30AP001 -M01 |  |  | 1 | 1727 | 11BMA51.SA001-P2059 | 0.6/1kV CU/XLPE/LSZH | 3C x 35sqmm + 1C X 25sqmm | PE-L1-4C35/25-01 | 50.6 | 400 | E | 60 | GT PKG | 11BMA51.SA001 | GTG #11 400V AC EMERGENCY SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, L2, L3, PE | 11MBV30AP001 -M01 | LIFTING OIL PUMP 1 | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, L2, L3, PE | B111-016BT0025 → B111-016BT0007 → B111-016BT0008 → B111-016BT0009 → B111-016BT0010 → B111-016BT0002 → B111-016BT0012 → B111-996BT0026 → B161-016BC0111 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5
11BFA02.SA001 | -P20 | 60 |  | PE-L1-4C35/25-01 | PE-L1-4C35/25-01 | GT#1-1-11MBV30AP002 -M01 |  |  | 1 | 1728 | 11BFA02.SA001-P2060 | 0.6/1kV CU/XLPE/LSZH | 3C x 35sqmm + 1C X 25sqmm | PE-L1-4C35/25-01 | 50.6 | 400 | N | 40 | GT PKG | 11BFA02.SA001 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, L2, L3, PE | 11MBV30AP002 -M01 | LIFTING OIL PUMP 2 | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, L2, L3, PE | B111-016BT0001 → B111-016BT0002 → B111-016BT0012 → B111-996BT0026 → B161-016BC0112 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5
11BMA52.CB001 | -P20 | 61 |  | PE-L1-4C4-01 | PE-L1-4C4-01 | GT#1-1-11MBV50AN001 -M01 |  |  | 1 | 1729 | 11BMA52.CB001-P2061 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-01 | 2.2 | 400 | E | 60 | GT PKG | 11BMA52.CB001 | GTG #11 400V AC EMERGENCY SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, L2, L3, PE | 11MBV50AN001 -M01 | OIL-VAP-EXTR1 LUB-OIL-TNK | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, L2, L3, PE | B111-016BT0025 → B111-016BT0007 → B111-016BT0008 → B111-016BT0009 → B111-016BT0010 → B111-016BT0002 → B111-016BT0012 → B111-996BT0026 → B161-016BC0123 |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
11BFA02.EA001 | -P20 | 62 |  | PE-L1-4C4-01 | PE-L1-4C4-01 | GT#1-1-11MBV50AN002 -M01 |  |  | 1 | 1730 | 11BFA02.EA001-P2062 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-01 | 2.2 | 400 | N | 50 | GT PKG | 11BFA02.EA001 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, L2, L3, PE | 11MBV50AN002 -M01 | OIL-VAP-EXTR2 LUB-OIL-TNK | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, L2, L3, PE | B111-016BT0001 → B111-016BT0002 → B111-016BT0012 → B111-996BT0026 → B161-016BC0121 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
11BFA02.FB001 | -P20 | 63 |  | PE-L1-4C4-01 | PE-L1-4C4-01 | GT#1-1-11MBX01AH001 -E01 |  |  | 1 | 1731 | 11BFA02.FB001-P2063 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-01 | 1 | 400 | N | 50 | GT PKG | 11BFA02.FB001 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, L2, L3, PE | 11MBX01AH001 -E01 | TNK HTG 1 HYDRC OIL | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, L2, L3, PE | B111-016BT0001 → B111-016BT0002 → B111-016BT0012 → B111-996BT0026 → B161-016BC0124 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
11BFA02.FB002 | -P20 | 64 |  | PE-L1-4C4-01 | PE-L1-4C4-01 | GT#1-1-11MBX01AH002 -E01 |  |  | 1 | 1732 | 11BFA02.FB002-P2064 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-01 | 1 | 400 | N | 50 | GT PKG | 11BFA02.FB002 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, L2, L3, PE | 11MBX01AH002 -E01 | TNK HTG 2 HYDRC OIL | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, L2, L3, PE | B111-016BT0001 → B111-016BT0002 → B111-016BT0012 → B111-996BT0026 → B161-016BC0122 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
11BFA02.HA002 | -P20 | 65 |  | PE-L1-4C4-01 | PE-L1-4C4-01 | GT#1-1-11MBX02AP001 -M01 |  |  | 1 | 1733 | 11BFA02.HA002-P2065 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-01 | 7.5 | 400 | N | 60 | GT PKG | 11BFA02.HA002 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, L2, L3, PE | 11MBX02AP001 -M01 | MN PP 1 HYDRC OIL | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, L2, L3, PE | B111-016BT0025 → B111-016BT0007 → B111-016BT0008 → B111-016BT0009 → B111-016BT0010 → B111-016BT0002 → B111-016BT0012 → B111-996BT0026 → B161-016BC0114 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
11BFA02.HA003 | -P20 | 66 |  | PE-L1-4C4-01 | PE-L1-4C4-01 | GT#1-1-11MBX02AP002 -M01 |  |  | 1 | 1734 | 11BFA02.HA003-P2066 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-01 | 7.5 | 400 | N | 50 | GT PKG | 11BFA02.HA003 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, L2, L3, PE | 11MBX02AP002 -M01 | MN PP 2 HYDRC OIL | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, L2, L3, PE | B111-016BT0001 → B111-016BT0002 → B111-016BT0012 → B111-996BT0026 → B161-016BC0115 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
11BFA02.HA001 | -P20 | 67 |  | PE-L1-4C4-01 | PE-L1-4C4-01 | GT#1-1-11MBX06AH001 -M01 |  |  | 1 | 1735 | 11BFA02.HA001-P2067 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-01 | 0.18 | 400 | N | 60 | GT PKG | 11BFA02.HA001 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, L2, L3, PE | 11MBX06AH001 -M01 | FAN COOL-CCT HYDRC OIL | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, L2, L3, PE | B111-016BT0025 → B111-016BT0007 → B111-016BT0008 → B111-016BT0009 → B111-016BT0010 → B111-016BT0002 → B111-016BT0012 → B111-996BT0026 → B161-016BC0116 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
11BFA02.JB001 | -P20 | 68 |  | PE-L1-4C16-01 | PE-L1-4C16-01 | GT#1-1-11MBY10GF002 -E01 | DONE(10/6) | DONE | 1 | 1736 | 11BFA02.JB001-P2068 | 0.6/1kV CU/XLPE/LSZH | 4C X 16sqmm | PE-L1-4C16-01 | 28 | 400 | N | 40 | GT PKG | 11BFA02.JB001 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, L2, L3, PE | 11MBY10GF002 -E01 | JUNCT BOX HTG LUB-OIL TNK | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, L2, L3, PE | B111-016BT0001 → B111-016BT0002 → B111-016BT0012 → B111-996BT0026 → B161-016BC0113 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MBY10GF002 -X01 (701, 702, 703, PE) | 1 | A2F-S-25a-N34 | 16 - 20.5 | 19.5
11BFA52.HA001 | -P20 | 69 |  | PE-L1-5C4-01 | PE-L1-5C4-01 | GT#1-1-11MBY40GH001 -E01 |  |  | 1 | 1737 | 11BFA52.HA001-P2069 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-01 | 9 | 400 | N | 70 | GT PKG | 11BFA52.HA001 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, L2, L3, N, PE | 11MBY40GH001 -E01 | JB INSTR AIR SYST | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, L2, L3, N, PE | B111-016AT0011 → B111-996AT0023 → M0327 → B161-006BC0012 → B161-016BC0104 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MBY40GH001 -X01 (701, 702, 703, 704, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
11BFA51.HA002 | -P20 | 70 |  | PE-L1-5C4-01 | PE-L1-5C4-01 | GT#1-1-11MBY80GH001 -E01 | DONE(10/6) | DONE | 1 | 1738 | 11BFA51.HA002-P2070 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-01 | 7 | 400 | N | 60 | GT PKG | 11BFA51.HA002 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, L2, L3, N, PE | 11MBY80GH001 -E01 | TRACE HEATING CABINET | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, L2, L3, N, PE | B111-016AT0011 → B111-016AT0010 → B111-016AT0009 → B111-016AT0015 → B111-016AT0016 → B161-016BC0019 → B161-016BC0102 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MBY80GH001 -X02 (L1, L2, L3, N, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
11BFA02.EA002 | -P20 | 71 |  | PE-L1-4C4-01 | PE-L1-4C4-01 | GT#1-1-11MKA10AH010 -E01 |  |  | 1 | 1739 | 11BFA02.EA002-P2071 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-01 | 3.2 | 400 | N | 40 | GT PKG | 11BFA02.EA002 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, L2, L3, PE | 11MKA10AH010 -E01 | GENERATOR SPACE HEATER | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, L2, L3, PE | B111-016BT0025 → B111-016BT0007 → B111-016BT0019 → B111-016BT0020 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
11MKC01GT002 -E01 | -P20 | 74 |  | PE-L1-1C240-01 | PE-L1-1C240-01 | GT#1-1-11MKC01GT002 -E01 | DONE(10/6) | DONE | 1 | 1740 | 11MKC1001 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-01 | 1100 | 550 | N | 50 | GT PKG | 11MKC01GT002 -E01 | GTG #11 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1 | 11CJT21 | GTG #11 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | L1 | B161-007BC0013 → M0325 → D0320-L27 → M0326 → B111-996AT0021 → B111-016AT0004 → B111-016AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
11MKC01GT002 -E01 | -P20 | 75 |  | PE-L1-1C240-01 | PE-L1-1C240-01 | GT#1-1 | DONE(10/6) | DONE | 1 | 1741 | 11MKC1004 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-01 | 1100 | 550 | N | 50 | GT PKG | 11MKC01GT002 -E01 | GTG #11 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #11 | L2 | 11CJT21 | GTG #11 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | L2 | B161-007BC0013 → M0325 → D0320-L27 → M0326 → B111-996AT0021 → B111-016AT0004 → B111-016AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
11MKC01GT002 -E01 | -P20 | 76 |  | PE-L1-1C240-01 | PE-L1-1C240-01 | GT#1-1 | DONE(10/6) | DONE | 1 | 1742 | 11MKC1007 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-01 | 1100 | 550 | N | 50 | GT PKG | 11MKC01GT002 -E01 | GTG #11 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #11 | L3 | 11CJT21 | GTG #11 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | L3 | B161-007BC0013 → M0325 → D0320-L27 → M0326 → B111-996AT0021 → B111-016AT0004 → B111-016AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
11MKC01GT002 -E01 | -P20 | 77 |  | PE-L1-1C240-01 | PE-L1-1C240-01 | GT#1-1 | DONE(10/6) | DONE | 1 | 1743 | 11MKC1002 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-01 | 1100 | 550 | N | 50 | GT PKG | 11MKC01GT002 -E01 | GTG #11 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1 | 11CJT21 | GTG #11 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | L1 | B161-007BC0014 → M0325 → D0320-L27 → M0326 → B111-996AT0021 → B111-016AT0004 → B111-016AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
11MKC01GT002 -E01 | -P20 | 78 |  | PE-L1-1C240-01 | PE-L1-1C240-01 | GT#1-1 | DONE(10/6) | DONE | 1 | 1744 | 11MKC1005 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-01 | 1100 | 550 | N | 50 | GT PKG | 11MKC01GT002 -E01 | GTG #11 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #11 | L2 | 11CJT21 | GTG #11 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | L2 | B161-007BC0014 → M0325 → D0320-L27 → M0326 → B111-996AT0021 → B111-016AT0004 → B111-016AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
11MKC01GT002 -E01 | -P20 | 79 |  | PE-L1-1C240-01 | PE-L1-1C240-01 | GT#1-1 | DONE(10/6) | DONE | 1 | 1745 | 11MKC1008 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-01 | 1100 | 550 | N | 50 | GT PKG | 11MKC01GT002 -E01 | GTG #11 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #11 | L3 | 11CJT21 | GTG #11 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | L3 | B161-007BC0014 → M0325 → D0320-L27 → M0326 → B111-996AT0021 → B111-016AT0004 → B111-016AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
11MKC01GT002 -E01 | -P20 | 82 |  | PE-L1-1C240-01 | PE-L1-1C240-01 | GT#1-1 | DONE(10/6) | DONE | 1 | 1746 | 11MKC1003 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-01 | 1100 | 550 | N | 50 | GT PKG | 11MKC01GT002 -E01 | GTG #11 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1 | 11CJT21 | GTG #11 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | L1 | B161-007BC0015 → M0325 → D0320-L34 → M0326 → B111-996AT0021 → B111-016AT0004 → B111-016AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
11MKC01GT002 -E01 | -P20 | 83 |  | PE-L1-1C240-01 | PE-L1-1C240-01 | GT#1-1 | DONE(10/6) | DONE | 1 | 1747 | 11MKC1006 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-01 | 1100 | 550 | N | 50 | GT PKG | 11MKC01GT002 -E01 | GTG #11 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #11 | L2 | 11CJT21 | GTG #11 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | L2 | B161-007BC0015 → M0325 → D0320-L34 → M0326 → B111-996AT0021 → B111-016AT0004 → B111-016AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
11MKC01GT002 -E01 | -P20 | 84 |  | PE-L1-1C240-01 | PE-L1-1C240-01 | GT#1-1 | DONE(10/6) | DONE | 1 | 1748 | 11MKC1009 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-01 | 1100 | 550 | N | 50 | GT PKG | 11MKC01GT002 -E01 | GTG #11 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #11 | L3 | 11CJT21 | GTG #11 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | L3 | B161-007BC0015 → M0325 → D0320-L34 → M0326 → B111-996AT0021 → B111-016AT0004 → B111-016AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
11BFA52.DA002 | -P20 | 90 |  | PE-L1-3C4-03 | PE-L1-3C4-03 | GT#1-1-11MKC01GW035 -E01 | DONE(9/28) | DONE | 1 | 1749 | 11BFA52.DA002-P2090 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-03 | 1.2 | 230 | N | 50 | GT PKG | 11BFA52.DA002 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3210) | L1, N, PE | 11MKC01GW035 -E01 | MKC 1AC AUX-VOLT SUP | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, N, PE | B111-016AT0011 → B111-996AT0023 → M0327 → D0329-L24 → M0326 → D0320-L34 → M0325 → B161-007BC0012 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
11BFA51.HA003 | -P20 | 91 |  | PE-L1-5C4-01 | PE-L1-5C4-01 | GT#1-1-11MKC05GE001 -E01 | DONE(10/6) | DONE | 1 | 1750 | 11BFA51.HA003-P2091 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-01 | 1.15 | 400 | N | 50 | GT PKG | 11BFA51.HA003 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, L2, L3, N, PE | 11MKC05GE001 -E01 | TERBO POW-SUP SLRNGRM-VEN | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, L2, L3, N, PE | B111-016AT0011 → B111-996AT0023 → M0327 → D0329-L24 → M0326 → D0320-L34 → M0325 → B161-007BC0012 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MKC05GE001 -X0 (1, 2, 3, 4, N, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
11BFA51.DA003 | -P20 | 92 |  | PE-L1-3C4-18 | PE-L1-3C4-18 | GT#1-1-11MKC10GP001 -E01 | DONE(10/6) | DONE | 1 | 1751 | 11BFA51.DA003-P2092 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-18 | 0.22 | 230 | N | 50 | GT PKG | 11BFA51.DA003 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, N, PE | 11MKC10GP001 -E01 | LIGHTING EXCITER HOUSING | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, N, PE | B111-016AT0011 → B111-996AT0023 → M0327 → D0329-L24 → M0326 → D0320-L34 → M0325 → B161-007BC0012 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
11CJT21 | -P20 | 93 |  | PE-L1-1C240-01 | PE-L1-1C240-01 | GT#1-1-11MKC30GE001 -E01 | DONE(10/12) | DONE | 1 | 1752 | 11CJT1001 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-01 | - | 700 | D | 40 | GT PKG | 11CJT21 | GTG #11 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | L+ | 11MKC30GE001 -E01 | GEN EXCN BRSH | 1.1_MAIN BUILDING COMPLEX / GT #11 | L+ | B111-016BT0005 → B111-016BT0006 → B111-016BT0007 → B111-016BT0019 → B111-016BT0020 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 | To 단자대 Hole 확인필요
11CJT21 | -P20 | 94 |  | PE-L1-1C240-01 | PE-L1-1C240-01 | GT#1-1 | DONE(10/12) | DONE | 1 | 1753 | 11CJT1002 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-01 | - | 700 | D | 40 | GT PKG | 11CJT21 | GTG #11 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | L+ | 11MKC30GE001 -E01 | GEN EXCN BRSH | 1.1_MAIN BUILDING COMPLEX / GT #11 | L+ | B111-016BT0005 → B111-016BT0006 → B111-016BT0007 → B111-016BT0019 → B111-016BT0020 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 | To 단자대 Hole 확인필요
11CJT21 | -P20 | 95 |  | PE-L1-1C240-01 | PE-L1-1C240-01 | GT#1-1 | DONE(10/12) | DONE | 1 | 1754 | 11CJT1003 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-01 | - | 700 | D | 40 | GT PKG | 11CJT21 | GTG #11 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | L+ | 11MKC30GE001 -E01 | GEN EXCN BRSH | 1.1_MAIN BUILDING COMPLEX / GT #11 | L+ | B111-016BT0005 → B111-016BT0006 → B111-016BT0007 → B111-016BT0019 → B111-016BT0020 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 | To 단자대 Hole 확인필요
11CJT21 | -P20 | 96 |  | PE-L1-1C240-01 | PE-L1-1C240-01 | GT#1-1 | DONE(10/12) | DONE | 1 | 1755 | 11CJT1004 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-01 | - | 700 | D | 40 | GT PKG | 11CJT21 | GTG #11 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | L+ | 11MKC30GE001 -E01 | GEN EXCN BRSH | 1.1_MAIN BUILDING COMPLEX / GT #11 | L+ | B111-016BT0005 → B111-016BT0006 → B111-016BT0007 → B111-016BT0019 → B111-016BT0020 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 | To 단자대 Hole 확인필요
11CJT21 | -P20 | 97 |  | PE-L1-1C240-01 | PE-L1-1C240-01 | GT#1-1 | DONE(10/12) | DONE | 1 | 1756 | 11CJT1005 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-01 | - | 700 | D | 40 | GT PKG | 11CJT21 | GTG #11 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | L- | 11MKC30GE001 -E01 | GEN EXCN BRSH | 1.1_MAIN BUILDING COMPLEX / GT #11 | L- | B111-016BT0005 → B111-016BT0006 → B111-016BT0007 → B111-016BT0019 → B111-016BT0020 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 | To 단자대 Hole 확인필요
11CJT21 | -P20 | 98 |  | PE-L1-1C240-01 | PE-L1-1C240-01 | GT#1-1 | DONE(10/12) | DONE | 1 | 1757 | 11CJT1006 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-01 | - | 700 | D | 40 | GT PKG | 11CJT21 | GTG #11 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | L- | 11MKC30GE001 -E01 | GEN EXCN BRSH | 1.1_MAIN BUILDING COMPLEX / GT #11 | L- | B111-016BT0005 → B111-016BT0006 → B111-016BT0007 → B111-016BT0019 → B111-016BT0020 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 | To 단자대 Hole 확인필요
11CJT21 | -P20 | 98 |  | PE-L1-1C240-01 | PE-L1-1C240-01 | GT#1-1 | DONE(10/12) | DONE | 1 | 1758 | 11CJT1007 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-01 | - | 700 | D | 40 | GT PKG | 11CJT21 | GTG #11 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | L- | 11MKC30GE001 -E01 | GEN EXCN BRSH | 1.1_MAIN BUILDING COMPLEX / GT #11 | L- | B111-016BT0005 → B111-016BT0006 → B111-016BT0007 → B111-016BT0019 → B111-016BT0020 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 | To 단자대 Hole 확인필요
11CJT21 | -P20 | 98 |  | PE-L1-1C240-01 | PE-L1-1C240-01 | GT#1-1 | DONE(10/12) | DONE | 1 | 1759 | 11CJT1008 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-01 | - | 700 | D | 40 | GT PKG | 11CJT21 | GTG #11 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #11(UBA3310) | L- | 11MKC30GE001 -E01 | GEN EXCN BRSH | 1.1_MAIN BUILDING COMPLEX / GT #11 | L- | B111-016BT0005 → B111-016BT0006 → B111-016BT0007 → B111-016BT0019 → B111-016BT0020 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 | To 단자대 Hole 확인필요
11BUA51.DA001 | -P20 | 99 |  | PE-L1-2C4-06 | PE-L1-2C4-06 | GT#1-1-11MPB10GW011 -E01 | DONE(10/6) | DONE | 1 | 1760 | 11BUA51.DA001-P2099 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-06 | 1 | 220 | D | 120 | GT PKG | 11BUA51.DA001 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L+, L- | 11MPB10GW011 -E01 | GAS-TURB ENCL EMERG LITG | 1.1_MAIN BUILDING COMPLEX / GT #11 | L+, L- | B111-016AT0011 → B111-996AT0023 → M0327 → D0329-L24 → M0326 → D0320-L24 → M0325 → D0319-L22 → M0324 → B161-006BC0005 → B161-006BC0003 → B161-017BC0101 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
11BFA51.DA004 | -P2 | 100 |  | PE-L1-3C4-18 | PE-L1-3C4-18 | GT#1-1-11MPB10GW023 -E01 | DONE(10/6) | DONE | 1 | 1761 | 11BFA51.DA004-P2100 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-18 | 1 | 230 | N | 120 | GT PKG | 11BFA51.DA004 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, N, PE | 11MPB10GW023 -E01 | GAS-TURB ENCL LITG | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, N, PE | B111-016AT0011 → B111-996AT0023 → M0327 → D0329-L24 → M0326 → D0320-L24 → M0325 → D0319-L22 → M0324 → B161-006BC0005 → B161-006BC0003 → B161-017BC0102 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
11BUA51.DA002 | -P2 | 101 |  | PE-L1-2C4-06 | PE-L1-2C4-06 | GT#1-1-11MPB13GW011 -E01 | DONE(10/6) | DONE | 1 | 1762 | 11BUA51.DA002-P2101 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-06 | 0.22 | 220 | D | 40 | GT PKG | 11BUA51.DA002 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L+, L- | 11MPB13GW011 -E01 | FGS ENCL EMERG LITG | 1.1_MAIN BUILDING COMPLEX / GT #11 | L+, L- | B111-016BT0001 → B111-996BT0022 → M0327 → B161-006BC0021 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
11BFA51.DA005 | -P2 | 102 |  | PE-L1-3C4-18 | PE-L1-3C4-18 | GT#1-1-11MPB13GW023 -E01 |  |  | 1 | 1763 | 11BFA51.DA005-P2102 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-18 | 1 | 230 | N | 40 | GT PKG | 11BFA51.DA005 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, N, PE | 11MPB13GW023 -E01 | FGS ENCL LITG | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, N, PE | B111-016BT0001 → B111-996BT0022 → M0327 → B161-006BC0020 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
11BUA51.DA003 | -P2 | 103 |  | PE-L1-2C4-06 | PE-L1-2C4-06 | GT#1-1-11MPB16GW011 -E01 | DONE(10/6) | DONE | 1 | 1764 | 11BUA51.DA003-P2103 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-06 | 0.44 | 220 | D | 30 | GT PKG | 11BUA51.DA003 | GTG #11 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L+, L- | 11MPB16GW011 -E01 | IMS + GEN ENCL EMERG LITG | 1.1_MAIN BUILDING COMPLEX / GT #11 | L+, L- | B111-016AT0011 → B111-016AT0010 → B111-016AT0009 → B111-016AT0015 → B111-016AT0016 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
11BFA51.DA006 | -P2 | 104 |  | PE-L1-3C4-01 | PE-L1-3C4-01 | GT#1-1-11MPB16GW023 -E01 | DONE(10/6) | DONE | 1 | 1765 | 11BFA51.DA006-P2104 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-01 | 1 | 230 | N | 30 | GT PKG | 11BFA51.DA006 | GTG #11 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, N, PE | 11MPB16GW023 -E01 | IMS + GEN ENCL LITG | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, N, PE | B111-016AT0011 → B111-016AT0010 → B111-016AT0009 → B111-016AT0015 → B111-016AT0016 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
11BMA51.CB001 | -P2 | 105 |  | PE-L1-4C4-01 | PE-L1-4C4-01 | GT#1-1-11SAM33AN001 -M01 |  |  | 1 | 1766 | 11BMA51.CB001-P2105 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-01 | 0.55 | 400 | E | 60 | GT PKG | 11BMA51.CB001 | GTG #11 400V AC EMERGENCY SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, L2, L3, PE | 11SAM33AN001 -M01 | EXH-AIR FAN FU-GAS ENCL | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, L2, L3, PE | B111-016BT0025 → B111-016BT0007 → B111-016BT0008 → B111-016BT0009 → B111-016BT0010 → B111-016BT0002 → B111-016BT0012 → B111-996BT0026 → B161-016BC0109 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
11BFA02.FB001 | -P2 | 106 |  | PE-L1-4C4-01 | PE-L1-4C4-01 | GT#1-1-11SAM33AN002 -M01 |  |  | 1 | 1767 | 11BFA02.FB001-P2106 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-01 | 0.55 | 400 | N | 60 | GT PKG | 11BMA51.CB003 | GTG #11 400V AC EMERGENCY SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #11 | L1, L2, L3, PE | 11SAM33AN002 -M01 | EXH-AIR FAN FU-GAS ENCL | 1.1_MAIN BUILDING COMPLEX / GT #11 | L1, L2, L3, PE | B111-016BT0025 → B111-016BT0007 → B111-016BT0008 → B111-016BT0009 → B111-016BT0010 → B111-016BT0002 → B111-016BT0012 → B111-996BT0026 → B161-016BC0110 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
12BFA51.DA001 | -P20 | 01 | 미배정Drum 사용(10/6) | PE-L1-3C4-18 | PE-L1-3C4-18 | GT#1-2-12BAB11GW023 -E01 | DONE(10/6) | DONE | 1 | 1768 | 12BFA51.DA001-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-18 | 0.15 | 230 | N | 30 | GT PKG | 12BFA51.DA001 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, N, PE | 12BAB11GW023 -E01 | GEN NEUT GND CAB | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, N, PE | B111-016CT0001 → B111-016CT0010 → B111-016CT0009 → B111-016CT0015 → B111-016CT0016 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
12BFA03.CB001 | -P20 | 02 |  | PE-L1-3C4-18 | PE-L1-3C4-18 | GT#1-2-12MBA18AA001 -Y01 | DONE(10/6) | DONE | 1 | 1769 | 12BFA03.CB001-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-18 | 0.073 | 230 | N | 120 | GT PKG | 12BFA03.CB001 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, N, PE | 12MBA18AA001 -Y01 | DRN-VLV 1 FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, N, PE | B111-996CT0021 → B111-016CT0004 → B111-016CT0003 → B111-016CT0002 → B111-016CT0001 → M0322 → D0318-L24 → M0321 → D0317-L24 → M0320 → B161-006DC0004 → B161-007DC0001 → B161-006DC0023 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MYB17GF010 -X01 (701, 702, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 13
12BFA03.CB002 | -P20 | 03 |  | PE-L1-3C4-18 | PE-L1-3C4-18 | GT#1-2-12MBA18AA002 -Y01 | DONE(10/6) | DONE | 1 | 1770 | 12BFA03.CB002-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-18 | 0.073 | 230 | N | 120 | GT PKG | 12BFA03.CB002 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, N, PE | 12MBA18AA002 -Y01 | DRN-VLV 2 FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, N, PE | B111-996CT0021 → B111-016CT0004 → B111-016CT0003 → B111-016CT0002 → B111-016CT0001 → M0322 → D0318-L24 → M0321 → D0317-L24 → M0320 → B161-006DC0004 → B161-007DC0001 → B161-006DC0023 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MYB17GF010 -X01 (703, 704, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 13
12BFA03.CB003 | -P20 | 04 |  | PE-L1-3C4-18 | PE-L1-3C4-18 | GT#1-2-12MBA18AA003 -Y01 | DONE(10/6) | DONE | 1 | 1771 | 12BFA03.CB003-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-18 | 0.073 | 230 | N | 120 | GT PKG | 12BFA03.CB003 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, N, PE | 12MBA18AA003 -Y01 | DRN-VLV 3 FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, N, PE | B111-996CT0021 → B111-016CT0004 → B111-016CT0003 → B111-016CT0002 → B111-016CT0001 → M0322 → D0318-L24 → M0321 → D0317-L24 → M0320 → B161-006DC0004 → B161-007DC0001 → B161-006DC0023 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MYB17GF010 -X01 (705, 706, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 13
12BFA02.CB001 | -P20 | 05 |  | PE-L1-4C4-02 | PE-L1-4C4-02 | GT#1-2-12MBA30AP001 -M01 | DONE(10/6) | DONE | 1 | 1772 | 12BFA02.CB001-P2005 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-02 | 4.9 | 400 | N | 120 | GT PKG | 12BFA02.CB001 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, L2, L3, PE | 12MBA30AP001 -M01 | MXG-PP | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, L2, L3, PE | B111-996CT0021 → B111-016CT0004 → B111-016CT0003 → B111-016CT0002 → B111-016CT0001 → M0322 → D0318-L24 → M0321 → D0317-L24 → M0320 → B161-006DC0002 → B161-017DC0112 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
12BFA02.EA003 | -P20 | 06 |  | PE-L1-3C4-18 | PE-L1-3C4-18 | GT#1-2-12MBA32AP001 -M01 | DONE(10/6) | DONE | 1 | 1773 | 12BFA02.EA003-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-18 | 0.5 | 230 | N | 120 | GT PKG | 12BFA02.EA003 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, N, PE | 12MBA32AP001 -M01 | CLNG-AGT-PP | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, N, PE | B111-996CT0021 → B111-016CT0004 → B111-016CT0003 → B111-016CT0002 → B111-016CT0001 → M0322 → D0318-L24 → M0321 → D0317-L24 → M0320 → B161-006DC0002 → B161-017DC0113 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
12BFA53.DA002 | -P20 | 07 |  | PE-L1-3C4-18 | PE-L1-3C4-18 | GT#1-2-12MBA32GQ012 -X01 | DONE(10/6) | DONE | 1 | 1774 | 12BFA53.DA002-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-18 | 0.5 | 230 | N | 120 | GT PKG | 12BFA53.DA002 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, N, PE | 12MBA32GQ012 -X01 | EL-SCKT JUNCT-BOX | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, N, PE | B111-996CT0021 → B111-016CT0004 → B111-016CT0003 → B111-016CT0002 → B111-016CT0001 → M0322 → D0318-L24 → M0321 → D0317-L24 → M0320 → B161-006DC0002 → B161-017DC0114 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
12BFA02.EA004 | -P20 | 08 |  | PE-L1-3C4-17 | PE-L1-3C4-17 | GT#1-2-12MBA33AP001 -M01 | DONE(10/6) | DONE | 1 | 1775 | 12BFA02.EA004-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-17 | 0.5 | 230 | N | 120 | GT PKG | 12BFA02.EA004 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, N, PE | 12MBA33AP001 -M01 | ANTIFRZ-AGT-PP | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, N, PE | B111-996CT0021 → B111-016CT0004 → B111-016CT0003 → B111-016CT0002 → B111-016CT0001 → M0322 → D0318-L24 → M0321 → D0317-L24 → M0320 → B161-006DC0002 → B161-017DC0115 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
12BFA02.CB002 | -P20 | 09 |  | PE-L1-4C4-01 | PE-L1-4C4-01 | GT#1-2-12MBA51AP001 -M01 |  |  | 1 | 1776 | 12BFA02.CB002-P2009 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-01 | 2.2 | 400 | N | 50 | GT PKG | 12BFA02.CB002 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, L2, L3, PE | 12MBA51AP001 -M01 | HYDRC-PP 1 HCO | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, L2, L3, PE | B111-016DT0001 → B111-016DT0002 → B111-016DT0012 → B111-996DT0026 → B161-016DC0117 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
12BFA02.CB003 | -P20 | 10 |  | PE-L1-4C4-01 | PE-L1-4C4-01 | GT#1-2-12MBA51AP002 -M01 |  |  | 1 | 1777 | 12BFA02.CB003-P2010 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-01 | 2.2 | 400 | N | 60 | GT PKG | 12BFA02.CB003 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, L2, L3, PE | 12MBA51AP002 -M01 | HYDRC-PP 2 HCO | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, L2, L3, PE | B111-016DT0025 → B111-016DT0007 → B111-016DT0008 → B111-016DT0009 → B111-016DT0010 → B111-016DT0002 → B111-016DT0012 → B111-996DT0026 → B161-016DC0118 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
12CJT91 (12MBJ01GS091 -E01) | -P10 | 01 | Drum 재배정(9/30) | PE-M3-1C240-02 | PE-M1-1C240-08 | GT#1-2-12MBJ01GS091 -E01 |  |  | 1 | 1778 | 12CJT0001 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-08 |  | 1400 | N | 60 | GT PKG | 12CJT91 (12MBJ01GS091 -E01) | GTG #12 SFC CABINET (GTG #12 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | U1 | B1-CB-12301 | BLOCK #1 GENERATOR CIRCUIT BREAKER FOR GT#2 | 1.1_MAIN BUILDING COMPLEX / GT #12 | U1 | B161-013DC0001 → B161-003DC0007 → M0321 → D0318-M11 → M0322 → B111-993BT0021 → B111-013BT0004 → B111-013BT0003 → B111-013BT0002 → B111-013BT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
12CJT91 (12MBJ01GS091 -E01) | -P10 | 02 | Drum 재배정(9/30) | PE-M3-1C240-02 | PE-M1-1C240-08 | GT#1-2 |  |  | 1 | 1779 | 12CJT0004 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-08 |  | 1400 | N | 60 | GT PKG | 12CJT91 (12MBJ01GS091 -E01) | GTG #12 SFC CABINET (GTG #12 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | V1 | B1-CB-12301 | BLOCK #1 GENERATOR CIRCUIT BREAKER FOR GT#2 | 1.1_MAIN BUILDING COMPLEX / GT #12 | V1 | B161-013DC0001 → B161-003DC0007 → M0321 → D0318-M11 → M0322 → B111-993BT0021 → B111-013BT0004 → B111-013BT0003 → B111-013BT0002 → B111-013BT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
12CJT91 (12MBJ01GS091 -E01) | -P10 | 03 | Drum 재배정(9/30) | PE-M3-1C240-02 | PE-M1-1C240-08 | GT#1-2 |  |  | 1 | 1780 | 12CJT0007 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-08 |  | 1400 | N | 60 | GT PKG | 12CJT91 (12MBJ01GS091 -E01) | GTG #12 SFC CABINET (GTG #12 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | W1 | B1-CB-12301 | BLOCK #1 GENERATOR CIRCUIT BREAKER FOR GT#2 | 1.1_MAIN BUILDING COMPLEX / GT #12 | W1 | B161-013DC0001 → B161-003DC0007 → M0321 → D0318-M11 → M0322 → B111-993BT0021 → B111-013BT0004 → B111-013BT0003 → B111-013BT0002 → B111-013BT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
12CJT91 (12MBJ01GS091 -E01) | -P10 | 04 | Drum 재배정(9/30) | PE-M3-1C240-02 | PE-M1-1C240-08 | GT#1-2 |  |  | 1 | 1781 | 12CJT0002 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-08 |  | 1400 | N | 60 | GT PKG | 12CJT91 (12MBJ01GS091 -E01) | GTG #12 SFC CABINET (GTG #12 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | U1 | B1-CB-12301 | BLOCK #1 GENERATOR CIRCUIT BREAKER FOR GT#2 | 1.1_MAIN BUILDING COMPLEX / GT #12 | U1 | B161-013DC0002 → B161-003DC0008 → M0321 → D0318-M12 → M0322 → B111-993BT0021 → B111-013BT0004 → B111-013BT0003 → B111-013BT0002 → B111-013BT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
12CJT91 (12MBJ01GS091 -E01) | -P10 | 05 | Drum 재배정(9/30) | PE-M3-1C240-02 | PE-M1-1C240-08 | GT#1-2 |  |  | 1 | 1782 | 12CJT0005 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-08 |  | 1400 | N | 60 | GT PKG | 12CJT91 (12MBJ01GS091 -E01) | GTG #12 SFC CABINET (GTG #12 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | V1 | B1-CB-12301 | BLOCK #1 GENERATOR CIRCUIT BREAKER FOR GT#2 | 1.1_MAIN BUILDING COMPLEX / GT #12 | V1 | B161-013DC0002 → B161-003DC0008 → M0321 → D0318-M12 → M0322 → B111-993BT0021 → B111-013BT0004 → B111-013BT0003 → B111-013BT0002 → B111-013BT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
12CJT91 (12MBJ01GS091 -E01) | -P10 | 06 | Drum 재배정(9/30) | PE-M3-1C240-02 | PE-M1-1C240-09 | GT#1-2 |  |  | 1 | 1783 | 12CJT0008 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-09 |  | 1400 | N | 60 | GT PKG | 12CJT91 (12MBJ01GS091 -E01) | GTG #12 SFC CABINET (GTG #12 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | W1 | B1-CB-12301 | BLOCK #1 GENERATOR CIRCUIT BREAKER FOR GT#2 | 1.1_MAIN BUILDING COMPLEX / GT #12 | W1 | B161-013DC0002 → B161-003DC0008 → M0321 → D0318-M12 → M0322 → B111-993BT0021 → B111-013BT0004 → B111-013BT0003 → B111-013BT0002 → B111-013BT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
12CJT91 (12MBJ01GS091 -E01) | -P10 | 07 | Drum 재배정(9/30) | PE-M3-1C240-02 | PE-M1-1C240-09 | GT#1-2 |  |  | 1 | 1784 | 12CJT0003 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-09 |  | 1400 | N | 60 | GT PKG | 12CJT91 (12MBJ01GS091 -E01) | GTG #12 SFC CABINET (GTG #12 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | U1 | B1-CB-12301 | BLOCK #1 GENERATOR CIRCUIT BREAKER FOR GT#2 | 1.1_MAIN BUILDING COMPLEX / GT #12 | U1 | B161-013DC0003 → B161-003DC0009 → M0321 → D0318-M13 → M0322 → B111-993BT0021 → B111-013BT0004 → B111-013BT0003 → B111-013BT0002 → B111-013BT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
12CJT91 (12MBJ01GS091 -E01) | -P10 | 08 | Drum 재배정(9/30) | PE-M3-1C240-02 | PE-M1-1C240-09 | GT#1-2 |  |  | 1 | 1785 | 12CJT0006 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-09 |  | 1400 | N | 60 | GT PKG | 12CJT91 (12MBJ01GS091 -E01) | GTG #12 SFC CABINET (GTG #12 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | V1 | B1-CB-12301 | BLOCK #1 GENERATOR CIRCUIT BREAKER FOR GT#2 | 1.1_MAIN BUILDING COMPLEX / GT #12 | V1 | B161-013DC0003 → B161-003DC0009 → M0321 → D0318-M13 → M0322 → B111-993BT0021 → B111-013BT0004 → B111-013BT0003 → B111-013BT0002 → B111-013BT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
12CJT91 (12MBJ01GS091 -E01) | -P10 | 09 | Drum 재배정(9/30) | PE-M3-1C240-02 | PE-M1-1C240-09 | GT#1-2 |  |  | 1 | 1786 | 12CJT0009 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-09 |  | 1400 | N | 60 | GT PKG | 12CJT91 (12MBJ01GS091 -E01) | GTG #12 SFC CABINET (GTG #12 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | W1 | B1-CB-12301 | BLOCK #1 GENERATOR CIRCUIT BREAKER FOR GT#2 | 1.1_MAIN BUILDING COMPLEX / GT #12 | W1 | B161-013DC0003 → B161-003DC0009 → M0321 → D0318-M13 → M0322 → B111-993BT0021 → B111-013BT0004 → B111-013BT0003 → B111-013BT0002 → B111-013BT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
12MBJ01GT002 -E01 | -P10 | 01 | Drum 재배정(9/30) SE의견에 때른 재포설필요 | PE-M3-1C240-02 | PE-M1-1C240-09 | GT#1-2-12MBJ01GT002 -E01 |  | DONE 재포설 | 1 | 1787 | 12MBJ0001 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-09 |  | 1400 | N | 35 | GT PKG | 12MBJ01GT002 -E01 | GTG #12 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #12 | U1 | 12CJT91 | GTG #12 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | U1 | B161-003DC0003 → M0322 → B111-993BT0021 → B111-013BT0004 → B111-013BT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
12MBJ01GT002 -E01 | -P10 | 02 | Drum 재배정(9/30) SE의견에 때른 재포설필요 | PE-M3-1C240-04 | PE-M1-1C240-10 | GT#1-2 |  | DONE 재포설 | 1 | 1788 | 12MBJ0004 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-10 |  | 1400 | N | 35 | GT PKG | 12MBJ01GT002 -E01 | GTG #12 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #12 | V1 | 12CJT91 | GTG #12 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | V1 | B161-003DC0003 → M0322 → B111-993BT0021 → B111-013BT0004 → B111-013BT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
12MBJ01GT002 -E01 | -P10 | 03 | Drum 재배정(9/30) SE의견에 때른 재포설필요 | PE-M3-1C240-04 | PE-M1-1C240-10 | GT#1-2 |  | DONE 재포설 | 1 | 1789 | 12MBJ0007 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-10 |  | 1400 | N | 35 | GT PKG | 12MBJ01GT002 -E01 | GTG #12 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #12 | W1 | 12CJT91 | GTG #12 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | W1 | B161-003DC0003 → M0322 → B111-993BT0021 → B111-013BT0004 → B111-013BT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
12MBJ01GT002 -E01 | -P10 | 04 | Drum 재배정(9/30) SE의견에 때른 재포설필요 | PE-M3-1C240-04 | PE-M1-1C240-10 | GT#1-2 |  | DONE 재포설 | 1 | 1790 | 12MBJ0002 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-10 |  | 1400 | N | 35 | GT PKG | 12MBJ01GT002 -E01 | GTG #12 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #12 | U1 | 12CJT91 | GTG #12 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | U1 | B161-003DC0004 → M0322 → B111-993BT0021 → B111-013BT0004 → B111-013BT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
12MBJ01GT002 -E01 | -P10 | 05 | Drum 재배정(9/30) SE의견에 때른 재포설필요 | PE-M3-1C240-04 | PE-M1-1C240-10 | GT#1-2 |  | DONE 재포설 | 1 | 1791 | 12MBJ0005 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-10 |  | 1400 | N | 35 | GT PKG | 12MBJ01GT002 -E01 | GTG #12 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #12 | V1 | 12CJT91 | GTG #12 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | V1 | B161-003DC0004 → M0322 → B111-993BT0021 → B111-013BT0004 → B111-013BT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
12MBJ01GT002 -E01 | -P10 | 06 | Drum 재배정(9/30) SE의견에 때른 재포설필요 | PE-M3-1C240-04 | PE-M1-1C240-10 | GT#1-2 |  | DONE 재포설 | 1 | 1792 | 12MBJ0008 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-10 |  | 1400 | N | 35 | GT PKG | 12MBJ01GT002 -E01 | GTG #12 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #12 | W1 | 12CJT91 | GTG #12 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | W1 | B161-003DC0004 → M0322 → B111-993BT0021 → B111-013BT0004 → B111-013BT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
12MBJ01GT002 -E01 | -P10 | 07 | Drum 재배정(9/30) SE의견에 때른 재포설필요 | PE-M3-1C240-04 | PE-M1-1C240-10 | GT#1-2 |  | DONE 재포설 | 1 | 1793 | 12MBJ0003 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-10 |  | 1400 | N | 35 | GT PKG | 12MBJ01GT002 -E01 | GTG #12 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #12 | U1 | 12CJT91 | GTG #12 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | U1 | B161-003DC0005 → M0322 → B111-993BT0021 → B111-013BT0004 → B111-013BT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
12MBJ01GT002 -E01 | -P10 | 08 | Drum 재배정(9/30) SE의견에 때른 재포설필요 | PE-M3-1C240-04 | PE-M1-1C240-10 | GT#1-2 |  | DONE 재포설 | 1 | 1794 | 12MBJ0006 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-10 |  | 1400 | N | 35 | GT PKG | 12MBJ01GT002 -E01 | GTG #12 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #12 | V1 | 12CJT91 | GTG #12 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | V1 | B161-003DC0005 → M0322 → B111-993BT0021 → B111-013BT0004 → B111-013BT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
12MBJ01GT002 -E01 | -P10 | 09 | Drum 재배정(9/30) SE의견에 때른 재포설필요 | PE-M3-1C240-04 | PE-M1-1C240-10 | GT#1-2 |  | DONE 재포설 | 1 | 1795 | 12MBJ0009 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-10 |  | 1400 | N | 35 | GT PKG | 12MBJ01GT002 -E01 | GTG #12 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #12 | W1 | 12CJT91 | GTG #12 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | W1 | B161-003DC0005 → M0322 → B111-993BT0021 → B111-013BT0004 → B111-013BT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57 | zz
12BFA52.DA001 | -P20 | 11 |  | PE-L1-3C4-17 | PE-L1-3C4-17 | GT#1-2-12MBJ01GW035 -E01 | DONE(9/28) | DONE | 1 | 1796 | 12BFA52.DA001-P2011 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-17 | 1.2 | 230 | N | 40 | GT PKG | 12BFA52.DA001 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, N, PE | 12MBJ01GW035 -E01 | MBJ 1AC AUX-VOLT SUP | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, N, PE | B111-016CT0001 → B111-016CT0002 → B111-016CT0003 → B111-016CT0004 → B111-996CT0021 → M0322 → B161-007DC0010 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
12BFA53.HA002 | -P20 | 12 |  | PE-L1-5C6-01 | PE-L1-5C6-01 | GT#1-2-12MBL10GH001 -E01 |  | DONE | 1 | 1797 | 12BFA53.HA002-P2012 | 0.6/1kV CU/XLPE/LSZH | 5C x 6sqmm | PE-L1-5C6-01 | 15 | 400 | N | 165 | GT PKG | 12BFA53.HA002 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, L2, L3, N, PE | 12MBL10GH001 -E01 | CABINET AIR INTAKE | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, L2, L3, N, PE | B111-016CT0001 → B111-016CT0002 → B111-016CT0003 → B111-016CT0004 → B111-996CT0021 → M0322 → D0318-L31 → M0321 → B161-006DC0025 → B161-026EC0006 → B161-026EC0004 → B161-026EC0003 → B161-026EC0001 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MBL10GH001 -X01 (001, 002, 003, 004, 005) | 1 | A2F-S-25a-N34 | 16 - 20.5 | 17
12BFA53.HA003 | -P20 | 13 |  | PE-L1-5C6-01 | PE-L1-5C6-01 | GT#1-2-12MBL20GH001 -E01 |  | DONE | 1 | 1798 | 12BFA53.HA003-P2013 | 0.6/1kV CU/XLPE/LSZH | 5C x 6sqmm | PE-L1-5C6-01 | 11 | 400 | N | 115 | GT PKG | 12BFA53.HA003 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, L2, L3, N, PE | 12MBL20GH001 -E01 | CAB AIR-INTK-FLP | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, L2, L3, N, PE | B111-016CT0001 → B111-016CT0002 → B111-016CT0003 → B111-016CT0004 → B111-996CT0021 → M0322 → D0318-L24 → M0321 → D0317-L25 → M0320 → B161-006DC0004 → B161-016DC0101 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MBL20GH001 -X01 (001, 002, 003, 004, 005) | 1 | A2F-S-25a-N34 | 16 - 20.5 | 17
12BFA51.HA001 | -P20 | 14 |  | PE-L1-5C4-02 | PE-L1-5C4-02 | GT#1-2-12MBL25AT001 -E01 |  | DONE | 1 | 1799 | 12BFA51.HA001-P2014 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-02 | 5.2 | 400 | N | 110 | GT PKG | 12BFA51.HA001 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, L2, L3, N, PE | 12MBL25AT001 -E01 | STANDSTL AIR DEHUMI | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, L2, L3, N, PE | B111-016CT0001 → B111-016CT0002 → B111-016CT0003 → B111-016CT0004 → B111-996CT0021 → M0322 → D0318-L24 → M0321 → D0317-L25 → M0320 → B161-006DC0006 → B161-016DC0037 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 15
12BFA03.JB001 | -P20 | 15 |  | PE-L1-5C25/16-02 | PE-L1-5C25/16-02 | GT#1-2-12MBL30GH001 -E01 |  | DONE | 1 | 1800 | 12BFA03.JB001-P2015 | 0.6/1kV CU/XLPE/LSZH | 4C x 25sqmm + 1C X 16sqmm | PE-L1-5C25/16-02 | 40 | 400 | N | 85 | GT PKG | 12BFA03.JB001 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, L2, L3, N, PE | 12MBL30GH001 -E01 | CAB PULS-AIR | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, L2, L3, N, PE | B111-016CT0001 → B111-016CT0002 → B111-016CT0003 → B111-016CT0004 → B111-996CT0021 → M0322 → D0318-L22 → M0321 → D0317-L25 → M0320 → B161-006DC0007 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MBL30GH001 -X01 (001, 002, 003, 004, 005) | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5
12BFA53.HA004 | -P20 | 16 |  | PE-L1-5C6-01 | PE-L1-5C6-01 | GT#1-2-12MBL40GH001 -E01 |  | DONE | 1 | 1801 | 12BFA53.HA004-P2016 | 0.6/1kV CU/XLPE/LSZH | 5C x 6sqmm | PE-L1-5C6-01 | 18 | 400 | N | 105 | GT PKG | 12BFA53.HA004 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, L2, L3, N, PE | 12MBL40GH001 -E01 | CAB EVAP COOL | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, L2, L3, N, PE | B111-016CT0001 → B111-016CT0002 → B111-016CT0003 → B111-016CT0004 → B111-996CT0021 → M0322 → D0318-L24 → M0321 → D0317-L25 → M0320 → B161-006DC0006 → B161-016DC0103 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MBL40GH001 -X01 (001, 002, 003, 004, 005) | 1 | A2F-S-25a-N34 | 16 - 20.5 | 17
12BFA03.CB004 | -P20 | 17 |  | PE-L1-3C4-18 | PE-L1-3C4-18 | GT#1-2-12MBM12GT100 -E01 |  | DONE | 1 | 1802 | 12BFA03.CB004-P2017 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-18 | 1.6 | 230 | N | 120 | GT PKG | 12BFA03.CB004 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, N, PE | 12MBM12GT100 -E01 | IGNITION TRANSFORMERS | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, N, PE | B111-016CT0001 → B111-016CT0002 → B111-016CT0003 → B111-016CT0004 → B111-996CT0021 → M0322 → D0318-L23 → M0321 → D0317-L22 → M0320 → B161-006DC0005 → B161-006DC0003 → B161-017DC0103 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MYB30GF202 -X03 | 1 | A2F-S-25-N34 | 12 - 18 | 13
12BUA01.EA001 | -P20 | 18 | 재배정 | PE-L1-2C4-01 | PE-L1-2C4-06 | GT#1-2-12MBN12AA505 -Y01 |  | DONE | 1 | 1803 | 12BUA01.EA001-P2018 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-06 | 0.055 | 220 | D | 90 | GT PKG | 12BUA01.EA001 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L+, L- | 12MBN12AA505 -Y01 | RL-VLV FEED FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #12 | L+, L- | B111-016CT0001 → B111-016CT0010 → B111-016CT0009 → B111-016CT0008 → B111-016CT0007 → B111-016CT0024 → B111-996CT0023 → M0323 → B161-006DC0014 → B161-017DC0132 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MBY08GF001 -X04 (401, 402) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
12BUA01.EA002 | -P20 | 19 | 재배정 | PE-L1-2C4-01 | PE-L1-2C4-06 | GT#1-2-12MBN13AA501 -Y01 |  | DONE | 1 | 1804 | 12BUA01.EA002-P2019 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-06 | 0.048 | 220 | D | 80 | GT PKG | 12BUA01.EA002 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L+, L- | 12MBN13AA501 -Y01 | STOP-VLV FUEL OIL SUPPLY | 1.1_MAIN BUILDING COMPLEX / GT #12 | L+, L- | B111-016CT0001 → B111-016CT0010 → B111-016CT0009 → B111-016CT0008 → B111-016CT0007 → B111-016CT0024 → B111-996CT0023 → M0323 → B161-006DC0014 → B161-017DC0133 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MYB30GF010 -X03 (403, 404) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
12BUA01.EA003 | -P20 | 20 | 재배정 | PE-L1-2C4-01 | PE-L1-2C4-06 | GT#1-2-12MBN13AA502 -Y01 |  | DONE | 1 | 1805 | 12BUA01.EA003-P2020 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-06 | 0.048 | 220 | D | 80 | GT PKG | 12BUA01.EA003 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L+, L- | 12MBN13AA502 -Y01 | RL-VLV RETN DIFFU FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #12 | L+, L- | B111-016CT0001 → B111-016CT0010 → B111-016CT0009 → B111-016CT0008 → B111-016CT0007 → B111-016CT0024 → B111-996CT0023 → M0323 → B161-006DC0014 → B161-017DC0134 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MYB30GF010 -X03 (401, 402) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
12BUA51.JA001 | -P20 | 21 | 미배정Drum사용 5C4로 재포설필요 | PE-L1-5C4-02 | PE-L1-5C4-02 | GT#1-2-12MBN21AA001 -Y02 |  | DONE 재포설 | 1 | 1806 | 12BUA51.JA001-P2021 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-02 | 0.13 | 220 | D | 120 | GT PKG | 12BUA51.JA001 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 12MBN21AA001 -Y02 | BLL-VLV ASSY LFT FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #12 | RL, LL, L-, BR, PE | B111-016CT0001 → B111-016CT0002 → B111-016CT0003 → B111-016CT0004 → B111-996CT0021 → M0322 → D0318-L23 → M0321 → D0317-L22 → M0320 → B161-006DC0005 → B161-006DC0003 → B161-017DC0104 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 15
12BUA01.EA004 | -P20 | 22 |  | PE-L1-2C4-01 | PE-L1-2C4-01 | GT#1-2-12MBN21AA002 -Y01 |  | DONE | 1 | 1807 | 12BUA01.EA004-P2022 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-01 | 0.048 | 220 | D | 120 | GT PKG | 12BUA01.EA004 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L+, L- | 12MBN21AA002 -Y01 | BYP-VLV LFT FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #12 | L+, L- | B111-016CT0001 → B111-016CT0002 → B111-016CT0003 → B111-016CT0004 → B111-996CT0021 → M0322 → D0318-L23 → M0321 → D0317-L22 → M0320 → B161-006DC0005 → B161-006DC0003 → B161-017DC0105 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MYB30GF102 -X03 (429, 430) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
12BUA51.KB001 | -P20 | 23 | 미배정Drum사용 5C4로 재포설필요 | PE-L1-5C4-02 | PE-L1-5C4-02 | GT#1-2-12MBN22AA001 -Y02 |  | DONE 재포설 | 1 | 1808 | 12BUA51.KB001-P2023 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-02 | 0.13 | 220 | D | 120 | GT PKG | 12BUA51.KB001 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 12MBN22AA001 -Y02 | BLL-VLV ASSY RGHT FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #12 | RL, LL, L-, BR, PE | B111-016CT0001 → B111-016CT0002 → B111-016CT0003 → B111-016CT0004 → B111-996CT0021 → M0322 → D0318-L23 → M0321 → D0317-L22 → M0320 → B161-006DC0005 → B161-006DC0003 → B161-017DC0106 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 15
12BUA01.FB001 | -P20 | 24 |  | PE-L1-2C4-01 | PE-L1-2C4-01 | GT#1-2-12MBN22AA002 -Y01 |  | DONE | 1 | 1809 | 12BUA01.FB001-P2024 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-01 | 0.048 | 220 | D | 120 | GT PKG | 12BUA01.FB001 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L+, L- | 12MBN22AA002 -Y01 | BYP-VLV RGHT FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #12 | L+, L- | B111-016CT0001 → B111-016CT0002 → B111-016CT0003 → B111-016CT0004 → B111-996CT0021 → M0322 → D0318-L23 → M0321 → D0317-L22 → M0320 → B161-006DC0005 → B161-006DC0003 → B161-017DC0107 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MYB30GF202 -X03 (429, 430) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
12BUA01.FB002 | -P20 | 25 |  | PE-L1-2C4-01 | PE-L1-2C4-01 | GT#1-2-12MBN23AA501 -Y01 |  | DONE | 1 | 1810 | 12BUA01.FB002-P2025 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-01 | 0.048 | 220 | D | 120 | GT PKG | 12BUA01.FB002 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L+, L- | 12MBN23AA501 -Y01 | DRN-VLV FEED PREM FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #12 | L+, L- | B111-016CT0001 → B111-016CT0002 → B111-016CT0003 → B111-016CT0004 → B111-996CT0021 → M0322 → D0318-L23 → M0321 → D0317-L22 → M0320 → B161-006DC0005 → B161-006DC0003 → B161-017DC0108 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MYB30GF010 -X03 (405, 406) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
12BUA51.MA001 | -P20 | 26 | 미배정Drum사용 5C4로 재포설필요 | PE-L1-5C4-02 | PE-L1-5C4-02 | GT#1-2-12MBN25AA001 -Y02 |  | DONE 재포설 | 1 | 1811 | 12BUA51.MA001-P2026 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-02 | 0.13 | 220 | D | 120 | GT PKG | 12BUA51.MA001 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 12MBN25AA001 -Y02 | BLL-VLV PREM LFT FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #12 | RL, LL, L-, BR, PE | B111-016CT0001 → B111-016CT0002 → B111-016CT0003 → B111-016CT0004 → B111-996CT0021 → M0322 → D0318-L23 → M0321 → D0317-L22 → M0320 → B161-006DC0005 → B161-006DC0003 → B161-017DC0109 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MYB30GF102 -X03 (401, 402, 403, 404, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
12BUA01.FB003 | -P20 | 27 |  | PE-L1-2C4-01 | PE-L1-2C4-01 | GT#1-2-12MBN25AA501 -Y01 |  | DONE | 1 | 1812 | 12BUA01.FB003-P2027 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-01 | 0.053 | 220 | D | 120 | GT PKG | 12BUA01.FB003 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L+, L- | 12MBN25AA501 -Y01 | FIL-VLV PREM LFT FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #12 | L+, L- | B111-016CT0001 → B111-016CT0002 → B111-016CT0003 → B111-016CT0004 → B111-996CT0021 → M0322 → D0318-L23 → M0321 → D0317-L22 → M0320 → B161-006DC0005 → B161-006DC0003 → B161-017DC0110 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MYB30GF102 -X03 (701, 702) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
12BUA51.NB001 | -P20 | 28 | 미배정Drum사용 5C4로 재포설필요 | PE-L1-5C4-02 | PE-L1-5C4-02 | GT#1-2-12MBN26AA001 -Y02 |  | DONE 재포설 | 1 | 1813 | 12BUA51.NB001-P2028 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-02 | 0.13 | 220 | D | 120 | GT PKG | 12BUA51.NB001 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 12MBN26AA001 -Y02 | BLL-VLV PREM RGHT FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #12 | RL, LL, L-, BR, PE | B111-016CT0001 → B111-016CT0002 → B111-016CT0003 → B111-016CT0004 → B111-996CT0021 → M0322 → D0318-L23 → M0321 → D0317-L22 → M0320 → B161-006DC0005 → B161-006DC0003 → B161-017DC0111 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MYB30GF202 -X03 (401, 402, 403, 404, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
12BUA01.FB004 | -P20 | 29 |  | PE-L1-2C4-01 | PE-L1-2C4-01 | GT#1-2-12MBN26AA501 -Y01 | DONE(10/6) | DONE | 1 | 1814 | 12BUA01.FB004-P2029 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-01 | 0.053 | 220 | D | 70 | GT PKG | 12BUA01.FB004 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L+, L- | 12MBN26AA501 -Y01 | FIL-VLV PREM RGHT FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #12 | L+, L- | B111-016CT0001 → B111-016CT0010 → B111-016CT0009 → B111-016CT0015 → B111-016CT0016 → B161-017DC0006 → B161-017DC0116 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MYB30GF202 -X03 (701, 702) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
12BUA01.HA001 | -P20 | 30 |  | PE-L1-2C4-01 | PE-L1-2C4-01 | GT#1-2-12MBN27AA501 -Y01 | DONE(10/6) | DONE | 1 | 1815 | 12BUA01.HA001-P2030 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-01 | 0.048 | 220 | D | 70 | GT PKG | 12BUA01.HA001 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L+, L- | 12MBN27AA501 -Y01 | LKG VLV PREM FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #12 | L+, L- | B111-016CT0001 → B111-016CT0010 → B111-016CT0009 → B111-016CT0015 → B111-016CT0016 → B161-017DC0006 → B161-017DC0117 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MYB30GF010 -X03 (407, 408) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
12BFA02.CB004 | -P20 | 31 | 재배정 | PE-L1-4C4-01 | PE-L1-4C4-02 | GT#1-2-12MBN60AP001 -M01 |  | DONE | 1 | 1816 | 12BFA02.CB004-P2031 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-02 | 1.1 | 400 | N | 80 | GT PKG | 12BFA02.CB004 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, L2, L3, PE | 12MBN60AP001 -M01 | DRNG PP AUX-TNK 1 FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, L2, L3, PE | B111-016CT0001 → B111-016CT0010 → B111-016CT0009 → B111-016CT0008 → B111-016CT0007 → B111-016CT0024 → B111-996CT0023 → M0323 → B161-006DC0014 → B161-016DC0105 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
12BFA03.EA003 | -P20 | 32 |  | PE-L1-4C6-01 | PE-L1-4C6-01 | GT#1-2-12MBN81AP001 -M01 |  | DONE | 1 | 1817 | 12BFA03.EA003-P2032 | 0.6/1kV CU/XLPE/LSZH | 4C x 6sqmm | PE-L1-4C6-01 | 11 | 400 | N | 80 | GT PKG | 12BFA03.EA003 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, L2, L3, PE | 12MBN81AP001 -M01 | PP FLUSH-WTR FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, L2, L3, PE | B111-016CT0001 → B111-016CT0010 → B111-016CT0009 → B111-016CT0008 → B111-016CT0007 → B111-016CT0024 → B111-996CT0023 → M0323 → B161-006DC0014 → B161-016DC0106 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 15.5
12BUA01.HA002 | -P20 | 33 | 재배정 | PE-L1-2C4-01 | PE-L1-2C4-06 | GT#1-2-12MBN82AA001 -Y01 |  | DONE | 1 | 1818 | 12BUA01.HA002-P2033 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-06 | 0.078 | 220 | D | 90 | GT PKG | 12BUA01.HA002 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L+, L- | 12MBN82AA001 -Y01 | FLUSHING WATER VALVE 1 | 1.1_MAIN BUILDING COMPLEX / GT #12 | L+, L- | B111-016CT0001 → B111-016CT0010 → B111-016CT0009 → B111-016CT0008 → B111-016CT0007 → B111-016CT0024 → B111-996CT0023 → M0323 → B161-006DC0014 → B161-017DC0135 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MBY11GF001 -X01 (401, 402) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
12BUA01.HA003 | -P20 | 34 | 재배정 | PE-L1-2C4-01 | PE-L1-2C4-06 | GT#1-2-12MBN82AA002 -Y01 |  | DONE | 1 | 1819 | 12BUA01.HA003-P2034 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-06 | 0.078 | 220 | D | 90 | GT PKG | 12BUA01.HA003 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L+, L- | 12MBN82AA002 -Y01 | FLUSHING WATER VALVE 2 | 1.1_MAIN BUILDING COMPLEX / GT #12 | L+, L- | B111-016CT0001 → B111-016CT0010 → B111-016CT0009 → B111-016CT0008 → B111-016CT0007 → B111-016CT0024 → B111-996CT0023 → M0323 → B161-006DC0014 → B161-017DC0136 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MBY11GF001 -X01 (403, 404) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
12BUB01.EA001 | -P20 | 35 |  | PE-L1-2C4-01 | PE-L1-2C4-01 | GT#1-2-12MBP13AA501 -Y01 | DONE(10/6) | DONE | 1 | 1820 | 12BUB01.EA001-P2035 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-01 | 0.205 | 220 | D | 40 | GT PKG | 12BUB01.EA001 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L+, L- | 12MBP13AA501 -Y01 | VENT-VLV MN SUP NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #12 | L+, L- | B111-016DT0001 → B111-016DT0002 → B111-016DT0012 → B111-996DT0026 → B161-017DC0137 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MBY09GF001 -X02 (401, 402) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
12BUB01.EA002 | -P20 | 36 |  | PE-L1-2C4-01 | PE-L1-2C4-01 | GT#1-2-12MBP14AA501 -Y01 | DONE(10/6) | DONE | 1 | 1821 | 12BUB01.EA002-P2036 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-01 | 0.205 | 220 | D | 40 | GT PKG | 12BUB01.EA002 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L+, L- | 12MBP14AA501 -Y01 | SOL-VLV VENTG NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #12 | L+, L- | B111-016DT0001 → B111-016DT0002 → B111-016DT0012 → B111-996DT0026 → B161-017DC0138 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MBY09GF001 -X02 (403, 404) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
12BUB01.EA003 | -P20 | 37 |  | PE-L1-2C4-01 | PE-L1-2C4-01 | GT#1-2-12MBP15AA501 -Y01 | DONE(10/6) | DONE | 1 | 1822 | 12BUB01.EA003-P2037 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-01 | 0.205 | 220 | D | 40 | GT PKG | 12BUB01.EA003 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L+, L- | 12MBP15AA501 -Y01 | VENT-VLV CLD SUP NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #12 | L+, L- | B111-016DT0001 → B111-016DT0002 → B111-016DT0012 → B111-996DT0026 → B161-017DC0139 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MBY09GF001 -X02 (405, 406) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
12BUB51.JA001 | -P20 | 38 |  | PE-L1-3C4-01 | PE-L1-3C4-01 | GT#1-2-12MBP21AA001 -E01 |  |  | 1 | 1823 | 12BUB51.JA001-P2038 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-01 | 0.008 | 220 | D | 60 | GT PKG | 12BUB51.JA001 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | X19(D3, D4), PE | 12MBP21AA001 -E01 | SO-VLV LFT DIFFU NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #12 | L, N, PE | B111-016CT0001 → B111-016CT0010 → B111-016CT0009 → B111-016CT0015 → B111-016CT0016 → B161-017DC0006 → B161-017DC0118 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MYB30GF102 -X03 (412, 413, 414) | 1 | A2F-S-25-N34 | 12 - 18 | 13
12BUB51.JA001 | -P20 | 39 |  | PE-L1-5C4-02 | PE-L1-5C4-02 | GT#1-2-12MBP21AA001 -Y02 |  |  | 1 | 1824 | 12BUB51.JA001-P2039 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-02 | 0.13 | 220 | D | 60 | GT PKG | 12BUB51.JA001 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 12MBP21AA001 -Y02 | SO-VLV LFT DIFFU NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #12 | RL, LL, L-, BR, PE | B111-016CT0001 → B111-016CT0010 → B111-016CT0009 → B111-016CT0015 → B111-016CT0016 → B161-017DC0006 → B161-017DC0119 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MYB30GF102 -X03 (408, 409, 410, 411, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
12BUB51.KB001 | -P20 | 40 |  | PE-L1-3C4-01 | PE-L1-3C4-01 | GT#1-2-12MBP21AA002 -E01 |  |  | 1 | 1825 | 12BUB51.KB001-P2040 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-01 | 0.008 | 220 | D | 60 | GT PKG | 12BUB51.KB001 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | X19(D3, D4), PE | 12MBP21AA002 -E01 | SO-VLV LFT PREM NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #12 | L, N, PE | B111-016CT0001 → B111-016CT0010 → B111-016CT0009 → B111-016CT0015 → B111-016CT0016 → B161-017DC0006 → B161-017DC0120 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MYB30GF102 -X03 (419, 420, 421) | 1 | A2F-S-25-N34 | 12 - 18 | 13
12BUB51.KB001 | -P20 | 41 |  | PE-L1-5C4-02 | PE-L1-5C4-02 | GT#1-2-12MBP21AA002 -Y02 |  |  | 1 | 1826 | 12BUB51.KB001-P2041 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-02 | 0.13 | 220 | D | 60 | GT PKG | 12BUB51.KB001 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 12MBP21AA002 -Y02 | SO-VLV LFT PREM NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #12 | RL, LL, L-, BR, PE | B111-016CT0001 → B111-016CT0010 → B111-016CT0009 → B111-016CT0015 → B111-016CT0016 → B161-017DC0006 → B161-017DC0121 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MYB30GF102 -X03 (415, 416, 417, 418, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
12BUB51.MA001 | -P20 | 42 |  | PE-L1-3C4-01 | PE-L1-3C4-01 | GT#1-2-12MBP21AA003 -E01 |  |  | 1 | 1827 | 12BUB51.MA001-P2042 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-01 | 0.008 | 220 | D | 60 | GT PKG | 12BUB51.MA001 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | X19(D3, D4), PE | 12MBP21AA003 -E01 | SO-VLV LFT PILOT NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #12 | L, N, PE | B111-016CT0001 → B111-016CT0010 → B111-016CT0009 → B111-016CT0015 → B111-016CT0016 → B161-017DC0006 → B161-017DC0122 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MYB30GF102 -X03 (426, 427, 428) | 1 | A2F-S-25-N34 | 12 - 18 | 13
12BUB51.MA001 | -P20 | 43 |  | PE-L1-5C4-02 | PE-L1-5C4-02 | GT#1-2-12MBP21AA003 -Y02 |  |  | 1 | 1828 | 12BUB51.MA001-P2043 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-02 | 0.13 | 220 | D | 60 | GT PKG | 12BUB51.MA001 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 12MBP21AA003 -Y02 | SO-VLV LFT PILOT NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #12 | RL, LL, L-, BR, PE | B111-016CT0001 → B111-016CT0010 → B111-016CT0009 → B111-016CT0015 → B111-016CT0016 → B161-017DC0006 → B161-017DC0123 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MYB30GF102 -X03 (422, 423, 424, 425, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
12BUB51.NB001 | -P20 | 44 |  | PE-L1-3C4-01 | PE-L1-3C4-01 | GT#1-2-12MBP22AA001 -E01 |  |  | 1 | 1829 | 12BUB51.NB001-P2044 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-01 | 0.008 | 220 | D | 60 | GT PKG | 12BUB51.NB001 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | X19(D3, D4), PE | 12MBP22AA001 -E01 | SO-VLV RGHT DIFFU NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #12 | L, N, PE | B111-016CT0001 → B111-016CT0010 → B111-016CT0009 → B111-016CT0015 → B111-016CT0016 → B161-017DC0006 → B161-017DC0124 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MYB30GF202 -X03 (412, 413, 414) | 1 | A2F-S-25-N34 | 12 - 18 | 13
12BUB51.NB001 | -P20 | 45 |  | PE-L1-5C4-02 | PE-L1-5C4-02 | GT#1-2-12MBP22AA001 -Y02 |  |  | 1 | 1830 | 12BUB51.NB001-P2045 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-02 | 0.13 | 220 | D | 60 | GT PKG | 12BUB51.NB001 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 12MBP22AA001 -Y02 | SO-VLV RGHT DIFFU NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #12 | RL, LL, L-, BR, PE | B111-016CT0001 → B111-016CT0010 → B111-016CT0009 → B111-016CT0015 → B111-016CT0016 → B161-017DC0006 → B161-017DC0125 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MYB30GF202 -X03 (408, 409, 410, 411, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
12BUB51.QA001 | -P20 | 46 |  | PE-L1-3C4-01 | PE-L1-3C4-01 | GT#1-2-12MBP22AA002 -E01 |  |  | 1 | 1831 | 12BUB51.QA001-P2046 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-01 | 0.008 | 220 | D | 60 | GT PKG | 12BUB51.QA001 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | X19(D3, D4), PE | 12MBP22AA002 -E01 | SO-VLV RGHT PREM NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #12 | L, N, PE | B111-016CT0001 → B111-016CT0010 → B111-016CT0009 → B111-016CT0015 → B111-016CT0016 → B161-017DC0006 → B161-017DC0126 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MYB30GF202 -X03 (419, 420, 421) | 1 | A2F-S-25-N34 | 12 - 18 | 13
12BUB51.QA001 | -P20 | 47 |  | PE-L1-5C4-02 | PE-L1-5C4-02 | GT#1-2-12MBP22AA002 -Y02 |  |  | 1 | 1832 | 12BUB51.QA001-P2047 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-02 | 0.13 | 220 | D | 60 | GT PKG | 12BUB51.QA001 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 12MBP22AA002 -Y02 | SO-VLV RGHT PREM NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #12 | RL, LL, L-, BR, PE | B111-016CT0001 → B111-016CT0010 → B111-016CT0009 → B111-016CT0015 → B111-016CT0016 → B161-017DC0006 → B161-017DC0127 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MYB30GF202 -X03 (415, 416, 417, 418, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
12BUB51.RB001 | -P20 | 48 |  | PE-L1-3C4-06 | PE-L1-3C4-06 | GT#1-2-12MBP22AA003 -E01 |  |  | 1 | 1833 | 12BUB51.RB001-P2048 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-06 | 0.008 | 220 | D | 60 | GT PKG | 12BUB51.RB001 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | X19(D3, D4), PE | 12MBP22AA003 -E01 | SO-VLV RGHT PILOT NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #12 | L, N, PE | B111-016CT0001 → B111-016CT0010 → B111-016CT0009 → B111-016CT0015 → B111-016CT0016 → B161-017DC0006 → B161-017DC0128 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MYB30GF202 -X03 (426, 427, 428) | 1 | A2F-S-25-N34 | 12 - 18 | 13
12BUB51.RB001 | -P20 | 49 |  | PE-L1-5C4-02 | PE-L1-5C4-02 | GT#1-2-12MBP22AA003 -Y02 |  |  | 1 | 1834 | 12BUB51.RB001-P2049 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-02 | 0.13 | 220 | D | 60 | GT PKG | 12BUB51.RB001 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 12MBP22AA003 -Y02 | SO-VLV RGHT PILOT NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #12 | RL, LL, L-, BR, PE | B111-016CT0001 → B111-016CT0010 → B111-016CT0009 → B111-016CT0015 → B111-016CT0016 → B161-017DC0006 → B161-017DC0129 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MYB30GF202 -X03 (422, 423, 424, 425, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
12BFA03.EA001 | -P20 | 50 | 미배정Drum 사용(10/6) | PE-L1-3C4-15 | PE-L1-3C4-15 | GT#1-2-12MBQ11AA001 -Y01 | DONE(10/6) | DONE | 1 | 1835 | 12BFA03.EA001-P2050 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 0.16 | 230 | N | 50 | GT PKG | 12BFA03.EA001 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, N, PE | 12MBQ11AA001 -Y01 | SOL-VLV 1 IGN-GAS | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, N, PE | B111-016CT0001 → B111-016CT0010 → B111-016CT0009 → B111-016CT0015 → B111-016CT0016 → B161-017DC0006 → B161-017DC0130 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MYB30GF021 -X01 (701, 702, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 13
12BFA03.EA002 | -P20 | 51 | 재배정 '미배정Drum 사용(10/6) | PE-L1-3C4-06 | PE-L1-3C4-13 | GT#1-2-12MBQ11AA002 -Y01 | DONE(10/6) | DONE | 1 | 1836 | 12BFA03.EA002-P2051 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-13 | 0.125 | 230 | N | 60 | GT PKG | 12BFA03.EA002 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, N, PE | 12MBQ11AA002 -Y01 | SOL-VLV 2 IGN-GAS | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, N, PE | B111-016CT0001 → B111-016CT0010 → B111-016CT0009 → B111-016CT0015 → B111-016CT0016 → B161-017DC0006 → B161-017DC0131 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MYB30GF021 -X01 (703, 704, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 13
12BMA52.PB001 | -P20 | 54 |  | PE-L1-4C10-01 | PE-L1-4C10-01 | GT#1-2-12MBV21AP001 -M01 | DONE(10/6) | DONE | 1 | 1837 | 12BMA52.PB001-P2054 | 0.6/1kV CU/XLPE/LSZH | 4C x 10sqmm | PE-L1-4C10-01 | 22 | 400 | E | 60 | GT PKG | 12BMA52.PB001 | GTG #12 400V AC EMERGENCY SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, L2, L3, PE | 12MBV21AP001 -M01 | LUBRICATING OIL PUMP 1 | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, L2, L3, PE | B111-016DT0025 → B111-016DT0007 → B111-016DT0008 → B111-016DT0009 → B111-016DT0010 → B111-016DT0002 → B111-016DT0012 → B111-996DT0026 → B161-016DC0107 → END |  | 1 | A2F-S-25a-N34 | 16 - 20.5 | 18
12BFA02.PB001 | -P20 | 55 |  | PE-L1-4C10-01 | PE-L1-4C10-01 | GT#1-2-12MBV21AP002 -M01 | DONE(10/6) | DONE | 1 | 1838 | 12BFA02.PB001-P2055 | 0.6/1kV CU/XLPE/LSZH | 4C x 10sqmm | PE-L1-4C10-01 | 22 | 400 | N | 60 | GT PKG | 12BFA02.PB001 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, L2, L3, PE | 12MBV21AP002 -M01 | LUBRICATING OIL PUMP 2 | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, L2, L3, PE | B111-016DT0025 → B111-016DT0007 → B111-016DT0008 → B111-016DT0009 → B111-016DT0010 → B111-016DT0002 → B111-016DT0012 → B111-996DT0026 → B161-016DC0108 → END |  | 1 | A2F-S-25a-N34 | 16 - 20.5 | 18
12BUA51.RA001 | -P20 | 56 |  | PE-L1-3C4-06 | PE-L1-3C4-06 | GT#1-2-12MBV21AP003 -E01 |  |  | 1 | 1839 | 12BUA51.RA001-P2056 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-06 | 0.1 | 220 | D | 40 | GT PKG | 12BUA51.RA001 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | X19(D03(L), D04(N)), PE | 12MBV21AP003 -E01 | EMERGENCY LUB-OIL-PP | 1.1_MAIN BUILDING COMPLEX / GT #12 | L, N, PE | B111-016DT0001 → B111-016DT0002 → B111-016DT0012 → B111-996DT0026 → B161-017DC0142 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
12BUA51.RA001 | -P20 | 57 |  | PE-L1-4C6-01 | PE-L1-4C6-01 | GT#1-2-12MBV21AP003 -M01 |  |  | 1 | 1840 | 12BUA51.RA001-P2057 | 0.6/1kV CU/XLPE/LSZH | 4C x 6sqmm | PE-L1-4C6-01 | 3.7 | 220 | D | 40 | GT PKG | 12BUA51.RA001 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | X2(1, 2, 3), PE | 12MBV21AP003 -M01 | EMERGENCY LUB-OIL-PP | 1.1_MAIN BUILDING COMPLEX / GT #12 | F1, A2, D2, PE | B111-016DT0001 → B111-016DT0002 → B111-016DT0012 → B111-996DT0026 → B161-017DC0143 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 15.5
12BUA51.RA001 | -P20 | 58 |  | PE-L1-3C95/50-01 | PE-L1-3C95/50-01 | GT#1-2-12MBV21AP003 -R01 |  |  | 1 | 1841 | 12BUA51.RA001-P2058 | 0.6/1kV CU/XLPE/LSZH | 2C x 95sqmm + 1C x 50sqmm | PE-L1-3C95/50-01 | 3.7 | 220 | D | 40 | GT PKG | 12BUA51.RA001 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | X2(1, 2), PE | 12MBV21AP003 -R01 | EMERGENCY LUB-OIL-PP | 1.1_MAIN BUILDING COMPLEX / GT #12 | 1, 2, PE | B111-016DT0001 → B111-016DT0002 → B111-016DT0012 → B111-996DT0026 → B161-017DC0144 → END |  | 1 | A2F-S-50-N1-12 | 32.1 - 40 | 34.5
12BMA51.SA001 | -P20 | 59 |  | PE-L1-4C35/25-01 | PE-L1-4C35/25-01 | GT#1-2-12MBV30AP001 -M01 |  |  | 1 | 1842 | 12BMA51.SA001-P2059 | 0.6/1kV CU/XLPE/LSZH | 3C x 35sqmm + 1C X 25sqmm | PE-L1-4C35/25-01 | 50.6 | 400 | E | 60 | GT PKG | 12BMA51.SA001 | GTG #12 400V AC EMERGENCY SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, L2, L3, PE | 12MBV30AP001 -M01 | LIFTING OIL PUMP 1 | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, L2, L3, PE | B111-016DT0025 → B111-016DT0007 → B111-016DT0008 → B111-016DT0009 → B111-016DT0010 → B111-016DT0002 → B111-016DT0012 → B111-996DT0026 → B161-016DC0111 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5
12BFA02.SA001 | -P20 | 60 |  | PE-L1-4C35/25-01 | PE-L1-4C35/25-01 | GT#1-2-12MBV30AP002 -M01 |  |  | 1 | 1843 | 12BFA02.SA001-P2060 | 0.6/1kV CU/XLPE/LSZH | 3C x 35sqmm + 1C X 25sqmm | PE-L1-4C35/25-01 | 50.6 | 400 | N | 40 | GT PKG | 12BFA02.SA001 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, L2, L3, PE | 12MBV30AP002 -M01 | LIFTING OIL PUMP 2 | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, L2, L3, PE | B111-016DT0001 → B111-016DT0002 → B111-016DT0012 → B111-996DT0026 → B161-016DC0112 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5
12BMA52.CB001 | -P20 | 61 |  | PE-L1-4C4-01 | PE-L1-4C4-01 | GT#1-2-12MBV50AN001 -M01 |  |  | 1 | 1844 | 12BMA52.CB001-P2061 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-01 | 2.2 | 400 | E | 60 | GT PKG | 12BMA52.CB001 | GTG #12 400V AC EMERGENCY SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, L2, L3, PE | 12MBV50AN001 -M01 | OIL-VAP-EXTR1 LUB-OIL-TNK | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, L2, L3, PE | B111-016DT0025 → B111-016DT0007 → B111-016DT0008 → B111-016DT0009 → B111-016DT0010 → B111-016DT0002 → B111-016DT0012 → B111-996DT0026 → B161-016DC0123 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
12BFA02.EA001 | -P20 | 62 |  | PE-L1-4C4-01 | PE-L1-4C4-01 | GT#1-2-12MBV50AN002 -M01 |  |  | 1 | 1845 | 12BFA02.EA001-P2062 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-01 | 2.2 | 400 | N | 50 | GT PKG | 12BFA02.EA001 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, L2, L3, PE | 12MBV50AN002 -M01 | OIL-VAP-EXTR2 LUB-OIL-TNK | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, L2, L3, PE | B111-016DT0001 → B111-016DT0002 → B111-016DT0012 → B111-996DT0026 → B161-016DC0121 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
12BFA02.FB001 | -P20 | 63 |  | PE-L1-4C4-01 | PE-L1-4C4-01 | GT#1-2-12MBX01AH001 -E01 |  |  | 1 | 1846 | 12BFA02.FB001-P2063 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-01 | 1 | 400 | N | 50 | GT PKG | 12BFA02.FB001 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, L2, L3, PE | 12MBX01AH001 -E01 | TNK HTG 1 HYDRC OIL | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, L2, L3, PE | B111-016DT0001 → B111-016DT0002 → B111-016DT0012 → B111-996DT0026 → B161-016DC0124 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
12BFA02.FB002 | -P20 | 64 |  | PE-L1-4C4-01 | PE-L1-4C4-01 | GT#1-2-12MBX01AH002 -E01 |  |  | 1 | 1847 | 12BFA02.FB002-P2064 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-01 | 1 | 400 | N | 50 | GT PKG | 12BFA02.FB002 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, L2, L3, PE | 12MBX01AH002 -E01 | TNK HTG 2 HYDRC OIL | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, L2, L3, PE | B111-016DT0001 → B111-016DT0002 → B111-016DT0012 → B111-996DT0026 → B161-016DC0122 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
12BFA02.HA002 | -P20 | 65 |  | PE-L1-4C4-01 | PE-L1-4C4-01 | GT#1-2-12MBX02AP001 -M01 |  |  | 1 | 1848 | 12BFA02.HA002-P2065 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-01 | 7.5 | 400 | N | 60 | GT PKG | 12BFA02.HA002 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, L2, L3, PE | 12MBX02AP001 -M01 | MN PP 1 HYDRC OIL | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, L2, L3, PE | B111-016DT0025 → B111-016DT0007 → B111-016DT0008 → B111-016DT0009 → B111-016DT0010 → B111-016DT0002 → B111-016DT0012 → B111-996DT0026 → B161-016DC0114 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
12BFA02.HA003 | -P20 | 66 |  | PE-L1-4C4-01 | PE-L1-4C4-01 | GT#1-2-12MBX02AP002 -M01 |  |  | 1 | 1849 | 12BFA02.HA003-P2066 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-01 | 7.5 | 400 | N | 60 | GT PKG | 12BFA02.HA003 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, L2, L3, PE | 12MBX02AP002 -M01 | MN PP 2 HYDRC OIL | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, L2, L3, PE | B111-016DT0025 → B111-016DT0007 → B111-016DT0008 → B111-016DT0009 → B111-016DT0010 → B111-016DT0002 → B111-016DT0012 → B111-996DT0026 → B161-016DC0115 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
12BFA02.HA001 | -P20 | 67 |  | PE-L1-4C4-01 | PE-L1-4C4-01 | GT#1-2-12MBX06AH001 -M01 |  |  | 1 | 1850 | 12BFA02.HA001-P2067 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-01 | 0.18 | 400 | N | 60 | GT PKG | 12BFA02.HA001 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, L2, L3, PE | 12MBX06AH001 -M01 | FAN COOL-CCT HYDRC OIL | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, L2, L3, PE | B111-016DT0025 → B111-016DT0007 → B111-016DT0008 → B111-016DT0009 → B111-016DT0010 → B111-016DT0002 → B111-016DT0012 → B111-996DT0026 → B161-016DC0116 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
12BFA02.JB001 | -P20 | 68 |  | PE-L1-4C16-01 | PE-L1-4C16-01 | GT#1-2-12MBY10GF002 -E01 | DONE(10/6) | DONE | 1 | 1851 | 12BFA02.JB001-P2068 | 0.6/1kV CU/XLPE/LSZH | 4C X 16sqmm | PE-L1-4C16-01 | 28 | 400 | N | 40 | GT PKG | 12BFA02.JB001 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, L2, L3, PE | 12MBY10GF002 -E01 | JUNCT BOX HTG LUB-OIL TNK | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, L2, L3, PE | B111-016DT0001 → B111-016DT0002 → B111-016DT0012 → B111-996DT0026 → B161-016DC0113 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MBY10GF002 -X01 (701, 702, 703, PE) | 1 | A2F-S-25a-N34 | 16 - 20.5 | 19.5
12BFA52.HA001 | -P20 | 69 |  | PE-L1-5C4-02 | PE-L1-5C4-02 | GT#1-2-12MBY40GH001 -E01 |  |  | 1 | 1852 | 12BFA52.HA001-P2069 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-02 | 9 | 400 | N | 90 | GT PKG | 12BFA52.HA001 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, L2, L3, N, PE | 12MBY40GH001 -E01 | JB INSTR AIR SYST | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, L2, L3, N, PE | B111-016CT0001 → B111-016CT0010 → B111-016CT0009 → B111-016CT0008 → B111-016CT0007 → B111-016CT0024 → B111-996CT0023 → M0323 → B161-006DC0012 → B161-016DC0104 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MBY40GH001 -X01 (701, 702, 703, 704, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
12BFA51.HA002 | -P20 | 70 | 미배정Drum 사용(10/6) | PE-L1-5C4-02 | PE-L1-5C4-02 | GT#1-2-12MBY80GH001 -E01 | DONE(10/6) | DONE | 1 | 1853 | 12BFA51.HA002-P2070 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-02 | 7 | 400 | N | 60 | GT PKG | 12BFA51.HA002 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, L2, L3, N, PE | 12MBY80GH001 -E01 | TRACE HEATING CABINET | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, L2, L3, N, PE | B111-016CT0001 → B111-016CT0010 → B111-016CT0009 → B111-016CT0015 → B111-016CT0016 → B161-016DC0019 → B161-016DC0102 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MBY80GH001 -X02 (L1, L2, L3, N, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
12BFA02.EA002 | -P20 | 71 |  | PE-L1-4C4-01 | PE-L1-4C4-01 | GT#1-2-12MKA10AH010 -E01 |  |  | 1 | 1854 | 12BFA02.EA002-P2071 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-01 | 3.2 | 400 | N | 40 | GT PKG | 12BFA02.EA002 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, L2, L3, PE | 12MKA10AH010 -E01 | GENERATOR SPACE HEATER | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, L2, L3, PE | B111-016DT0025 → B111-016DT0007 → B111-016DT0019 → B111-016DT0020 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
12MKC01GT002 -E01 | -P20 | 74 |  | PE-L1-1C240-02 | PE-L1-1C240-02 | GT#1-2-12MKC01GT002 -E01 |  | DONE | 1 | 1855 | 12MKC1001 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-02 | 1100 | 550 | N | 50 | GT PKG | 12MKC01GT002 -E01 | GTG #12 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1 | 12CJT21 | GTG #12 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | L1 | B161-007DC0013 → M0321 → D0318-L23 → M0322 → B111-996DT0021 → B111-016DT0004 → B111-016DT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
12MKC01GT002 -E01 | -P20 | 75 |  | PE-L1-1C240-02 | PE-L1-1C240-02 | GT#1-2 |  | DONE | 1 | 1856 | 12MKC1004 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-02 | 1100 | 550 | N | 50 | GT PKG | 12MKC01GT002 -E01 | GTG #12 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #12 | L2 | 12CJT21 | GTG #12 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | L2 | B161-007DC0013 → M0321 → D0318-L23 → M0322 → B111-996DT0021 → B111-016DT0004 → B111-016DT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
12MKC01GT002 -E01 | -P20 | 76 |  | PE-L1-1C240-02 | PE-L1-1C240-02 | GT#1-2 |  | DONE | 1 | 1857 | 12MKC1007 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-02 | 1100 | 550 | N | 50 | GT PKG | 12MKC01GT002 -E01 | GTG #12 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #12 | L3 | 12CJT21 | GTG #12 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | L3 | B161-007DC0013 → M0321 → D0318-L23 → M0322 → B111-996DT0021 → B111-016DT0004 → B111-016DT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
12MKC01GT002 -E01 | -P20 | 77 |  | PE-L1-1C240-02 | PE-L1-1C240-02 | GT#1-2 |  | DONE | 1 | 1858 | 12MKC1002 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-02 | 1100 | 550 | N | 50 | GT PKG | 12MKC01GT002 -E01 | GTG #12 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1 | 12CJT21 | GTG #12 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | L1 | B161-007DC0014 → M0321 → D0318-L23 → M0322 → B111-996DT0021 → B111-016DT0004 → B111-016DT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
12MKC01GT002 -E01 | -P20 | 78 |  | PE-L1-1C240-02 | PE-L1-1C240-02 | GT#1-2 |  | DONE | 1 | 1859 | 12MKC1005 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-02 | 1100 | 550 | N | 50 | GT PKG | 12MKC01GT002 -E01 | GTG #12 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #12 | L2 | 12CJT21 | GTG #12 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | L2 | B161-007DC0014 → M0321 → D0318-L23 → M0322 → B111-996DT0021 → B111-016DT0004 → B111-016DT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
12MKC01GT002 -E01 | -P20 | 79 |  | PE-L1-1C240-02 | PE-L1-1C240-02 | GT#1-2 |  | DONE | 1 | 1860 | 12MKC1008 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-02 | 1100 | 550 | N | 50 | GT PKG | 12MKC01GT002 -E01 | GTG #12 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #12 | L3 | 12CJT21 | GTG #12 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | L3 | B161-007DC0014 → M0321 → D0318-L23 → M0322 → B111-996DT0021 → B111-016DT0004 → B111-016DT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
12MKC01GT002 -E01 | -P20 | 82 |  | PE-L1-1C240-02 | PE-L1-1C240-02 | GT#1-2 |  | DONE | 1 | 1861 | 12MKC1003 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-02 | 1100 | 550 | N | 50 | GT PKG | 12MKC01GT002 -E01 | GTG #12 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1 | 12CJT21 | GTG #12 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | L1 | B161-007DC0015 → M0321 → D0318-L22 → M0322 → B111-996DT0021 → B111-016DT0004 → B111-016DT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
12MKC01GT002 -E01 | -P20 | 83 |  | PE-L1-1C240-02 | PE-L1-1C240-02 | GT#1-2 |  | DONE | 1 | 1862 | 12MKC1006 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-02 | 1100 | 550 | N | 50 | GT PKG | 12MKC01GT002 -E01 | GTG #12 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #12 | L2 | 12CJT21 | GTG #12 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | L2 | B161-007DC0015 → M0321 → D0318-L22 → M0322 → B111-996DT0021 → B111-016DT0004 → B111-016DT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
12MKC01GT002 -E01 | -P20 | 84 |  | PE-L1-1C240-02 | PE-L1-1C240-02 | GT#1-2 |  | DONE | 1 | 1863 | 12MKC1009 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-02 | 1100 | 550 | N | 50 | GT PKG | 12MKC01GT002 -E01 | GTG #12 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #12 | L3 | 12CJT21 | GTG #12 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | L3 | B161-007DC0015 → M0321 → D0318-L22 → M0322 → B111-996DT0021 → B111-016DT0004 → B111-016DT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
12BFA52.DA002 | -P20 | 90 | 미배정Drum 사용(9/28) | PE-L1-3C4-06 | PE-L1-3C4-06 | GT#1-2-12MKC01GW035 -E01 | DONE(9/28) 미지정Drum(PE-L1-3C4-01)사용인지 확인필요 | DONE | 1 | 1864 | 12BFA52.DA002-P2090 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-06 | 1.2 | 230 | N | 40 | GT PKG | 12BFA52.DA002 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3210) | L1, N, PE | 12MKC01GW035 -E01 | MKC 1AC AUX-VOLT SUP | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, N, PE | B111-016CT0001 → B111-016CT0002 → B111-016CT0003 → B111-016CT0004 → B111-996CT0021 → M0322 → B161-007DC0012 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
12BFA51.HA003 | -P20 | 91 | 재배정 | PE-L1-5C4-02 | PE-L1-5C4-01 | GT#1-2-12MKC05GE001 -E01 |  | DONE | 1 | 1865 | 12BFA51.HA003-P2091 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-01 | 1.15 | 400 | N | 60 | GT PKG | 12BFA51.HA003 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, L2, L3, N, PE | 12MKC05GE001 -E01 | TERBO POW-SUP SLRNGRM-VEN | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, L2, L3, N, PE | B111-016CT0001 → B111-016CT0002 → B111-016CT0003 → B111-016CT0004 → B111-996CT0021 → M0322 → D0318-L22 → M0321 → B161-007DC0012 → END | SWGR to J/B : Doosan J/B to consumer : SE 12MKC05GE001 -X0 (1, 2, 3, 4, N, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
12BFA51.DA003 | -P20 | 92 | 재배정 | PE-L1-3C4-06 | PE-L1-3C4-01 | GT#1-2-12MKC10GP001 -E01 |  | DONE | 1 | 1866 | 12BFA51.DA003-P2092 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-01 | 0.22 | 230 | N | 40 | GT PKG | 12BFA51.DA003 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, N, PE | 12MKC10GP001 -E01 | LIGHTING EXCITER HOUSING | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, N, PE | B111-016CT0001 → B111-016CT0002 → B111-016CT0003 → B111-016CT0004 → B111-996CT0021 → M0322 → B161-007DC0012 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
12CJT21 | -P20 | 93 |  | PE-L1-1C240-01 | PE-L1-1C240-01 | GT#1-2-12MKC30GE001 -E01 |  |  | 1 | 1867 | 12CJT1001 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-01 | - | 700 | D | 40 | GT PKG | 12CJT21 | GTG #12 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | L+ | 12MKC30GE001 -E01 | GEN EXCN BRSH | 1.1_MAIN BUILDING COMPLEX / GT #12 | L+ | B111-016DT0005 → B111-016DT0006 → B111-016DT0007 → B111-016DT0019 → B111-016DT0020 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 | To 단자대 Hole 확인필요
12CJT21 | -P20 | 94 |  | PE-L1-1C240-01 | PE-L1-1C240-01 | GT#1-2 |  |  | 1 | 1868 | 12CJT1002 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-01 | - | 700 | D | 40 | GT PKG | 12CJT21 | GTG #12 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | L+ | 12MKC30GE001 -E01 | GEN EXCN BRSH | 1.1_MAIN BUILDING COMPLEX / GT #12 | L+ | B111-016DT0005 → B111-016DT0006 → B111-016DT0007 → B111-016DT0019 → B111-016DT0020 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 | To 단자대 Hole 확인필요
12CJT21 | -P20 | 95 |  | PE-L1-1C240-01 | PE-L1-1C240-01 | GT#1-2 |  |  | 1 | 1869 | 12CJT1003 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-01 | - | 700 | D | 40 | GT PKG | 12CJT21 | GTG #12 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | L+ | 12MKC30GE001 -E01 | GEN EXCN BRSH | 1.1_MAIN BUILDING COMPLEX / GT #12 | L+ | B111-016DT0005 → B111-016DT0006 → B111-016DT0007 → B111-016DT0019 → B111-016DT0020 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 | To 단자대 Hole 확인필요
12CJT21 | -P20 | 96 |  | PE-L1-1C240-01 | PE-L1-1C240-01 | GT#1-2 |  |  | 1 | 1870 | 12CJT1004 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-01 | - | 700 | D | 40 | GT PKG | 12CJT21 | GTG #12 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | L+ | 12MKC30GE001 -E01 | GEN EXCN BRSH | 1.1_MAIN BUILDING COMPLEX / GT #12 | L+ | B111-016DT0005 → B111-016DT0006 → B111-016DT0007 → B111-016DT0019 → B111-016DT0020 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 | To 단자대 Hole 확인필요
12CJT21 | -P20 | 97 |  | PE-L1-1C240-01 | PE-L1-1C240-01 | GT#1-2 |  |  | 1 | 1871 | 12CJT1005 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-01 | - | 700 | D | 40 | GT PKG | 12CJT21 | GTG #12 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | L- | 12MKC30GE001 -E01 | GEN EXCN BRSH | 1.1_MAIN BUILDING COMPLEX / GT #12 | L- | B111-016DT0005 → B111-016DT0006 → B111-016DT0007 → B111-016DT0019 → B111-016DT0020 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 | To 단자대 Hole 확인필요
12CJT21 | -P20 | 98 |  | PE-L1-1C240-01 | PE-L1-1C240-01 | GT#1-2 |  |  | 1 | 1872 | 12CJT1006 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-01 | - | 700 | D | 40 | GT PKG | 12CJT21 | GTG #12 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | L- | 12MKC30GE001 -E01 | GEN EXCN BRSH | 1.1_MAIN BUILDING COMPLEX / GT #12 | L- | B111-016DT0005 → B111-016DT0006 → B111-016DT0007 → B111-016DT0019 → B111-016DT0020 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 | To 단자대 Hole 확인필요
12CJT21 | -P20 | 98 |  | PE-L1-1C240-01 | PE-L1-1C240-01 | GT#1-2 |  |  | 1 | 1873 | 12CJT1007 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-01 | - | 700 | D | 40 | GT PKG | 12CJT21 | GTG #12 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | L- | 12MKC30GE001 -E01 | GEN EXCN BRSH | 1.1_MAIN BUILDING COMPLEX / GT #12 | L- | B111-016DT0005 → B111-016DT0006 → B111-016DT0007 → B111-016DT0019 → B111-016DT0020 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 | To 단자대 Hole 확인필요
12CJT21 | -P20 | 98 |  | PE-L1-1C240-01 | PE-L1-1C240-01 | GT#1-2 |  |  | 1 | 1874 | 12CJT1008 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-01 | - | 700 | D | 40 | GT PKG | 12CJT21 | GTG #12 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #12(UBA3310) | L- | 12MKC30GE001 -E01 | GEN EXCN BRSH | 1.1_MAIN BUILDING COMPLEX / GT #12 | L- | B111-016DT0005 → B111-016DT0006 → B111-016DT0007 → B111-016DT0019 → B111-016DT0020 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 | To 단자대 Hole 확인필요
12BUA51.DA001 | -P20 | 99 |  | PE-L1-2C4-06 | PE-L1-2C4-06 | GT#1-2-12MPB10GW011 -E01 |  | DONE | 1 | 1875 | 12BUA51.DA001-P2099 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-06 | 1 | 220 | D | 120 | GT PKG | 12BUA51.DA001 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L+, L- | 12MPB10GW011 -E01 | GAS-TURB ENCL EMERG LITG | 1.1_MAIN BUILDING COMPLEX / GT #12 | L+, L- | B111-016CT0001 → B111-016CT0002 → B111-016CT0003 → B111-016CT0004 → B111-996CT0021 → M0322 → D0318-L23 → M0321 → D0317-L22 → M0320 → B161-006DC0005 → B161-006DC0003 → B161-017DC0101 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
12BFA51.DA004 | -P2 | 100 |  | PE-L1-3C4-18 | PE-L1-3C4-18 | GT#1-2-12MPB10GW023 -E01 |  | DONE | 1 | 1876 | 12BFA51.DA004-P2100 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-18 | 1 | 230 | N | 120 | GT PKG | 12BFA51.DA004 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, N, PE | 12MPB10GW023 -E01 | GAS-TURB ENCL LITG | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, N, PE | B111-016CT0001 → B111-016CT0002 → B111-016CT0003 → B111-016CT0004 → B111-996CT0021 → M0322 → D0318-L23 → M0321 → D0317-L22 → M0320 → B161-006DC0005 → B161-006DC0003 → B161-017DC0102 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
12BUA51.DA002 | -P2 | 101 |  | PE-L1-2C4-06 | PE-L1-2C4-06 | GT#1-2-12MPB13GW011 -E01 | DONE(10/6) | DONE | 1 | 1877 | 12BUA51.DA002-P2101 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-06 | 0.22 | 220 | D | 40 | GT PKG | 12BUA51.DA002 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L+, L- | 12MPB13GW011 -E01 | FGS ENCL EMERG LITG | 1.1_MAIN BUILDING COMPLEX / GT #12 | L+, L- | B111-016DT0025 → B111-996DT0022 → M0323 → B161-006DC0021 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
12BFA51.DA005 | -P2 | 102 | 재배정 | PE-L1-3C4-06 | PE-L1-3C4-14 | GT#1-2-12MPB13GW023 -E01 |  |  | 1 | 1878 | 12BFA51.DA005-P2102 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-14 | 1 | 230 | N | 40 | GT PKG | 12BFA51.DA005 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, N, PE | 12MPB13GW023 -E01 | FGS ENCL LITG | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, N, PE | B111-016DT0025 → B111-996DT0022 → M0323 → B161-006DC0020 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
12BUA51.DA003 | -P2 | 103 |  | PE-L1-2C4-06 | PE-L1-2C4-06 | GT#1-2-12MPB16GW011 -E01 | DONE(10/6) | DONE | 1 | 1879 | 12BUA51.DA003-P2103 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-06 | 0.44 | 220 | D | 30 | GT PKG | 12BUA51.DA003 | GTG #12 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L+, L- | 12MPB16GW011 -E01 | IMS + GEN ENCL EMERG LITG | 1.1_MAIN BUILDING COMPLEX / GT #12 | L+, L- | B111-016CT0001 → B111-016CT0010 → B111-016CT0009 → B111-016CT0015 → B111-016CT0016 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
12BFA51.DA006 | -P2 | 104 | 재배정 '미배정Drum 사용(10/6) | PE-L1-3C4-06 | PE-L1-3C4-14 | GT#1-2-12MPB16GW023 -E01 | DONE(10/6) | DONE | 1 | 1880 | 12BFA51.DA006-P2104 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-14 | 1 | 230 | N | 30 | GT PKG | 12BFA51.DA006 | GTG #12 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, N, PE | 12MPB16GW023 -E01 | IMS + GEN ENCL LITG | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, N, PE | B111-016CT0001 → B111-016CT0010 → B111-016CT0009 → B111-016CT0015 → B111-016CT0016 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
12BMA51.CB001 | -P2 | 105 |  | PE-L1-4C4-01 | PE-L1-4C4-01 | GT#1-2-12SAM33AN001 -M01 |  |  | 1 | 1881 | 12BMA51.CB001-P2105 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-01 | 0.55 | 400 | E | 60 | GT PKG | 12BMA51.CB001 | GTG #12 400V AC EMERGENCY SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, L2, L3, PE | 12SAM33AN001 -M01 | EXH-AIR FAN FU-GAS ENCL | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, L2, L3, PE | B111-016DT0025 → B111-016DT0007 → B111-016DT0008 → B111-016DT0009 → B111-016DT0010 → B111-016DT0002 → B111-016DT0012 → B111-996DT0026 → B161-016DC0109 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
12BFA02.FB001 | -P2 | 106 |  | PE-L1-4C4-01 | PE-L1-4C4-01 | GT#1-2-12SAM33AN002 -M01 |  |  | 1 | 1882 | 12BFA02.FB001-P2106 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-01 | 0.55 | 400 | N | 60 | GT PKG | 12BMA51.CB003 | GTG #12 400V AC EMERGENCY SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #12 | L1, L2, L3, PE | 12SAM33AN002 -M01 | EXH-AIR FAN FU-GAS ENCL | 1.1_MAIN BUILDING COMPLEX / GT #12 | L1, L2, L3, PE | B111-016DT0025 → B111-016DT0007 → B111-016DT0008 → B111-016DT0009 → B111-016DT0010 → B111-016DT0002 → B111-016DT0012 → B111-996DT0026 → B161-016DC0110 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
21BFA51.DA001 | -P20 | 01 |  | PE-L1-3C4-22 | PE-L1-3C4-22 | GT#2-1-21BAB11GW023 -E01 |  |  | 1 | 1883 | 21BFA51.DA001-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-22 | 0.15 | 230 | N | 30 | GT PKG | 21BFA51.DA001 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, N, PE | 21BAB11GW023 -E01 | GEN NEUT GND CAB | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, N, PE | B212-016AT0011 → B212-016AT0010 → B212-016AT0009 → B212-016AT0015 → B212-016AT0016 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
21BFA03.CB001 | -P20 | 02 |  | PE-L1-3C4-22 | PE-L1-3C4-22 | GT#2-1-21MBA18AA001 -Y01 |  |  | 1 | 1884 | 21BFA03.CB001-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-22 | 0.073 | 230 | N | 120 | GT PKG | 21BFA03.CB001 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, N, PE | 21MBA18AA001 -Y01 | DRN-VLV 1 FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, N, PE | B212-016AT0011 → B212-996AT0023 → M0309 → D0322-L31 → M0308 → D0306-L31 → M0307 → D0321-L27 → M0306 → B261-006DC0004 → B261-007DC0001 → B261-006DC0023 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MYB17GF010 -X01 (701, 702, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 13
21BFA03.CB002 | -P20 | 03 |  | PE-L1-3C4-22 | PE-L1-3C4-22 | GT#2-1-21MBA18AA002 -Y01 |  |  | 1 | 1885 | 21BFA03.CB002-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-22 | 0.073 | 230 | N | 120 | GT PKG | 21BFA03.CB002 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, N, PE | 21MBA18AA002 -Y01 | DRN-VLV 2 FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, N, PE | B212-016AT0011 → B212-996AT0023 → M0309 → D0322-L31 → M0308 → D0306-L31 → M0307 → D0321-L27 → M0306 → B261-006DC0004 → B261-007DC0001 → B261-006DC0023 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MYB17GF010 -X01 (703, 704, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 13
21BFA03.CB003 | -P20 | 04 |  | PE-L1-3C4-22 | PE-L1-3C4-22 | GT#2-1-21MBA18AA003 -Y01 |  |  | 1 | 1886 | 21BFA03.CB003-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-22 | 0.073 | 230 | N | 120 | GT PKG | 21BFA03.CB003 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, N, PE | 21MBA18AA003 -Y01 | DRN-VLV 3 FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, N, PE | B212-016AT0011 → B212-996AT0023 → M0309 → D0322-L31 → M0308 → D0306-L31 → M0307 → D0321-L27 → M0306 → B261-006DC0004 → B261-007DC0001 → B261-006DC0023 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MYB17GF010 -X01 (705, 706, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 13
21BFA02.CB001 | -P20 | 05 |  | PE-L1-4C4-23 | PE-L1-4C4-23 | GT#2-1-21MBA30AP001 -M01 |  |  | 1 | 1887 | 21BFA02.CB001-P2005 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-23 | 4.9 | 400 | N | 120 | GT PKG | 21BFA02.CB001 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, L2, L3, PE | 21MBA30AP001 -M01 | MXG-PP | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, L2, L3, PE | B212-016AT0011 → B212-996AT0023 → M0309 → D0322-L31 → M0308 → D0306-L31 → M0307 → D0321-L27 → M0306 → B261-006DC0002 → B261-017DC0112 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
21BFA02.EA003 | -P20 | 06 |  | PE-L1-3C4-22 | PE-L1-3C4-22 | GT#2-1-21MBA32AP001 -M01 |  |  | 1 | 1888 | 21BFA02.EA003-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-22 | 0.5 | 230 | N | 120 | GT PKG | 21BFA02.EA003 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, N, PE | 21MBA32AP001 -M01 | CLNG-AGT-PP | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, N, PE | B212-016AT0011 → B212-996AT0023 → M0309 → D0322-L31 → M0308 → D0306-L31 → M0307 → D0321-L27 → M0306 → B261-006DC0002 → B261-017DC0113 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
21BFA53.DA002 | -P20 | 07 |  | PE-L1-3C4-22 | PE-L1-3C4-22 | GT#2-1-21MBA32GQ012 -X01 |  |  | 1 | 1889 | 21BFA53.DA002-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-22 | 0.5 | 230 | N | 120 | GT PKG | 21BFA53.DA002 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, N, PE | 21MBA32GQ012 -X01 | EL-SCKT JUNCT-BOX | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, N, PE | B212-016AT0011 → B212-996AT0023 → M0309 → D0322-L31 → M0308 → D0306-L31 → M0307 → D0321-L27 → M0306 → B261-006DC0002 → B261-017DC0114 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
21BFA02.EA004 | -P20 | 08 |  | PE-L1-3C4-22 | PE-L1-3C4-22 | GT#2-1-21MBA33AP001 -M01 |  |  | 1 | 1890 | 21BFA02.EA004-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-22 | 0.5 | 230 | N | 120 | GT PKG | 21BFA02.EA004 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, N, PE | 21MBA33AP001 -M01 | ANTIFRZ-AGT-PP | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, N, PE | B212-016AT0011 → B212-996AT0023 → M0309 → D0322-L23 → M0308 → D0306-L31 → M0307 → D0321-L27 → M0306 → B261-006DC0002 → B261-017DC0115 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
21BFA02.CB002 | -P20 | 09 |  | PE-L1-4C4-23 | PE-L1-4C4-23 | GT#2-1-21MBA51AP001 -M01 |  |  | 1 | 1891 | 21BFA02.CB002-P2009 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-23 | 2.2 | 400 | N | 50 | GT PKG | 21BFA02.CB002 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, L2, L3, PE | 21MBA51AP001 -M01 | HYDRC-PP 1 HCO | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, L2, L3, PE | B212-016BT0001 → B212-016BT0002 → B212-016BT0012 → B212-996BT0026 → B261-016DC0117 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
21BFA02.CB003 | -P20 | 10 |  | PE-L1-4C4-23 | PE-L1-4C4-23 | GT#2-1-21MBA51AP002 -M01 |  |  | 1 | 1892 | 21BFA02.CB003-P2010 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-23 | 2.2 | 400 | N | 50 | GT PKG | 21BFA02.CB003 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, L2, L3, PE | 21MBA51AP002 -M01 | HYDRC-PP 2 HCO | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, L2, L3, PE | B212-016BT0001 → B212-016BT0002 → B212-016BT0012 → B212-996BT0026 → B261-016DC0118 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
21CJT91 (21MBJ01GS091 -E01) | -P10 | 01 |  | PE-M3-1C240-02 | PE-M1-1C240-09 | GT#2-1-21MBJ01GS091 -E01 |  |  | 1 | 1893 | 21CJT0001 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-09 |  | 1400 | N | 60 | GT PKG | 21CJT91 (21MBJ01GS091 -E01) | GTG #21 SFC CABINET (GTG #21 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | U1 | B2-CB-11301 | BLOCK #2 GENERATOR CIRCUIT BREAKER FOR GT#1 | 1.1_MAIN BUILDING COMPLEX / GT #21 | U1 | B261-013DC0001 → B261-003DC0007 → M0307 → D0306-M11 → M0308 → D0322-M11 → M0309 → B212-993AT0022 → B212-013AT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
21CJT91 (21MBJ01GS091 -E01) | -P10 | 02 |  | PE-M3-1C240-03 | PE-M1-1C240-10 | GT#2-1 |  |  | 1 | 1894 | 21CJT0004 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-10 |  | 1400 | N | 60 | GT PKG | 21CJT91 (21MBJ01GS091 -E01) | GTG #21 SFC CABINET (GTG #21 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | V1 | B2-CB-11301 | BLOCK #2 GENERATOR CIRCUIT BREAKER FOR GT#1 | 1.1_MAIN BUILDING COMPLEX / GT #21 | V1 | B261-013DC0001 → B261-003DC0007 → M0307 → D0306-M11 → M0308 → D0322-M11 → M0309 → B212-993AT0022 → B212-013AT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
21CJT91 (21MBJ01GS091 -E01) | -P10 | 03 |  | PE-M3-1C240-03 | PE-M1-1C240-10 | GT#2-1 |  |  | 1 | 1895 | 21CJT0007 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-10 |  | 1400 | N | 60 | GT PKG | 21CJT91 (21MBJ01GS091 -E01) | GTG #21 SFC CABINET (GTG #21 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | W1 | B2-CB-11301 | BLOCK #2 GENERATOR CIRCUIT BREAKER FOR GT#1 | 1.1_MAIN BUILDING COMPLEX / GT #21 | W1 | B261-013DC0001 → B261-003DC0007 → M0307 → D0306-M11 → M0308 → D0322-M11 → M0309 → B212-993AT0022 → B212-013AT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
21CJT91 (21MBJ01GS091 -E01) | -P10 | 04 |  | PE-M3-1C240-03 | PE-M1-1C240-10 | GT#2-1 |  |  | 1 | 1896 | 21CJT0002 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-10 |  | 1400 | N | 60 | GT PKG | 21CJT91 (21MBJ01GS091 -E01) | GTG #21 SFC CABINET (GTG #21 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | U1 | B2-CB-11301 | BLOCK #2 GENERATOR CIRCUIT BREAKER FOR GT#1 | 1.1_MAIN BUILDING COMPLEX / GT #21 | U1 | B261-013DC0002 → B261-003DC0008 → M0307 → D0306-M12 → M0308 → D0322-M12 → M0309 → B212-993AT0022 → B212-013AT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
21CJT91 (21MBJ01GS091 -E01) | -P10 | 05 |  | PE-M3-1C240-03 | PE-M1-1C240-11 | GT#2-1 |  |  | 1 | 1897 | 21CJT0005 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-11 |  | 1400 | N | 60 | GT PKG | 21CJT91 (21MBJ01GS091 -E01) | GTG #21 SFC CABINET (GTG #21 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | V1 | B2-CB-11301 | BLOCK #2 GENERATOR CIRCUIT BREAKER FOR GT#1 | 1.1_MAIN BUILDING COMPLEX / GT #21 | V1 | B261-013DC0002 → B261-003DC0008 → M0307 → D0306-M12 → M0308 → D0322-M12 → M0309 → B212-993AT0022 → B212-013AT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
21CJT91 (21MBJ01GS091 -E01) | -P10 | 06 |  | PE-M3-1C240-03 | PE-M1-1C240-11 | GT#2-1 |  |  | 1 | 1898 | 21CJT0008 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-11 |  | 1400 | N | 60 | GT PKG | 21CJT91 (21MBJ01GS091 -E01) | GTG #21 SFC CABINET (GTG #21 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | W1 | B2-CB-11301 | BLOCK #2 GENERATOR CIRCUIT BREAKER FOR GT#1 | 1.1_MAIN BUILDING COMPLEX / GT #21 | W1 | B261-013DC0002 → B261-003DC0008 → M0307 → D0306-M12 → M0308 → D0322-M12 → M0309 → B212-993AT0022 → B212-013AT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
21CJT91 (21MBJ01GS091 -E01) | -P10 | 07 |  | PE-M3-1C240-03 | PE-M1-1C240-11 | GT#2-1 |  |  | 1 | 1899 | 21CJT0003 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-11 |  | 1400 | N | 60 | GT PKG | 21CJT91 (21MBJ01GS091 -E01) | GTG #21 SFC CABINET (GTG #21 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | U1 | B2-CB-11301 | BLOCK #2 GENERATOR CIRCUIT BREAKER FOR GT#1 | 1.1_MAIN BUILDING COMPLEX / GT #21 | U1 | B261-013DC0003 → B261-003DC0009 → M0307 → D0306-M13 → M0308 → D0322-M13 → M0309 → B212-993AT0022 → B212-013AT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
21CJT91 (21MBJ01GS091 -E01) | -P10 | 08 |  | PE-M3-1C240-03 | PE-M1-1C240-11 | GT#2-1 |  |  | 1 | 1900 | 21CJT0006 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-11 |  | 1400 | N | 60 | GT PKG | 21CJT91 (21MBJ01GS091 -E01) | GTG #21 SFC CABINET (GTG #21 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | V1 | B2-CB-11301 | BLOCK #2 GENERATOR CIRCUIT BREAKER FOR GT#1 | 1.1_MAIN BUILDING COMPLEX / GT #21 | V1 | B261-013DC0003 → B261-003DC0009 → M0307 → D0306-M13 → M0308 → D0322-M13 → M0309 → B212-993AT0022 → B212-013AT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
21CJT91 (21MBJ01GS091 -E01) | -P10 | 09 |  | PE-M3-1C240-03 | PE-M1-1C240-11 | GT#2-1 |  |  | 1 | 1901 | 21CJT0009 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-11 |  | 1400 | N | 60 | GT PKG | 21CJT91 (21MBJ01GS091 -E01) | GTG #21 SFC CABINET (GTG #21 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | W1 | B2-CB-11301 | BLOCK #2 GENERATOR CIRCUIT BREAKER FOR GT#1 | 1.1_MAIN BUILDING COMPLEX / GT #21 | W1 | B261-013DC0003 → B261-003DC0009 → M0307 → D0306-M13 → M0308 → D0322-M13 → M0309 → B212-993AT0022 → B212-013AT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
21MBJ01GT002 -E01 | -P10 | 01 |  | PE-M3-1C240-04 | PE-M1-1C240-12 | GT#2-1-21MBJ01GT002 -E01 |  |  | 1 | 1902 | 21MBJ0001 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-12 |  | 1400 | N | 35 | GT PKG | 21MBJ01GT002 -E01 | GTG #21 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #21 | U1 | 21CJT91 | GTG #21 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | U1 | B261-003DC0003 → M0308 → B212-993AT0021 → B212-013AT0004 → B212-013AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
21MBJ01GT002 -E01 | -P10 | 02 |  | PE-M3-1C240-04 | PE-M1-1C240-12 | GT#2-1 |  |  | 1 | 1903 | 21MBJ0004 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-12 |  | 1400 | N | 35 | GT PKG | 21MBJ01GT002 -E01 | GTG #21 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #21 | V1 | 21CJT91 | GTG #21 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | V1 | B261-003DC0003 → M0308 → B212-993AT0021 → B212-013AT0004 → B212-013AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
21MBJ01GT002 -E01 | -P10 | 03 |  | PE-M3-1C240-04 | PE-M1-1C240-12 | GT#2-1 |  |  | 1 | 1904 | 21MBJ0007 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-12 |  | 1400 | N | 35 | GT PKG | 21MBJ01GT002 -E01 | GTG #21 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #21 | W1 | 21CJT91 | GTG #21 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | W1 | B261-003DC0003 → M0308 → B212-993AT0021 → B212-013AT0004 → B212-013AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
21MBJ01GT002 -E01 | -P10 | 04 |  | PE-M3-1C240-05 | PE-M1-1C240-12 | GT#2-1 |  |  | 1 | 1905 | 21MBJ0002 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-12 |  | 1400 | N | 35 | GT PKG | 21MBJ01GT002 -E01 | GTG #21 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #21 | U1 | 21CJT91 | GTG #21 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | U1 | B261-003DC0004 → M0308 → B212-993AT0021 → B212-013AT0004 → B212-013AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
21MBJ01GT002 -E01 | -P10 | 05 |  | PE-M3-1C240-05 | PE-M1-1C240-13 | GT#2-1 |  |  | 1 | 1906 | 21MBJ0005 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-13 |  | 1400 | N | 35 | GT PKG | 21MBJ01GT002 -E01 | GTG #21 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #21 | V1 | 21CJT91 | GTG #21 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | V1 | B261-003DC0004 → M0308 → B212-993AT0021 → B212-013AT0004 → B212-013AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
21MBJ01GT002 -E01 | -P10 | 06 |  | PE-M3-1C240-05 | PE-M1-1C240-13 | GT#2-1 |  |  | 1 | 1907 | 21MBJ0008 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-13 |  | 1400 | N | 35 | GT PKG | 21MBJ01GT002 -E01 | GTG #21 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #21 | W1 | 21CJT91 | GTG #21 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | W1 | B261-003DC0004 → M0308 → B212-993AT0021 → B212-013AT0004 → B212-013AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
21MBJ01GT002 -E01 | -P10 | 07 |  | PE-M3-1C240-05 | PE-M1-1C240-13 | GT#2-1 |  |  | 1 | 1908 | 21MBJ0003 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-13 |  | 1400 | N | 35 | GT PKG | 21MBJ01GT002 -E01 | GTG #21 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #21 | U1 | 21CJT91 | GTG #21 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | U1 | B261-003DC0005 → M0308 → B212-993AT0021 → B212-013AT0004 → B212-013AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
21MBJ01GT002 -E01 | -P10 | 08 |  | PE-M3-1C240-05 | PE-M1-1C240-13 | GT#2-1 |  |  | 1 | 1909 | 21MBJ0006 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-13 |  | 1400 | N | 35 | GT PKG | 21MBJ01GT002 -E01 | GTG #21 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #21 | V1 | 21CJT91 | GTG #21 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | V1 | B261-003DC0005 → M0308 → B212-993AT0021 → B212-013AT0004 → B212-013AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
21MBJ01GT002 -E01 | -P10 | 09 |  | PE-M3-1C240-05 | PE-M1-1C240-13 | GT#2-1 |  |  | 1 | 1910 | 21MBJ0009 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-13 |  | 1400 | N | 35 | GT PKG | 21MBJ01GT002 -E01 | GTG #21 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #21 | W1 | 21CJT91 | GTG #21 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | W1 | B261-003DC0005 → M0308 → B212-993AT0021 → B212-013AT0004 → B212-013AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
21BFA52.DA001 | -P20 | 11 |  | PE-L1-3C4-22 | PE-L1-3C4-22 | GT#2-1-21MBJ01GW035 -E01 |  |  | 1 | 1911 | 21BFA52.DA001-P2011 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-22 | 1.2 | 230 | N | 40 | GT PKG | 21BFA52.DA001 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, N, PE | 21MBJ01GW035 -E01 | MBJ 1AC AUX-VOLT SUP | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, N, PE | B212-016AT0011 → B212-996AT0023 → M0309 → D0322-L23 → M0308 → B261-007DC0010 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
21BFA53.HA002 | -P20 | 12 |  | PE-L1-5C6-02 | PE-L1-5C6-02 | GT#2-1-21MBL10GH001 -E01 |  |  | 1 | 1912 | 21BFA53.HA002-P2012 | 0.6/1kV CU/XLPE/LSZH | 5C x 6sqmm | PE-L1-5C6-02 | 15 | 400 | N | 200 | GT PKG | 21BFA53.HA002 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, L2, L3, N, PE | 21MBL10GH001 -E01 | CABINET AIR INTAKE | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, L2, L3, N, PE | B212-016AT0011 → B212-996AT0023 → M0309 → D0322-L23 → M0308 → D0306-L31 → M0307 → D0321-L27 → M0306 → D0305-L27 → M0303 → B261-006BC0025 → B261-026EC0006 → B261-026EC0005 → B261-026EC0002 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MBL10GH001 -X01 (001, 002, 003, 004, 005) | 1 | A2F-S-25a-N34 | 16 - 20.5 | 17
21BFA53.HA003 | -P20 | 13 |  | PE-L1-5C6-02 | PE-L1-5C6-02 | GT#2-1-21MBL20GH001 -E01 |  |  | 1 | 1913 | 21BFA53.HA003-P2013 | 0.6/1kV CU/XLPE/LSZH | 5C x 6sqmm | PE-L1-5C6-02 | 11 | 400 | N | 120 | GT PKG | 21BFA53.HA003 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, L2, L3, N, PE | 21MBL20GH001 -E01 | CAB AIR-INTK-FLP | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, L2, L3, N, PE | B212-016AT0011 → B212-996AT0023 → M0309 → D0322-L25 → M0308 → D0306-L25 → M0307 → D0321-L32 → M0306 → B261-006DC0004 → B261-016DC0101 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MBL20GH001 -X01 (001, 002, 003, 004, 005) | 1 | A2F-S-25a-N34 | 16 - 20.5 | 17
21BFA51.HA001 | -P20 | 14 |  | PE-L1-5C4-04 | PE-L1-5C4-04 | GT#2-1-21MBL25AT001 -E01 |  |  | 1 | 1914 | 21BFA51.HA001-P2014 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-04 | 5.2 | 400 | N | 110 | GT PKG | 21BFA51.HA001 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, L2, L3, N, PE | 21MBL25AT001 -E01 | STANDSTL AIR DEHUMI | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, L2, L3, N, PE | B212-016AT0011 → B212-996AT0023 → M0309 → D0322-L25 → M0308 → D0306-L25 → M0307 → D0321-L32 → M0306 → B261-006DC0005 → B261-007DC0001 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 15
21BFA03.JB001 | -P20 | 15 |  | PE-L1-5C25/16-02 | PE-L1-5C25/16-02 | GT#2-1-21MBL30GH001 -E01 |  |  | 1 | 1915 | 21BFA03.JB001-P2015 | 0.6/1kV CU/XLPE/LSZH | 4C x 25sqmm + 1C X 16sqmm | PE-L1-5C25/16-02 | 40 | 400 | N | 85 | GT PKG | 21BFA03.JB001 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, L2, L3, N, PE | 21MBL30GH001 -E01 | CAB PULS-AIR | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, L2, L3, N, PE | B212-016AT0011 → B212-996AT0023 → M0309 → D0322-L23 → M0308 → D0306-L21 → M0307 → D0321-L27 → M0306 → B261-006DC0007 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MBL30GH001 -X01 (001, 002, 003, 004, 005) | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5
21BFA53.HA004 | -P20 | 16 |  | PE-L1-5C6-02 | PE-L1-5C6-02 | GT#2-1-21MBL40GH001 -E01 |  |  | 1 | 1916 | 21BFA53.HA004-P2016 | 0.6/1kV CU/XLPE/LSZH | 5C x 6sqmm | PE-L1-5C6-02 | 18 | 400 | N | 110 | GT PKG | 21BFA53.HA004 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, L2, L3, N, PE | 21MBL40GH001 -E01 | CAB EVAP COOL | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, L2, L3, N, PE | B212-016AT0011 → B212-996AT0023 → M0309 → D0322-L25 → M0308 → D0306-L25 → M0307 → D0321-L32 → M0306 → B261-006DC0006 → B261-016DC0103 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MBL40GH001 -X01 (001, 002, 003, 004, 005) | 1 | A2F-S-25a-N34 | 16 - 20.5 | 17
21BFA03.CB004 | -P20 | 17 |  | PE-L1-3C4-23 | PE-L1-3C4-23 | GT#2-1-21MBM12GT100 -E01 |  |  | 1 | 1917 | 21BFA03.CB004-P2017 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-23 | 1.6 | 230 | N | 120 | GT PKG | 21BFA03.CB004 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, N, PE | 21MBM12GT100 -E01 | IGNITION TRANSFORMERS | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, N, PE | B212-016AT0011 → B212-996AT0023 → M0309 → D0322-L24 → M0308 → D0306-L24 → M0307 → D0321-L22 → M0306 → B261-006DC0005 → B261-006DC0003 → B261-017DC0103 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MYB30GF202 -X03 | 1 | A2F-S-25-N34 | 12 - 18 | 13
21BUA01.EA001 | -P20 | 18 |  | PE-L1-2C4-07 | PE-L1-2C4-07 | GT#2-1-21MBN12AA505 -Y01 |  |  | 1 | 1918 | 21BUA01.EA001-P2018 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-07 | 0.055 | 220 | D | 70 | GT PKG | 21BUA01.EA001 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L+, L- | 21MBN12AA505 -Y01 | RL-VLV FEED FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #21 | L+, L- | B212-016AT0011 → B212-996AT0023 → M0309 → B261-006DC0014 → B261-017DC0132 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MBY08GF001 -X04 (401, 402) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
21BUA01.EA002 | -P20 | 19 |  | PE-L1-2C4-07 | PE-L1-2C4-07 | GT#2-1-21MBN13AA501 -Y01 |  |  | 1 | 1919 | 21BUA01.EA002-P2019 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-07 | 0.048 | 220 | D | 60 | GT PKG | 21BUA01.EA002 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L+, L- | 21MBN13AA501 -Y01 | STOP-VLV FUEL OIL SUPPLY | 1.1_MAIN BUILDING COMPLEX / GT #21 | L+, L- | B212-016AT0011 → B212-996AT0023 → M0309 → B261-006DC0014 → B261-017DC0133 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MYB30GF010 -X03 (403, 404) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
21BUA01.EA003 | -P20 | 20 |  | PE-L1-2C4-07 | PE-L1-2C4-07 | GT#2-1-21MBN13AA502 -Y01 |  |  | 1 | 1920 | 21BUA01.EA003-P2020 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-07 | 0.048 | 220 | D | 60 | GT PKG | 21BUA01.EA003 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L+, L- | 21MBN13AA502 -Y01 | RL-VLV RETN DIFFU FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #21 | L+, L- | B212-016AT0011 → B212-996AT0023 → M0309 → B261-006DC0014 → B261-017DC0134 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MYB30GF010 -X03 (401, 402) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
21BUA51.JA001 | -P20 | 21 |  | PE-L1-5C4-03 | PE-L1-5C4-03 | GT#2-1-21MBN21AA001 -Y02 |  |  | 1 | 1921 | 21BUA51.JA001-P2021 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-03 | 0.13 | 220 | D | 120 | GT PKG | 21BUA51.JA001 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 21MBN21AA001 -Y02 | BLL-VLV ASSY LFT FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #21 | RL, LL, L-, BR, PE | B212-016AT0011 → B212-996AT0023 → M0309 → D0322-L24 → M0308 → D0306-L24 → M0307 → D0321-L22 → M0306 → B261-006DC0005 → B261-006DC0003 → B261-017DC0104 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 15
21BUA01.EA004 | -P20 | 22 |  | PE-L1-2C4-07 | PE-L1-2C4-07 | GT#2-1-21MBN21AA002 -Y01 |  |  | 1 | 1922 | 21BUA01.EA004-P2022 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-07 | 0.048 | 220 | D | 120 | GT PKG | 21BUA01.EA004 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L+, L- | 21MBN21AA002 -Y01 | BYP-VLV LFT FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #21 | L+, L- | B212-016AT0011 → B212-996AT0023 → M0309 → D0322-L24 → M0308 → D0306-L24 → M0307 → D0321-L22 → M0306 → B261-006DC0005 → B261-006DC0003 → B261-017DC0105 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MYB30GF102 -X03 (429, 430) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
21BUA51.KB001 | -P20 | 23 |  | PE-L1-5C4-03 | PE-L1-5C4-03 | GT#2-1-21MBN22AA001 -Y02 |  |  | 1 | 1923 | 21BUA51.KB001-P2023 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-03 | 0.13 | 220 | D | 120 | GT PKG | 21BUA51.KB001 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 21MBN22AA001 -Y02 | BLL-VLV ASSY RGHT FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #21 | RL, LL, L-, BR, PE | B212-016AT0011 → B212-996AT0023 → M0309 → D0322-L24 → M0308 → D0306-L24 → M0307 → D0321-L22 → M0306 → B261-006DC0005 → B261-006DC0003 → B261-017DC0106 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 15
21BUA01.FB001 | -P20 | 24 |  | PE-L1-2C4-07 | PE-L1-2C4-07 | GT#2-1-21MBN22AA002 -Y01 |  |  | 1 | 1924 | 21BUA01.FB001-P2024 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-07 | 0.048 | 220 | D | 120 | GT PKG | 21BUA01.FB001 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L+, L- | 21MBN22AA002 -Y01 | BYP-VLV RGHT FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #21 | L+, L- | B212-016AT0011 → B212-996AT0023 → M0309 → D0322-L24 → M0308 → D0306-L24 → M0307 → D0321-L22 → M0306 → B261-006DC0005 → B261-006DC0003 → B261-017DC0107 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MYB30GF202 -X03 (429, 430) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
21BUA01.FB002 | -P20 | 25 |  | PE-L1-2C4-07 | PE-L1-2C4-07 | GT#2-1-21MBN23AA501 -Y01 |  |  | 1 | 1925 | 21BUA01.FB002-P2025 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-07 | 0.048 | 220 | D | 120 | GT PKG | 21BUA01.FB002 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L+, L- | 21MBN23AA501 -Y01 | DRN-VLV FEED PREM FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #21 | L+, L- | B212-016AT0011 → B212-996AT0023 → M0309 → D0322-L24 → M0308 → D0306-L24 → M0307 → D0321-L22 → M0306 → B261-006DC0005 → B261-006DC0003 → B261-017DC0108 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MYB30GF010 -X03 (405, 406) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
21BUA51.MA001 | -P20 | 26 |  | PE-L1-5C4-03 | PE-L1-5C4-03 | GT#2-1-21MBN25AA001 -Y02 |  |  | 1 | 1926 | 21BUA51.MA001-P2026 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-03 | 0.13 | 220 | D | 120 | GT PKG | 21BUA51.MA001 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 21MBN25AA001 -Y02 | BLL-VLV PREM LFT FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #21 | RL, LL, L-, BR, PE | B212-016AT0011 → B212-996AT0023 → M0309 → D0322-L24 → M0308 → D0306-L24 → M0307 → D0321-L22 → M0306 → B261-006DC0005 → B261-006DC0003 → B261-017DC0109 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MYB30GF102 -X03 (401, 402, 403, 404, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
21BUA01.FB003 | -P20 | 27 |  | PE-L1-2C4-07 | PE-L1-2C4-07 | GT#2-1-21MBN25AA501 -Y01 |  |  | 1 | 1927 | 21BUA01.FB003-P2027 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-07 | 0.053 | 220 | D | 120 | GT PKG | 21BUA01.FB003 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L+, L- | 21MBN25AA501 -Y01 | FIL-VLV PREM LFT FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #21 | L+, L- | B212-016AT0011 → B212-996AT0023 → M0309 → D0322-L24 → M0308 → D0306-L24 → M0307 → D0321-L22 → M0306 → B261-006DC0005 → B261-006DC0003 → B261-017DC0110 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MYB30GF102 -X03 (701, 702) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
21BUA51.NB001 | -P20 | 28 |  | PE-L1-5C4-03 | PE-L1-5C4-03 | GT#2-1-21MBN26AA001 -Y02 |  |  | 1 | 1928 | 21BUA51.NB001-P2028 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-03 | 0.13 | 220 | D | 120 | GT PKG | 21BUA51.NB001 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 21MBN26AA001 -Y02 | BLL-VLV PREM RGHT FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #21 | RL, LL, L-, BR, PE | B212-016AT0011 → B212-996AT0023 → M0309 → D0322-L24 → M0308 → D0306-L24 → M0307 → D0321-L22 → M0306 → B261-006DC0005 → B261-006DC0003 → B261-017DC0111 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MYB30GF202 -X03 (401, 402, 403, 404, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
21BUA01.FB004 | -P20 | 29 |  | PE-L1-2C4-07 | PE-L1-2C4-07 | GT#2-1-21MBN26AA501 -Y01 |  |  | 1 | 1929 | 21BUA01.FB004-P2029 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-07 | 0.053 | 220 | D | 70 | GT PKG | 21BUA01.FB004 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L+, L- | 21MBN26AA501 -Y01 | FIL-VLV PREM RGHT FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #21 | L+, L- | B212-016AT0011 → B212-016AT0010 → B212-016AT0009 → B212-016AT0015 → B212-016AT0016 → B261-017DC0006 → B261-017DC0116 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MYB30GF202 -X03 (701, 702) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
21BUA01.HA001 | -P20 | 30 |  | PE-L1-2C4-07 | PE-L1-2C4-07 | GT#2-1-21MBN27AA501 -Y01 |  |  | 1 | 1930 | 21BUA01.HA001-P2030 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-07 | 0.048 | 220 | D | 70 | GT PKG | 21BUA01.HA001 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L+, L- | 21MBN27AA501 -Y01 | LKG VLV PREM FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #21 | L+, L- | B212-016AT0011 → B212-016AT0010 → B212-016AT0009 → B212-016AT0015 → B212-016AT0016 → B261-017DC0006 → B261-017DC0117 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MYB30GF010 -X03 (407, 408) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
21BFA02.CB004 | -P20 | 31 |  | PE-L1-4C4-23 | PE-L1-4C4-23 | GT#2-1-21MBN60AP001 -M01 |  |  | 1 | 1931 | 21BFA02.CB004-P2031 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-23 | 1.1 | 400 | N | 60 | GT PKG | 21BFA02.CB004 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, L2, L3, PE | 21MBN60AP001 -M01 | DRNG PP AUX-TNK 1 FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, L2, L3, PE | B212-016AT0011 → B212-996AT0023 → M0309 → B261-006DC0014 → B261-016DC0105 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
21BFA03.EA003 | -P20 | 32 |  | PE-L1-4C6-02 | PE-L1-4C6-02 | GT#2-1-21MBN81AP001 -M01 |  |  | 1 | 1932 | 21BFA03.EA003-P2032 | 0.6/1kV CU/XLPE/LSZH | 4C x 6sqmm | PE-L1-4C6-02 | 11 | 400 | N | 70 | GT PKG | 21BFA03.EA003 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, L2, L3, PE | 21MBN81AP001 -M01 | PP FLUSH-WTR FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, L2, L3, PE | B212-016AT0011 → B212-996AT0023 → M0309 → B261-006DC0014 → B261-016DC0106 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 15.5
21BUA01.HA002 | -P20 | 33 |  | PE-L1-2C4-07 | PE-L1-2C4-07 | GT#2-1-21MBN82AA001 -Y01 |  |  | 1 | 1933 | 21BUA01.HA002-P2033 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-07 | 0.078 | 220 | D | 70 | GT PKG | 21BUA01.HA002 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L+, L- | 21MBN82AA001 -Y01 | FLUSHING WATER VALVE 1 | 1.1_MAIN BUILDING COMPLEX / GT #21 | L+, L- | B212-016AT0011 → B212-996AT0023 → M0309 → B261-006DC0014 → B261-017DC0135 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MBY11GF001 -X01 (401, 402) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
21BUA01.HA003 | -P20 | 34 |  | PE-L1-2C4-07 | PE-L1-2C4-07 | GT#2-1-21MBN82AA002 -Y01 |  |  | 1 | 1934 | 21BUA01.HA003-P2034 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-07 | 0.078 | 220 | D | 70 | GT PKG | 21BUA01.HA003 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L+, L- | 21MBN82AA002 -Y01 | FLUSHING WATER VALVE 2 | 1.1_MAIN BUILDING COMPLEX / GT #21 | L+, L- | B212-016AT0011 → B212-996AT0023 → M0309 → B261-006DC0014 → B261-017DC0136 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MBY11GF001 -X01 (403, 404) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
21BUB01.EA001 | -P20 | 35 |  | PE-L1-2C4-08 | PE-L1-2C4-08 | GT#2-1-21MBP13AA501 -Y01 |  |  | 1 | 1935 | 21BUB01.EA001-P2035 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-08 | 0.205 | 220 | D | 50 | GT PKG | 21BUB01.EA001 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L+, L- | 21MBP13AA501 -Y01 | VENT-VLV MN SUP NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #21 | L+, L- | B212-016BT0001 → B212-016BT0002 → B212-016BT0012 → B212-996BT0026 → B261-017DC0137 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MBY09GF001 -X02 (401, 402) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
21BUB01.EA002 | -P20 | 36 |  | PE-L1-2C4-08 | PE-L1-2C4-08 | GT#2-1-21MBP14AA501 -Y01 |  |  | 1 | 1936 | 21BUB01.EA002-P2036 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-08 | 0.205 | 220 | D | 50 | GT PKG | 21BUB01.EA002 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L+, L- | 21MBP14AA501 -Y01 | SOL-VLV VENTG NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #21 | L+, L- | B212-016BT0001 → B212-016BT0002 → B212-016BT0012 → B212-996BT0026 → B261-017DC0138 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MBY09GF001 -X02 (403, 404) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
21BUB01.EA003 | -P20 | 37 |  | PE-L1-2C4-08 | PE-L1-2C4-08 | GT#2-1-21MBP15AA501 -Y01 |  |  | 1 | 1937 | 21BUB01.EA003-P2037 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-08 | 0.205 | 220 | D | 50 | GT PKG | 21BUB01.EA003 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L+, L- | 21MBP15AA501 -Y01 | VENT-VLV CLD SUP NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #21 | L+, L- | B212-016BT0001 → B212-016BT0002 → B212-016BT0012 → B212-996BT0026 → B261-017DC0139 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MBY09GF001 -X02 (405, 406) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
21BUB51.JA001 | -P20 | 38 |  | PE-L1-3C4-29 | PE-L1-3C4-29 | GT#2-1-21MBP21AA001 -E01 |  |  | 1 | 1938 | 21BUB51.JA001-P2038 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-29 | 0.008 | 220 | D | 60 | GT PKG | 21BUB51.JA001 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | X19(D3, D4), PE | 21MBP21AA001 -E01 | SO-VLV LFT DIFFU NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #21 | L, N, PE | B212-016AT0011 → B212-016AT0010 → B212-016AT0009 → B212-016AT0015 → B212-016AT0016 → B261-017DC0006 → B261-017DC0118 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MYB30GF102 -X03 (412, 413, 414) | 1 | A2F-S-25-N34 | 12 - 18 | 13
21BUB51.JA001 | -P20 | 39 |  | PE-L1-5C4-03 | PE-L1-5C4-03 | GT#2-1-21MBP21AA001 -Y02 |  |  | 1 | 1939 | 21BUB51.JA001-P2039 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-03 | 0.13 | 220 | D | 60 | GT PKG | 21BUB51.JA001 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 21MBP21AA001 -Y02 | SO-VLV LFT DIFFU NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #21 | RL, LL, L-, BR, PE | B212-016AT0011 → B212-016AT0010 → B212-016AT0009 → B212-016AT0015 → B212-016AT0016 → B261-017DC0006 → B261-017DC0119 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MYB30GF102 -X03 (408, 409, 410, 411, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
21BUB51.KB001 | -P20 | 40 |  | PE-L1-3C4-29 | PE-L1-3C4-29 | GT#2-1-21MBP21AA002 -E01 |  |  | 1 | 1940 | 21BUB51.KB001-P2040 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-29 | 0.008 | 220 | D | 60 | GT PKG | 21BUB51.KB001 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | X19(D3, D4), PE | 21MBP21AA002 -E01 | SO-VLV LFT PREM NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #21 | L, N, PE | B212-016AT0011 → B212-016AT0010 → B212-016AT0009 → B212-016AT0015 → B212-016AT0016 → B261-017DC0006 → B261-017DC0120 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MYB30GF102 -X03 (419, 420, 421) | 1 | A2F-S-25-N34 | 12 - 18 | 13
21BUB51.KB001 | -P20 | 41 |  | PE-L1-5C4-03 | PE-L1-5C4-03 | GT#2-1-21MBP21AA002 -Y02 |  |  | 1 | 1941 | 21BUB51.KB001-P2041 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-03 | 0.13 | 220 | D | 60 | GT PKG | 21BUB51.KB001 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 21MBP21AA002 -Y02 | SO-VLV LFT PREM NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #21 | RL, LL, L-, BR, PE | B212-016AT0011 → B212-016AT0010 → B212-016AT0009 → B212-016AT0015 → B212-016AT0016 → B261-017DC0006 → B261-017DC0121 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MYB30GF102 -X03 (415, 416, 417, 418, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
21BUB51.MA001 | -P20 | 42 |  | PE-L1-3C4-29 | PE-L1-3C4-29 | GT#2-1-21MBP21AA003 -E01 |  |  | 1 | 1942 | 21BUB51.MA001-P2042 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-29 | 0.008 | 220 | D | 60 | GT PKG | 21BUB51.MA001 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | X19(D3, D4), PE | 21MBP21AA003 -E01 | SO-VLV LFT PILOT NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #21 | L, N, PE | B212-016AT0011 → B212-016AT0010 → B212-016AT0009 → B212-016AT0015 → B212-016AT0016 → B261-017DC0006 → B261-017DC0122 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MYB30GF102 -X03 (426, 427, 428) | 1 | A2F-S-25-N34 | 12 - 18 | 13
21BUB51.MA001 | -P20 | 43 |  | PE-L1-5C4-03 | PE-L1-5C4-03 | GT#2-1-21MBP21AA003 -Y02 |  |  | 1 | 1943 | 21BUB51.MA001-P2043 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-03 | 0.13 | 220 | D | 60 | GT PKG | 21BUB51.MA001 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 21MBP21AA003 -Y02 | SO-VLV LFT PILOT NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #21 | RL, LL, L-, BR, PE | B212-016AT0011 → B212-016AT0010 → B212-016AT0009 → B212-016AT0015 → B212-016AT0016 → B261-017DC0006 → B261-017DC0123 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MYB30GF102 -X03 (422, 423, 424, 425, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
21BUB51.NB001 | -P20 | 44 |  | PE-L1-3C4-29 | PE-L1-3C4-29 | GT#2-1-21MBP22AA001 -E01 |  |  | 1 | 1944 | 21BUB51.NB001-P2044 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-29 | 0.008 | 220 | D | 60 | GT PKG | 21BUB51.NB001 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | X19(D3, D4), PE | 21MBP22AA001 -E01 | SO-VLV RGHT DIFFU NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #21 | L, N, PE | B212-016AT0011 → B212-016AT0010 → B212-016AT0009 → B212-016AT0015 → B212-016AT0016 → B261-017DC0006 → B261-017DC0124 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MYB30GF202 -X03 (412, 413, 414) | 1 | A2F-S-25-N34 | 12 - 18 | 13
21BUB51.NB001 | -P20 | 45 |  | PE-L1-5C4-03 | PE-L1-5C4-03 | GT#2-1-21MBP22AA001 -Y02 |  |  | 1 | 1945 | 21BUB51.NB001-P2045 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-03 | 0.13 | 220 | D | 60 | GT PKG | 21BUB51.NB001 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 21MBP22AA001 -Y02 | SO-VLV RGHT DIFFU NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #21 | RL, LL, L-, BR, PE | B212-016AT0011 → B212-016AT0010 → B212-016AT0009 → B212-016AT0015 → B212-016AT0016 → B261-017DC0006 → B261-017DC0125 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MYB30GF202 -X03 (408, 409, 410, 411, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
21BUB51.QA001 | -P20 | 46 |  | PE-L1-3C4-29 | PE-L1-3C4-29 | GT#2-1-21MBP22AA002 -E01 |  |  | 1 | 1946 | 21BUB51.QA001-P2046 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-29 | 0.008 | 220 | D | 60 | GT PKG | 21BUB51.QA001 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | X19(D3, D4), PE | 21MBP22AA002 -E01 | SO-VLV RGHT PREM NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #21 | L, N, PE | B212-016AT0011 → B212-016AT0010 → B212-016AT0009 → B212-016AT0015 → B212-016AT0016 → B261-017DC0006 → B261-017DC0126 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MYB30GF202 -X03 (419, 420, 421) | 1 | A2F-S-25-N34 | 12 - 18 | 13
21BUB51.QA001 | -P20 | 47 |  | PE-L1-5C4-03 | PE-L1-5C4-03 | GT#2-1-21MBP22AA002 -Y02 |  |  | 1 | 1947 | 21BUB51.QA001-P2047 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-03 | 0.13 | 220 | D | 60 | GT PKG | 21BUB51.QA001 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 21MBP22AA002 -Y02 | SO-VLV RGHT PREM NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #21 | RL, LL, L-, BR, PE | B212-016AT0011 → B212-016AT0010 → B212-016AT0009 → B212-016AT0015 → B212-016AT0016 → B261-017DC0006 → B261-017DC0127 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MYB30GF202 -X03 (415, 416, 417, 418, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
21BUB51.RB001 | -P20 | 48 |  | PE-L1-3C4-29 | PE-L1-3C4-29 | GT#2-1-21MBP22AA003 -E01 |  |  | 1 | 1948 | 21BUB51.RB001-P2048 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-29 | 0.008 | 220 | D | 60 | GT PKG | 21BUB51.RB001 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | X19(D3, D4), PE | 21MBP22AA003 -E01 | SO-VLV RGHT PILOT NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #21 | L, N, PE | B212-016AT0011 → B212-016AT0010 → B212-016AT0009 → B212-016AT0015 → B212-016AT0016 → B261-017DC0006 → B261-017DC0128 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MYB30GF202 -X03 (426, 427, 428) | 1 | A2F-S-25-N34 | 12 - 18 | 13
21BUB51.RB001 | -P20 | 49 |  | PE-L1-5C4-03 | PE-L1-5C4-03 | GT#2-1-21MBP22AA003 -Y02 |  |  | 1 | 1949 | 21BUB51.RB001-P2049 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-03 | 0.13 | 220 | D | 60 | GT PKG | 21BUB51.RB001 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 21MBP22AA003 -Y02 | SO-VLV RGHT PILOT NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #21 | RL, LL, L-, BR, PE | B212-016AT0011 → B212-016AT0010 → B212-016AT0009 → B212-016AT0015 → B212-016AT0016 → B261-017DC0006 → B261-017DC0129 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MYB30GF202 -X03 (422, 423, 424, 425, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
21BFA03.EA001 | -P20 | 50 |  | PE-L1-3C4-24 | PE-L1-3C4-24 | GT#2-1-21MBQ11AA001 -Y01 |  |  | 1 | 1950 | 21BFA03.EA001-P2050 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-24 | 0.16 | 230 | N | 50 | GT PKG | 21BFA03.EA001 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, N, PE | 21MBQ11AA001 -Y01 | SOL-VLV 1 IGN-GAS | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, N, PE | B212-016AT0011 → B212-016AT0010 → B212-016AT0009 → B212-016AT0015 → B212-016AT0016 → B261-017DC0006 → B261-017DC0130 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MYB30GF021 -X01 (701, 702, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 13
21BFA03.EA002 | -P20 | 51 |  | PE-L1-3C4-24 | PE-L1-3C4-24 | GT#2-1-21MBQ11AA002 -Y01 |  |  | 1 | 1951 | 21BFA03.EA002-P2051 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-24 | 0.125 | 230 | N | 60 | GT PKG | 21BFA03.EA002 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, N, PE | 21MBQ11AA002 -Y01 | SOL-VLV 2 IGN-GAS | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, N, PE | B212-016AT0011 → B212-016AT0010 → B212-016AT0009 → B212-016AT0015 → B212-016AT0016 → B261-017DC0006 → B261-017DC0131 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MYB30GF021 -X01 (703, 704, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 13
21BMA52.PB001 | -P20 | 54 |  | PE-L1-4C10-01 | PE-L1-4C10-01 | GT#2-1-21MBV21AP001 -M01 |  |  | 1 | 1952 | 21BMA52.PB001-P2054 | 0.6/1kV CU/XLPE/LSZH | 4C x 10sqmm | PE-L1-4C10-01 | 22 | 400 | E | 55 | GT PKG | 21BMA52.PB001 | GTG #21 400V AC EMERGENCY SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, L2, L3, PE | 21MBV21AP001 -M01 | LUBRICATING OIL PUMP 1 | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, L2, L3, PE | B212-016BT0025 → B212-016BT0007 → B212-016BT0008 → B212-016BT0009 → B212-016BT0010 → B212-016BT0002 → B212-016BT0012 → B212-996BT0026 → B261-016DC0107 → END |  | 1 | A2F-S-25a-N34 | 16 - 20.5 | 18
21BFA02.PB001 | -P20 | 55 |  | PE-L1-4C10-01 | PE-L1-4C10-01 | GT#2-1-21MBV21AP002 -M01 |  |  | 1 | 1953 | 21BFA02.PB001-P2055 | 0.6/1kV CU/XLPE/LSZH | 4C x 10sqmm | PE-L1-4C10-01 | 22 | 400 | N | 55 | GT PKG | 21BFA02.PB001 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, L2, L3, PE | 21MBV21AP002 -M01 | LUBRICATING OIL PUMP 2 | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, L2, L3, PE | B212-016BT0025 → B212-016BT0007 → B212-016BT0008 → B212-016BT0009 → B212-016BT0010 → B212-016BT0002 → B212-016BT0012 → B212-996BT0026 → B261-016DC0108 → END |  | 1 | A2F-S-25a-N34 | 16 - 20.5 | 18
21BUA51.RA001 | -P20 | 56 |  | PE-L1-3C4-29 | PE-L1-3C4-29 | GT#2-1-21MBV21AP003 -E01 |  |  | 1 | 1954 | 21BUA51.RA001-P2056 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-29 | 0.1 | 220 | D | 40 | GT PKG | 21BUA51.RA001 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | X19(D03(L), D04(N)), PE | 21MBV21AP003 -E01 | EMERGENCY LUB-OIL-PP | 1.1_MAIN BUILDING COMPLEX / GT #21 | L, N, PE | B212-016BT0001 → B212-016BT0002 → B212-016BT0012 → B212-996BT0026 → B261-017DC0142 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
21BUA51.RA001 | -P20 | 57 |  | PE-L1-4C6-03 | PE-L1-4C6-03 | GT#2-1-21MBV21AP003 -M01 |  |  | 1 | 1955 | 21BUA51.RA001-P2057 | 0.6/1kV CU/XLPE/LSZH | 4C x 6sqmm | PE-L1-4C6-03 | 3.7 | 220 | D | 40 | GT PKG | 21BUA51.RA001 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | X2(1, 2, 3), PE | 21MBV21AP003 -M01 | EMERGENCY LUB-OIL-PP | 1.1_MAIN BUILDING COMPLEX / GT #21 | F1, A2, D2, PE | B212-016BT0001 → B212-016BT0002 → B212-016BT0012 → B212-996BT0026 → B261-017DC0143 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 15.5
21BUA51.RA001 | -P20 | 58 |  | PE-L1-3C95/50-01 | PE-L1-3C95/50-01 | GT#2-1-21MBV21AP003 -R01 |  |  | 1 | 1956 | 21BUA51.RA001-P2058 | 0.6/1kV CU/XLPE/LSZH | 2C x 95sqmm + 1C x 50sqmm | PE-L1-3C95/50-01 | 3.7 | 220 | D | 40 | GT PKG | 21BUA51.RA001 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | X2(1, 2), PE | 21MBV21AP003 -R01 | EMERGENCY LUB-OIL-PP | 1.1_MAIN BUILDING COMPLEX / GT #21 | 1, 2, PE | B212-016BT0001 → B212-016BT0002 → B212-016BT0012 → B212-996BT0026 → B261-017DC0144 → END |  | 1 | A2F-S-50-N1-12 | 32.1 - 40 | 34.5
21BMA51.SA001 | -P20 | 59 |  | PE-L1-4C35/25-02 | PE-L1-4C35/25-02 | GT#2-1-21MBV30AP001 -M01 |  |  | 1 | 1957 | 21BMA51.SA001-P2059 | 0.6/1kV CU/XLPE/LSZH | 3C x 35sqmm + 1C X 25sqmm | PE-L1-4C35/25-02 | 50.6 | 400 | E | 60 | GT PKG | 21BMA51.SA001 | GTG #21 400V AC EMERGENCY SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, L2, L3, PE | 21MBV30AP001 -M01 | LIFTING OIL PUMP 1 | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, L2, L3, PE | B212-016BT0025 → B212-016BT0007 → B212-016BT0008 → B212-016BT0009 → B212-016BT0010 → B212-016BT0002 → B212-016BT0012 → B212-996BT0026 → B261-016DC0111 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5
21BFA02.SA001 | -P20 | 60 |  | PE-L1-4C35/25-02 | PE-L1-4C35/25-02 | GT#2-1-21MBV30AP002 -M01 |  |  | 1 | 1958 | 21BFA02.SA001-P2060 | 0.6/1kV CU/XLPE/LSZH | 3C x 35sqmm + 1C X 25sqmm | PE-L1-4C35/25-02 | 50.6 | 400 | N | 40 | GT PKG | 21BFA02.SA001 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, L2, L3, PE | 21MBV30AP002 -M01 | LIFTING OIL PUMP 2 | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, L2, L3, PE | B212-016BT0001 → B212-016BT0002 → B212-016BT0012 → B212-996BT0026 → B261-016DC0112 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5
21BMA52.CB001 | -P20 | 61 |  | PE-L1-4C4-23 | PE-L1-4C4-23 | GT#2-1-21MBV50AN001 -M01 |  |  | 1 | 1959 | 21BMA52.CB001-P2061 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-23 | 2.2 | 400 | E | 60 | GT PKG | 21BMA52.CB001 | GTG #21 400V AC EMERGENCY SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, L2, L3, PE | 21MBV50AN001 -M01 | OIL-VAP-EXTR1 LUB-OIL-TNK | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, L2, L3, PE | B212-016BT0025 → B212-016BT0007 → B212-016BT0008 → B212-016BT0009 → B212-016BT0010 → B212-016BT0002 → B212-016BT0012 → B212-996BT0026 → B261-016DC0123 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
21BFA02.EA001 | -P20 | 62 |  | PE-L1-4C4-23 | PE-L1-4C4-23 | GT#2-1-21MBV50AN002 -M01 |  |  | 1 | 1960 | 21BFA02.EA001-P2062 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-23 | 2.2 | 400 | N | 50 | GT PKG | 21BFA02.EA001 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, L2, L3, PE | 21MBV50AN002 -M01 | OIL-VAP-EXTR2 LUB-OIL-TNK | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, L2, L3, PE | B212-016BT0001 → B212-016BT0002 → B212-016BT0012 → B212-996BT0026 → B261-016DC0121 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
21BFA02.FB001 | -P20 | 63 |  | PE-L1-4C4-23 | PE-L1-4C4-23 | GT#2-1-21MBX01AH001 -E01 |  |  | 1 | 1961 | 21BFA02.FB001-P2063 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-23 | 1 | 400 | N | 50 | GT PKG | 21BFA02.FB001 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, L2, L3, PE | 21MBX01AH001 -E01 | TNK HTG 1 HYDRC OIL | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, L2, L3, PE | B212-016BT0001 → B212-016BT0002 → B212-016BT0012 → B212-996BT0026 → B261-016DC0124 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
21BFA02.FB002 | -P20 | 64 |  | PE-L1-4C4-23 | PE-L1-4C4-23 | GT#2-1-21MBX01AH002 -E01 |  |  | 1 | 1962 | 21BFA02.FB002-P2064 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-23 | 1 | 400 | N | 50 | GT PKG | 21BFA02.FB002 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, L2, L3, PE | 21MBX01AH002 -E01 | TNK HTG 2 HYDRC OIL | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, L2, L3, PE | B212-016BT0001 → B212-016BT0002 → B212-016BT0012 → B212-996BT0026 → B261-016DC0122 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
21BFA02.HA002 | -P20 | 65 |  | PE-L1-4C4-23 | PE-L1-4C4-23 | GT#2-1-21MBX02AP001 -M01 |  |  | 1 | 1963 | 21BFA02.HA002-P2065 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-23 | 7.5 | 400 | N | 60 | GT PKG | 21BFA02.HA002 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, L2, L3, PE | 21MBX02AP001 -M01 | MN PP 1 HYDRC OIL | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, L2, L3, PE | B212-016BT0025 → B212-016BT0007 → B212-016BT0008 → B212-016BT0009 → B212-016BT0010 → B212-016BT0002 → B212-016BT0012 → B212-996BT0026 → B261-016DC0114 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
21BFA02.HA003 | -P20 | 66 |  | PE-L1-4C4-23 | PE-L1-4C4-23 | GT#2-1-21MBX02AP002 -M01 |  |  | 1 | 1964 | 21BFA02.HA003-P2066 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-23 | 7.5 | 400 | N | 50 | GT PKG | 21BFA02.HA003 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, L2, L3, PE | 21MBX02AP002 -M01 | MN PP 2 HYDRC OIL | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, L2, L3, PE | B212-016BT0001 → B212-016BT0002 → B212-016BT0012 → B212-996BT0026 → B261-016DC0115 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
21BFA02.HA001 | -P20 | 67 |  | PE-L1-4C4-24 | PE-L1-4C4-24 | GT#2-1-21MBX06AH001 -M01 |  |  | 1 | 1965 | 21BFA02.HA001-P2067 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-24 | 0.18 | 400 | N | 60 | GT PKG | 21BFA02.HA001 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, L2, L3, PE | 21MBX06AH001 -M01 | FAN COOL-CCT HYDRC OIL | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, L2, L3, PE | B212-016BT0025 → B212-016BT0007 → B212-016BT0008 → B212-016BT0009 → B212-016BT0010 → B212-016BT0002 → B212-016BT0012 → B212-996BT0026 → B261-016DC0116 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
21BFA02.JB001 | -P20 | 68 |  | PE-L1-4C16-02 | PE-L1-4C16-02 | GT#2-1-21MBY10GF002 -E01 |  |  | 1 | 1966 | 21BFA02.JB001-P2068 | 0.6/1kV CU/XLPE/LSZH | 4C X 16sqmm | PE-L1-4C16-02 | 28 | 400 | N | 50 | GT PKG | 21BFA02.JB001 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, L2, L3, PE | 21MBY10GF002 -E01 | JUNCT BOX HTG LUB-OIL TNK | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, L2, L3, PE | B212-016BT0001 → B212-016BT0002 → B212-016BT0012 → B212-996BT0026 → B261-016DC0113 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MBY10GF002 -X01 (701, 702, 703, PE) | 1 | A2F-S-25a-N34 | 16 - 20.5 | 19.5
21BFA52.HA001 | -P20 | 69 |  | PE-L1-5C4-04 | PE-L1-5C4-04 | GT#2-1-21MBY40GH001 -E01 |  |  | 1 | 1967 | 21BFA52.HA001-P2069 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-04 | 9 | 400 | N | 70 | GT PKG | 21BFA52.HA001 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, L2, L3, N, PE | 21MBY40GH001 -E01 | JB INSTR AIR SYST | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, L2, L3, N, PE | B212-016AT0011 → B212-996AT0023 → M0308 → B261-006DC0012 → B261-016DC0104 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MBY40GH001 -X01 (701, 702, 703, 704, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
21BFA51.HA002 | -P20 | 70 |  | PE-L1-5C4-04 | PE-L1-5C4-04 | GT#2-1-21MBY80GH001 -E01 |  |  | 1 | 1968 | 21BFA51.HA002-P2070 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-04 | 7 | 400 | N | 60 | GT PKG | 21BFA51.HA002 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, L2, L3, N, PE | 21MBY80GH001 -E01 | TRACE HEATING CABINET | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, L2, L3, N, PE | B212-016AT0011 → B212-016AT0010 → B212-016AT0009 → B212-016AT0015 → B212-016AT0016 → B261-016DC0019 → B261-016DC0102 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MBY80GH001 -X02 (L1, L2, L3, N, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
21BFA02.EA002 | -P20 | 71 |  | PE-L1-4C4-24 | PE-L1-4C4-24 | GT#2-1-21MKA10AH010 -E01 |  |  | 1 | 1969 | 21BFA02.EA002-P2071 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-24 | 3.2 | 400 | N | 40 | GT PKG | 21BFA02.EA002 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, L2, L3, PE | 21MKA10AH010 -E01 | GENERATOR SPACE HEATER | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, L2, L3, PE | B212-016BT0025 → B212-016BT0007 → B212-016BT0019 → B212-016BT0020 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
21MKC01GT002 -E01 | -P20 | 74 |  | PE-L1-1C240-02 | PE-L1-1C240-02 | GT#2-1-21MKC01GT002 -E01 |  |  | 1 | 1970 | 21MKC1001 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-02 | 1100 | 550 | N | 50 | GT PKG | 21MKC01GT002 -E01 | GTG #21 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1 | 21CJT21 | GTG #21 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | L1 | B261-007DC0013 → M0307 → D0306-L34 → M0308 → B212-996AT0021 → B212-016AT0004 → B212-016AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
21MKC01GT002 -E01 | -P20 | 75 |  | PE-L1-1C240-02 | PE-L1-1C240-02 | GT#2-1 |  |  | 1 | 1971 | 21MKC1004 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-02 | 1100 | 550 | N | 50 | GT PKG | 21MKC01GT002 -E01 | GTG #21 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #21 | L2 | 21CJT21 | GTG #21 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | L2 | B261-007DC0013 → M0307 → D0306-L34 → M0308 → B212-996AT0021 → B212-016AT0004 → B212-016AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
21MKC01GT002 -E01 | -P20 | 76 |  | PE-L1-1C240-02 | PE-L1-1C240-02 | GT#2-1 |  |  | 1 | 1972 | 21MKC1007 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-02 | 1100 | 550 | N | 50 | GT PKG | 21MKC01GT002 -E01 | GTG #21 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #21 | L3 | 21CJT21 | GTG #21 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | L3 | B261-007DC0013 → M0307 → D0306-L34 → M0308 → B212-996AT0021 → B212-016AT0004 → B212-016AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
21MKC01GT002 -E01 | -P20 | 77 |  | PE-L1-1C240-02 | PE-L1-1C240-02 | GT#2-1 |  |  | 1 | 1973 | 21MKC1002 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-02 | 1100 | 550 | N | 50 | GT PKG | 21MKC01GT002 -E01 | GTG #21 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1 | 21CJT21 | GTG #21 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | L1 | B261-007DC0014 → M0307 → D0306-L34 → M0308 → B212-996AT0021 → B212-016AT0004 → B212-016AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
21MKC01GT002 -E01 | -P20 | 78 |  | PE-L1-1C240-02 | PE-L1-1C240-02 | GT#2-1 |  |  | 1 | 1974 | 21MKC1005 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-02 | 1100 | 550 | N | 50 | GT PKG | 21MKC01GT002 -E01 | GTG #21 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #21 | L2 | 21CJT21 | GTG #21 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | L2 | B261-007DC0014 → M0307 → D0306-L34 → M0308 → B212-996AT0021 → B212-016AT0004 → B212-016AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
21MKC01GT002 -E01 | -P20 | 79 |  | PE-L1-1C240-02 | PE-L1-1C240-02 | GT#2-1 |  |  | 1 | 1975 | 21MKC1008 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-02 | 1100 | 550 | N | 50 | GT PKG | 21MKC01GT002 -E01 | GTG #21 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #21 | L3 | 21CJT21 | GTG #21 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | L3 | B261-007DC0014 → M0307 → D0306-L34 → M0308 → B212-996AT0021 → B212-016AT0004 → B212-016AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
21MKC01GT002 -E01 | -P20 | 82 |  | PE-L1-1C240-02 | PE-L1-1C240-02 | GT#2-1 |  |  | 1 | 1976 | 21MKC1003 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-02 | 1100 | 550 | N | 50 | GT PKG | 21MKC01GT002 -E01 | GTG #21 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1 | 21CJT21 | GTG #21 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | L1 | B261-007DC0015 → M0307 → D0306-L34 → M0308 → B212-996AT0021 → B212-016AT0004 → B212-016AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
21MKC01GT002 -E01 | -P20 | 83 |  | PE-L1-1C240-02 | PE-L1-1C240-02 | GT#2-1 |  |  | 1 | 1977 | 21MKC1006 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-02 | 1100 | 550 | N | 50 | GT PKG | 21MKC01GT002 -E01 | GTG #21 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #21 | L2 | 21CJT21 | GTG #21 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | L2 | B261-007DC0015 → M0307 → D0306-L34 → M0308 → B212-996AT0021 → B212-016AT0004 → B212-016AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
21MKC01GT002 -E01 | -P20 | 84 |  | PE-L1-1C240-03 | PE-L1-1C240-03 | GT#2-1 |  |  | 1 | 1978 | 21MKC1009 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-03 | 1100 | 550 | N | 50 | GT PKG | 21MKC01GT002 -E01 | GTG #21 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #21 | L3 | 21CJT21 | GTG #21 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | L3 | B261-007DC0015 → M0307 → D0306-L34 → M0308 → B212-996AT0021 → B212-016AT0004 → B212-016AT0005 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
21BFA52.DA002 | -P20 | 90 |  | PE-L1-3C4-24 | PE-L1-3C4-24 | GT#2-1-21MKC01GW035 -E01 |  |  | 1 | 1979 | 21BFA52.DA002-P2090 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-24 | 1.2 | 230 | N | 50 | GT PKG | 21BFA52.DA002 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3210) | L1, N, PE | 21MKC01GW035 -E01 | MKC 1AC AUX-VOLT SUP | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, N, PE | B212-016AT0011 → B212-996AT0023 → M0309 → D0322-L24 → M0308 → D0306-L24 → M0307 → B261-007DC0012 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
21BFA51.HA003 | -P20 | 91 |  | PE-L1-5C4-04 | PE-L1-5C4-04 | GT#2-1-21MKC05GE001 -E01 |  |  | 1 | 1980 | 21BFA51.HA003-P2091 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-04 | 1.15 | 400 | N | 50 | GT PKG | 21BFA51.HA003 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, L2, L3, N, PE | 21MKC05GE001 -E01 | TERBO POW-SUP SLRNGRM-VEN | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, L2, L3, N, PE | B212-016AT0011 → B212-996AT0023 → M0309 → D0322-L24 → M0308 → D0306-L24 → M0307 → B261-007DC0012 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MKC05GE001 -X0 (1, 2, 3, 4, N, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
21BFA51.DA003 | -P20 | 92 |  | PE-L1-3C4-24 | PE-L1-3C4-24 | GT#2-1-21MKC10GP001 -E01 |  |  | 1 | 1981 | 21BFA51.DA003-P2092 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-24 | 0.22 | 230 | N | 50 | GT PKG | 21BFA51.DA003 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, N, PE | 21MKC10GP001 -E01 | LIGHTING EXCITER HOUSING | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, N, PE | B212-016AT0011 → B212-996AT0023 → M0309 → D0322-L23 → M0308 → B261-007DC0012 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
21CJT21 | -P20 | 93 |  | PE-L1-1C240-02 | PE-L1-1C240-02 | GT#2-1-21MKC30GE001 -E01 |  |  | 1 | 1982 | 21CJT1001 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-02 | - | 700 | D | 40 | GT PKG | 21CJT21 | GTG #21 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | L+ | 21MKC30GE001 -E01 | GEN EXCN BRSH | 1.1_MAIN BUILDING COMPLEX / GT #21 | L+ | B212-016BT0005 → B212-016BT0006 → B212-016BT0007 → B212-016BT0019 → B212-016BT0020 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 | To 단자대 Hole 확인필요
21CJT21 | -P20 | 94 |  | PE-L1-1C240-02 | PE-L1-1C240-02 | GT#2-1 |  |  | 1 | 1983 | 21CJT1002 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-02 | - | 700 | D | 40 | GT PKG | 21CJT21 | GTG #21 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | L+ | 21MKC30GE001 -E01 | GEN EXCN BRSH | 1.1_MAIN BUILDING COMPLEX / GT #21 | L+ | B212-016BT0005 → B212-016BT0006 → B212-016BT0007 → B212-016BT0019 → B212-016BT0020 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 | To 단자대 Hole 확인필요
21CJT21 | -P20 | 95 |  | PE-L1-1C240-02 | PE-L1-1C240-02 | GT#2-1 |  |  | 1 | 1984 | 21CJT1003 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-02 | - | 700 | D | 40 | GT PKG | 21CJT21 | GTG #21 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | L+ | 21MKC30GE001 -E01 | GEN EXCN BRSH | 1.1_MAIN BUILDING COMPLEX / GT #21 | L+ | B212-016BT0005 → B212-016BT0006 → B212-016BT0007 → B212-016BT0019 → B212-016BT0020 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 | To 단자대 Hole 확인필요
21CJT21 | -P20 | 96 |  | PE-L1-1C240-02 | PE-L1-1C240-02 | GT#2-1 |  |  | 1 | 1985 | 21CJT1004 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-02 | - | 700 | D | 40 | GT PKG | 21CJT21 | GTG #21 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | L+ | 21MKC30GE001 -E01 | GEN EXCN BRSH | 1.1_MAIN BUILDING COMPLEX / GT #21 | L+ | B212-016BT0005 → B212-016BT0006 → B212-016BT0007 → B212-016BT0019 → B212-016BT0020 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 | To 단자대 Hole 확인필요
21CJT21 | -P20 | 97 |  | PE-L1-1C240-02 | PE-L1-1C240-02 | GT#2-1 |  |  | 1 | 1986 | 21CJT1005 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-02 | - | 700 | D | 40 | GT PKG | 21CJT21 | GTG #21 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | L- | 21MKC30GE001 -E01 | GEN EXCN BRSH | 1.1_MAIN BUILDING COMPLEX / GT #21 | L- | B212-016BT0005 → B212-016BT0006 → B212-016BT0007 → B212-016BT0019 → B212-016BT0020 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 | To 단자대 Hole 확인필요
21CJT21 | -P20 | 98 |  | PE-L1-1C240-02 | PE-L1-1C240-02 | GT#2-1 |  |  | 1 | 1987 | 21CJT1006 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-02 | - | 700 | D | 40 | GT PKG | 21CJT21 | GTG #21 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | L- | 21MKC30GE001 -E01 | GEN EXCN BRSH | 1.1_MAIN BUILDING COMPLEX / GT #21 | L- | B212-016BT0005 → B212-016BT0006 → B212-016BT0007 → B212-016BT0019 → B212-016BT0020 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 | To 단자대 Hole 확인필요
21CJT21 | -P20 | 98 |  | PE-L1-1C240-02 | PE-L1-1C240-02 | GT#2-1 |  |  | 1 | 1988 | 21CJT1007 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-02 | - | 700 | D | 40 | GT PKG | 21CJT21 | GTG #21 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | L- | 21MKC30GE001 -E01 | GEN EXCN BRSH | 1.1_MAIN BUILDING COMPLEX / GT #21 | L- | B212-016BT0005 → B212-016BT0006 → B212-016BT0007 → B212-016BT0019 → B212-016BT0020 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 | To 단자대 Hole 확인필요
21CJT21 | -P20 | 98 |  | PE-L1-1C240-02 | PE-L1-1C240-02 | GT#2-1 |  |  | 1 | 1989 | 21CJT1008 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-02 | - | 700 | D | 40 | GT PKG | 21CJT21 | GTG #21 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #21(UBA3310) | L- | 21MKC30GE001 -E01 | GEN EXCN BRSH | 1.1_MAIN BUILDING COMPLEX / GT #21 | L- | B212-016BT0005 → B212-016BT0006 → B212-016BT0007 → B212-016BT0019 → B212-016BT0020 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 | To 단자대 Hole 확인필요
21BUA51.DA001 | -P20 | 99 |  | PE-L1-2C4-07 | PE-L1-2C4-07 | GT#2-1-21MPB10GW011 -E01 |  |  | 1 | 1990 | 21BUA51.DA001-P2099 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-07 | 1 | 220 | D | 130 | GT PKG | 21BUA51.DA001 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L+, L- | 21MPB10GW011 -E01 | GAS-TURB ENCL EMERG LITG | 1.1_MAIN BUILDING COMPLEX / GT #21 | L+, L- | B212-016AT0011 → B212-996AT0023 → M0309 → D0322-L24 → M0308 → D0306-L24 → M0307 → D0321-L22 → M0306 → B261-006DC0005 → B261-006DC0003 → B261-017DC0101 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
21BFA51.DA004 | -P2 | 100 |  | PE-L1-3C4-24 | PE-L1-3C4-24 | GT#2-1-21MPB10GW023 -E01 |  |  | 1 | 1991 | 21BFA51.DA004-P2100 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-24 | 1 | 230 | N | 130 | GT PKG | 21BFA51.DA004 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, N, PE | 21MPB10GW023 -E01 | GAS-TURB ENCL LITG | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, N, PE | B212-016AT0011 → B212-996AT0023 → M0309 → D0322-L24 → M0308 → D0306-L24 → M0307 → D0321-L22 → M0306 → B261-006DC0005 → B261-006DC0003 → B261-017DC0102 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
21BUA51.DA002 | -P2 | 101 |  | PE-L1-2C4-07 | PE-L1-2C4-07 | GT#2-1-21MPB13GW011 -E01 |  |  | 1 | 1992 | 21BUA51.DA002-P2101 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-07 | 0.22 | 220 | D | 40 | GT PKG | 21BUA51.DA002 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L+, L- | 21MPB13GW011 -E01 | FGS ENCL EMERG LITG | 1.1_MAIN BUILDING COMPLEX / GT #21 | L+, L- | B212-016BT0001 → B212-996BT0022 → M0309 → B261-006DC0021 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
21BFA51.DA005 | -P2 | 102 |  | PE-L1-3C4-24 | PE-L1-3C4-24 | GT#2-1-21MPB13GW023 -E01 |  |  | 1 | 1993 | 21BFA51.DA005-P2102 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-24 | 1 | 230 | N | 40 | GT PKG | 21BFA51.DA005 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, N, PE | 21MPB13GW023 -E01 | FGS ENCL LITG | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, N, PE | B212-016BT0001 → B212-996BT0022 → M0309 → B261-006DC0020 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
21BUA51.DA003 | -P2 | 103 |  | PE-L1-2C4-07 | PE-L1-2C4-07 | GT#2-1-21MPB16GW011 -E01 |  |  | 1 | 1994 | 21BUA51.DA003-P2103 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-07 | 0.44 | 220 | D | 30 | GT PKG | 21BUA51.DA003 | GTG #21 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L+, L- | 21MPB16GW011 -E01 | IMS + GEN ENCL EMERG LITG | 1.1_MAIN BUILDING COMPLEX / GT #21 | L+, L- | B212-016AT0011 → B212-016AT0010 → B212-016AT0009 → B212-016AT0015 → B212-016AT0016 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
21BFA51.DA006 | -P2 | 104 |  | PE-L1-3C4-24 | PE-L1-3C4-24 | GT#2-1-21MPB16GW023 -E01 |  |  | 1 | 1995 | 21BFA51.DA006-P2104 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-24 | 1 | 230 | N | 30 | GT PKG | 21BFA51.DA006 | GTG #21 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, N, PE | 21MPB16GW023 -E01 | IMS + GEN ENCL LITG | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, N, PE | B212-016AT0011 → B212-016AT0010 → B212-016AT0009 → B212-016AT0015 → B212-016AT0016 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
21BMA51.CB001 | -P2 | 105 |  | PE-L1-4C4-24 | PE-L1-4C4-24 | GT#2-1-21SAM33AN001 -M01 |  |  | 1 | 1996 | 21BMA51.CB001-P2105 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-24 | 0.55 | 400 | E | 60 | GT PKG | 21BMA51.CB001 | GTG #21 400V AC EMERGENCY SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, L2, L3, PE | 21SAM33AN001 -M01 | EXH-AIR FAN FU-GAS ENCL | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, L2, L3, PE | B212-016BT0025 → B212-016BT0007 → B212-016BT0008 → B212-016BT0009 → B212-016BT0010 → B212-016BT0002 → B212-016BT0012 → B212-996BT0026 → B261-016DC0109 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
21BFA02.FB001 | -P2 | 106 |  | PE-L1-4C4-24 | PE-L1-4C4-24 | GT#2-1-21SAM33AN002 -M01 |  |  | 1 | 1997 | 21BFA02.FB001-P2106 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-24 | 0.55 | 400 | N | 60 | GT PKG | 21BMA51.CB003 | GTG #21 400V AC EMERGENCY SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #21 | L1, L2, L3, PE | 21SAM33AN002 -M01 | EXH-AIR FAN FU-GAS ENCL | 1.1_MAIN BUILDING COMPLEX / GT #21 | L1, L2, L3, PE | B212-016BT0025 → B212-016BT0007 → B212-016BT0008 → B212-016BT0009 → B212-016BT0010 → B212-016BT0002 → B212-016BT0012 → B212-996BT0026 → B261-016DC0110 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
22BFA51.DA001 | -P20 | 01 |  | PE-L1-3C4-22 | PE-L1-3C4-22 | GT#2-2-22BAB11GW023 -E01 |  |  | 1 | 1998 | 22BFA51.DA001-P2001 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-22 | 0.15 | 230 | N | 30 | GT PKG | 22BFA51.DA001 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, N, PE | 22BAB11GW023 -E01 | GEN NEUT GND CAB | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, N, PE | B212-016CT0001 → B212-016CT0010 → B212-016CT0009 → B212-016CT0015 → B212-016CT0016 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
22BFA03.CB001 | -P20 | 02 |  | PE-L1-3C4-22 | PE-L1-3C4-22 | GT#2-2-22MBA18AA001 -Y01 |  |  | 1 | 1999 | 22BFA03.CB001-P2002 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-22 | 0.073 | 230 | N | 120 | GT PKG | 22BFA03.CB001 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, N, PE | 22MBA18AA001 -Y01 | DRN-VLV 1 FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, N, PE | B212-016CT0001 → B212-016CT0002 → B212-016CT0003 → B212-016CT0004 → B212-996CT0021 → M0304 → D0304-L31 → M0303 → D0303-L37 → M0302 → B261-006BC0004 → B261-007BC0001 → B261-006BC0023 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MYB17GF010 -X01 (701, 702, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 13
22BFA03.CB002 | -P20 | 03 |  | PE-L1-3C4-22 | PE-L1-3C4-22 | GT#2-2-22MBA18AA002 -Y01 |  |  | 1 | 2000 | 22BFA03.CB002-P2003 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-22 | 0.073 | 230 | N | 120 | GT PKG | 22BFA03.CB002 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, N, PE | 22MBA18AA002 -Y01 | DRN-VLV 2 FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, N, PE | B212-016CT0001 → B212-016CT0002 → B212-016CT0003 → B212-016CT0004 → B212-996CT0021 → M0304 → D0304-L31 → M0303 → D0303-L37 → M0302 → B261-006BC0004 → B261-007BC0001 → B261-006BC0023 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MYB17GF010 -X01 (703, 704, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 13
22BFA03.CB003 | -P20 | 04 |  | PE-L1-3C4-22 | PE-L1-3C4-22 | GT#2-2-22MBA18AA003 -Y01 |  |  | 1 | 2001 | 22BFA03.CB003-P2004 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-22 | 0.073 | 230 | N | 120 | GT PKG | 22BFA03.CB003 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, N, PE | 22MBA18AA003 -Y01 | DRN-VLV 3 FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, N, PE | B212-016CT0001 → B212-016CT0002 → B212-016CT0003 → B212-016CT0004 → B212-996CT0021 → M0304 → D0304-L31 → M0303 → D0303-L37 → M0302 → B261-006BC0004 → B261-007BC0001 → B261-006BC0023 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MYB17GF010 -X01 (705, 706, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 13
22BFA02.CB001 | -P20 | 05 |  | PE-L1-4C4-23 | PE-L1-4C4-23 | GT#2-2-22MBA30AP001 -M01 |  |  | 1 | 2002 | 22BFA02.CB001-P2005 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-23 | 4.9 | 400 | N | 120 | GT PKG | 22BFA02.CB001 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, L2, L3, PE | 22MBA30AP001 -M01 | MXG-PP | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, L2, L3, PE | B212-016CT0001 → B212-016CT0002 → B212-016CT0003 → B212-016CT0004 → B212-996CT0021 → M0304 → D0304-L21 → M0303 → D0303-L27 → M0302 → B261-006BC0002 → B261-017BC0112 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
22BFA02.EA003 | -P20 | 06 |  | PE-L1-3C4-22 | PE-L1-3C4-22 | GT#2-2-22MBA32AP001 -M01 |  |  | 1 | 2003 | 22BFA02.EA003-P2006 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-22 | 0.5 | 230 | N | 120 | GT PKG | 22BFA02.EA003 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, N, PE | 22MBA32AP001 -M01 | CLNG-AGT-PP | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, N, PE | B212-016CT0001 → B212-016CT0002 → B212-016CT0003 → B212-016CT0004 → B212-996CT0021 → M0304 → D0304-L21 → M0303 → D0303-L27 → M0302 → B261-006DC0002 → B261-017BC0113 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
22BFA53.DA002 | -P20 | 07 |  | PE-L1-3C4-22 | PE-L1-3C4-22 | GT#2-2-22MBA32GQ012 -X01 |  |  | 1 | 2004 | 22BFA53.DA002-P2007 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-22 | 0.5 | 230 | N | 120 | GT PKG | 22BFA53.DA002 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, N, PE | 22MBA32GQ012 -X01 | EL-SCKT JUNCT-BOX | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, N, PE | B212-016CT0001 → B212-016CT0002 → B212-016CT0003 → B212-016CT0004 → B212-996CT0021 → M0304 → D0304-L21 → M0303 → D0303-L27 → M0302 → B261-006DC0002 → B261-017BC0114 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
22BFA02.EA004 | -P20 | 08 |  | PE-L1-3C4-22 | PE-L1-3C4-22 | GT#2-2-22MBA33AP001 -M01 |  |  | 1 | 2005 | 22BFA02.EA004-P2008 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-22 | 0.5 | 230 | N | 120 | GT PKG | 22BFA02.EA004 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, N, PE | 22MBA33AP001 -M01 | ANTIFRZ-AGT-PP | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, N, PE | B212-016CT0001 → B212-016CT0002 → B212-016CT0003 → B212-016CT0004 → B212-996CT0021 → M0304 → D0304-L21 → M0303 → D0303-L27 → M0302 → B261-006DC0002 → B261-017BC0115 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
22BFA02.CB002 | -P20 | 09 |  | PE-L1-4C4-23 | PE-L1-4C4-23 | GT#2-2-22MBA51AP001 -M01 |  |  | 1 | 2006 | 22BFA02.CB002-P2009 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-23 | 2.2 | 400 | N | 50 | GT PKG | 22BFA02.CB002 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, L2, L3, PE | 22MBA51AP001 -M01 | HYDRC-PP 1 HCO | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, L2, L3, PE | B212-016DT0001 → B212-016DT0002 → B212-016DT0012 → B212-996DT0026 → B261-016BC0117 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
22BFA02.CB003 | -P20 | 10 |  | PE-L1-4C4-23 | PE-L1-4C4-23 | GT#2-2-22MBA51AP002 -M01 |  |  | 1 | 2007 | 22BFA02.CB003-P2010 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-23 | 2.2 | 400 | N | 60 | GT PKG | 22BFA02.CB003 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, L2, L3, PE | 22MBA51AP002 -M01 | HYDRC-PP 2 HCO | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, L2, L3, PE | B212-016DT0025 → B212-016DT0007 → B212-016DT0008 → B212-016DT0009 → B212-016DT0010 → B212-016DT0002 → B212-016DT0012 → B212-996DT0026 → B261-016BC0118 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
22CJT91 (22MBJ01GS091 -E01) | -P10 | 01 |  | PE-M3-1C240-03 | PE-M1-1C240-11 | GT#2-2-22MBJ01GS091 -E01 |  |  | 1 | 2008 | 22CJT0001 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-11 |  | 1400 | N | 60 | GT PKG | 22CJT91 (22MBJ01GS091 -E01) | GTG #22 SFC CABINET (GTG #22 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | U1 | B2-CB-12301 | BLOCK #2 GENERATOR CIRCUIT BREAKER FOR GT#2 | 1.1_MAIN BUILDING COMPLEX / GT #22 | U1 | B261-013BC0001 → B261-003BC0007 → M0303 → D0304-M11 → M0304 → B212-993BT0022 → B212-013BT0025 → B212-013BT0007 → B212-013BT0008 → B212-013BT0009 → B212-013BT0010 → B212-013BT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
22CJT91 (22MBJ01GS091 -E01) | -P10 | 02 |  | PE-M3-1C240-03 | PE-M1-1C240-11 | GT#2-2 |  |  | 1 | 2009 | 22CJT0004 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-11 |  | 1400 | N | 60 | GT PKG | 22CJT91 (22MBJ01GS091 -E01) | GTG #22 SFC CABINET (GTG #22 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | V1 | B2-CB-12301 | BLOCK #2 GENERATOR CIRCUIT BREAKER FOR GT#2 | 1.1_MAIN BUILDING COMPLEX / GT #22 | V1 | B261-013BC0001 → B261-003BC0007 → M0303 → D0304-M11 → M0304 → B212-993BT0022 → B212-013BT0025 → B212-013BT0007 → B212-013BT0008 → B212-013BT0009 → B212-013BT0010 → B212-013BT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
22CJT91 (22MBJ01GS091 -E01) | -P10 | 03 |  | PE-M3-1C240-03 | PE-M1-1C240-11 | GT#2-2 |  |  | 1 | 2010 | 22CJT0007 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-11 |  | 1400 | N | 60 | GT PKG | 22CJT91 (22MBJ01GS091 -E01) | GTG #22 SFC CABINET (GTG #22 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | W1 | B2-CB-12301 | BLOCK #2 GENERATOR CIRCUIT BREAKER FOR GT#2 | 1.1_MAIN BUILDING COMPLEX / GT #22 | W1 | B261-013BC0001 → B261-003BC0007 → M0303 → D0304-M11 → M0304 → B212-993BT0022 → B212-013BT0025 → B212-013BT0007 → B212-013BT0008 → B212-013BT0009 → B212-013BT0010 → B212-013BT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
22CJT91 (22MBJ01GS091 -E01) | -P10 | 04 |  | PE-M3-1C240-04 | PE-M1-1C240-12 | GT#2-2 |  |  | 1 | 2011 | 22CJT0002 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-12 |  | 1400 | N | 60 | GT PKG | 22CJT91 (22MBJ01GS091 -E01) | GTG #22 SFC CABINET (GTG #22 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | U1 | B2-CB-12301 | BLOCK #2 GENERATOR CIRCUIT BREAKER FOR GT#2 | 1.1_MAIN BUILDING COMPLEX / GT #22 | U1 | B261-013BC0002 → B261-003BC0008 → M0303 → D0304-M12 → M0304 → B212-993BT0022 → B212-013BT0025 → B212-013BT0007 → B212-013BT0008 → B212-013BT0009 → B212-013BT0010 → B212-013BT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
22CJT91 (22MBJ01GS091 -E01) | -P10 | 05 |  | PE-M3-1C240-04 | PE-M1-1C240-12 | GT#2-2 |  |  | 1 | 2012 | 22CJT0005 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-12 |  | 1400 | N | 60 | GT PKG | 22CJT91 (22MBJ01GS091 -E01) | GTG #22 SFC CABINET (GTG #22 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | V1 | B2-CB-12301 | BLOCK #2 GENERATOR CIRCUIT BREAKER FOR GT#2 | 1.1_MAIN BUILDING COMPLEX / GT #22 | V1 | B261-013BC0002 → B261-003BC0008 → M0303 → D0304-M12 → M0304 → B212-993BT0022 → B212-013BT0025 → B212-013BT0007 → B212-013BT0008 → B212-013BT0009 → B212-013BT0010 → B212-013BT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
22CJT91 (22MBJ01GS091 -E01) | -P10 | 06 |  | PE-M3-1C240-04 | PE-M1-1C240-12 | GT#2-2 |  |  | 1 | 2013 | 22CJT0008 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-12 |  | 1400 | N | 60 | GT PKG | 22CJT91 (22MBJ01GS091 -E01) | GTG #22 SFC CABINET (GTG #22 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | W1 | B2-CB-12301 | BLOCK #2 GENERATOR CIRCUIT BREAKER FOR GT#2 | 1.1_MAIN BUILDING COMPLEX / GT #22 | W1 | B261-013BC0002 → B261-003BC0008 → M0303 → D0304-M12 → M0304 → B212-993BT0022 → B212-013BT0025 → B212-013BT0007 → B212-013BT0008 → B212-013BT0009 → B212-013BT0010 → B212-013BT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
22CJT91 (22MBJ01GS091 -E01) | -P10 | 07 |  | PE-M3-1C240-04 | PE-M1-1C240-12 | GT#2-2 |  |  | 1 | 2014 | 22CJT0003 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-12 |  | 1400 | N | 60 | GT PKG | 22CJT91 (22MBJ01GS091 -E01) | GTG #22 SFC CABINET (GTG #22 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | U1 | B2-CB-12301 | BLOCK #2 GENERATOR CIRCUIT BREAKER FOR GT#2 | 1.1_MAIN BUILDING COMPLEX / GT #22 | U1 | B261-013BC0003 → B261-003BC0009 → M0303 → D0304-M13 → M0304 → B212-993BT0022 → B212-013BT0025 → B212-013BT0007 → B212-013BT0008 → B212-013BT0009 → B212-013BT0010 → B212-013BT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
22CJT91 (22MBJ01GS091 -E01) | -P10 | 08 |  | PE-M3-1C240-04 | PE-M1-1C240-12 | GT#2-2 |  |  | 1 | 2015 | 22CJT0006 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-12 |  | 1400 | N | 60 | GT PKG | 22CJT91 (22MBJ01GS091 -E01) | GTG #22 SFC CABINET (GTG #22 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | V1 | B2-CB-12301 | BLOCK #2 GENERATOR CIRCUIT BREAKER FOR GT#2 | 1.1_MAIN BUILDING COMPLEX / GT #22 | V1 | B261-013BC0003 → B261-003BC0009 → M0303 → D0304-M13 → M0304 → B212-993BT0022 → B212-013BT0025 → B212-013BT0007 → B212-013BT0008 → B212-013BT0009 → B212-013BT0010 → B212-013BT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
22CJT91 (22MBJ01GS091 -E01) | -P10 | 09 |  | PE-M3-1C240-05 | PE-M1-1C240-12 | GT#2-2 |  |  | 1 | 2016 | 22CJT0009 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-12 |  | 1400 | N | 60 | GT PKG | 22CJT91 (22MBJ01GS091 -E01) | GTG #22 SFC CABINET (GTG #22 SUFC EXTL ISOLR) | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | W1 | B2-CB-12301 | BLOCK #2 GENERATOR CIRCUIT BREAKER FOR GT#2 | 1.1_MAIN BUILDING COMPLEX / GT #22 | W1 | B261-013BC0003 → B261-003BC0009 → M0303 → D0304-M13 → M0304 → B212-993BT0022 → B212-013BT0025 → B212-013BT0007 → B212-013BT0008 → B212-013BT0009 → B212-013BT0010 → B212-013BT0001 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
22MBJ01GT002 -E01 | -P10 | 01 |  | PE-M3-1C240-05 | PE-M1-1C240-13 | GT#2-2-22MBJ01GT002 -E01 |  |  | 1 | 2017 | 22MBJ0001 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-13 |  | 1400 | N | 35 | GT PKG | 22MBJ01GT002 -E01 | GTG #22 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #22 | U1 | 22CJT91 | GTG #22 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | U1 | B261-003BC0003 → M0304 → B212-993BT0021 → B212-013BT0004 → B212-013BT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
22MBJ01GT002 -E01 | -P10 | 02 |  | PE-M3-1C240-05 | PE-M1-1C240-13 | GT#2-2 |  |  | 1 | 2018 | 22MBJ0004 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-13 |  | 1400 | N | 35 | GT PKG | 22MBJ01GT002 -E01 | GTG #22 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #22 | V1 | 22CJT91 | GTG #22 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | V1 | B261-003BC0003 → M0304 → B212-993BT0021 → B212-013BT0004 → B212-013BT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
22MBJ01GT002 -E01 | -P10 | 03 |  | PE-M3-1C240-05 | PE-M1-1C240-13 | GT#2-2 |  |  | 1 | 2019 | 22MBJ0007 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-13 |  | 1400 | N | 35 | GT PKG | 22MBJ01GT002 -E01 | GTG #22 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #22 | W1 | 22CJT91 | GTG #22 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | W1 | B261-003BC0003 → M0304 → B212-993BT0021 → B212-013BT0004 → B212-013BT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
22MBJ01GT002 -E01 | -P10 | 04 |  | PE-M3-1C240-05 | PE-M1-1C240-13 | GT#2-2 |  |  | 1 | 2020 | 22MBJ0002 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-13 |  | 1400 | N | 35 | GT PKG | 22MBJ01GT002 -E01 | GTG #22 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #22 | U1 | 22CJT91 | GTG #22 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | U1 | B261-003BC0004 → M0304 → B212-993BT0021 → B212-013BT0004 → B212-013BT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
22MBJ01GT002 -E01 | -P10 | 05 |  | PE-M3-1C240-05 | PE-M1-1C240-13 | GT#2-2 |  |  | 1 | 2021 | 22MBJ0005 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-13 |  | 1400 | N | 35 | GT PKG | 22MBJ01GT002 -E01 | GTG #22 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #22 | V1 | 22CJT91 | GTG #22 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | V1 | B261-003BC0004 → M0304 → B212-993BT0021 → B212-013BT0004 → B212-013BT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
22MBJ01GT002 -E01 | -P10 | 06 |  | PE-M3-1C240-05 | PE-M1-1C240-13 | GT#2-2 |  |  | 1 | 2022 | 22MBJ0008 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-13 |  | 1400 | N | 35 | GT PKG | 22MBJ01GT002 -E01 | GTG #22 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #22 | W1 | 22CJT91 | GTG #22 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | W1 | B261-003BC0004 → M0304 → B212-993BT0021 → B212-013BT0004 → B212-013BT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
22MBJ01GT002 -E01 | -P10 | 07 |  | PE-M3-1C240-05 | PE-M1-1C240-13 | GT#2-2 |  |  | 1 | 2023 | 22MBJ0003 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-13 |  | 1400 | N | 35 | GT PKG | 22MBJ01GT002 -E01 | GTG #22 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #22 | U1 | 22CJT91 | GTG #22 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | U1 | B261-003BC0005 → M0304 → B212-993BT0021 → B212-013BT0004 → B212-013BT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
22MBJ01GT002 -E01 | -P10 | 08 |  | PE-M3-1C240-05 | PE-M1-1C240-13 | GT#2-2 |  |  | 1 | 2024 | 22MBJ0006 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-13 |  | 1400 | N | 35 | GT PKG | 22MBJ01GT002 -E01 | GTG #22 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #22 | V1 | 22CJT91 | GTG #22 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | V1 | B261-003BC0005 → M0304 → B212-993BT0021 → B212-013BT0004 → B212-013BT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
22MBJ01GT002 -E01 | -P10 | 09 |  | PE-M3-1C240-05 | PE-M1-1C240-13 | GT#2-2 |  |  | 1 | 2025 | 22MBJ0009 | 6/10kV CU/XLPE/CTS/LSZH | 1C x 240sqmm | PE-M1-1C240-13 |  | 1400 | N | 35 | GT PKG | 22MBJ01GT002 -E01 | GTG #22 LV-SIDE SUFC TFR | 1.1_MAIN BUILDING COMPLEX / GT #22 | W1 | 22CJT91 | GTG #22 SFC CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | W1 | B261-003BC0005 → M0304 → B212-993BT0021 → B212-013BT0004 → B212-013BT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 33 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1 |  | 2 | EPKT-17C1XI-G57
22BFA52.DA001 | -P20 | 11 |  | PE-L1-3C4-22 | PE-L1-3C4-22 | GT#2-2-22MBJ01GW035 -E01 |  |  | 1 | 2026 | 22BFA52.DA001-P2011 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-22 | 1.2 | 230 | N | 40 | GT PKG | 22BFA52.DA001 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, N, PE | 22MBJ01GW035 -E01 | MBJ 1AC AUX-VOLT SUP | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, N, PE | B212-013BT0001 → B212-013BT0002 → B212-013BT0003 → B212-013BT0004 → B212-993BT0021 → M0304 → B261-007BC0010 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
22BFA53.HA002 | -P20 | 12 |  | PE-L1-5C6-02 | PE-L1-5C6-02 | GT#2-2-22MBL10GH001 -E01 |  |  | 1 | 2027 | 22BFA53.HA002-P2012 | 0.6/1kV CU/XLPE/LSZH | 5C x 6sqmm | PE-L1-5C6-02 | 15 | 400 | N | 170 | GT PKG | 22BFA53.HA002 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, L2, L3, N, PE | 22MBL10GH001 -E01 | CABINET AIR INTAKE | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, L2, L3, N, PE | B212-013BT0001 → B212-013BT0002 → B212-013BT0003 → B212-013BT0004 → B212-993BT0021 → M0304 → D0304-L21 → M0303 → B261-006BC0025 → B261-026EC0006 → B261-026EC0004 → B261-026EC0003 → B261-026EC0001 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MBL10GH001 -X01 (001, 002, 003, 004, 005) | 1 | A2F-S-25a-N34 | 16 - 20.5 | 17
22BFA53.HA003 | -P20 | 13 |  | PE-L1-5C6-02 | PE-L1-5C6-02 | GT#2-2-22MBL20GH001 -E01 |  |  | 1 | 2028 | 22BFA53.HA003-P2013 | 0.6/1kV CU/XLPE/LSZH | 5C x 6sqmm | PE-L1-5C6-02 | 11 | 400 | N | 120 | GT PKG | 22BFA53.HA003 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, L2, L3, N, PE | 22MBL20GH001 -E01 | CAB AIR-INTK-FLP | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, L2, L3, N, PE | B212-013BT0001 → B212-013BT0002 → B212-013BT0003 → B212-013BT0004 → B212-993BT0021 → M0304 → D0304-L24 → M0303 → D0303-L35 → M0302 → B261-006BC0004 → B261-016BC0101 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MBL20GH001 -X01 (001, 002, 003, 004, 005) | 1 | A2F-S-25a-N34 | 16 - 20.5 | 17
22BFA51.HA001 | -P20 | 14 |  | PE-L1-5C4-02 | PE-L1-5C4-02 | GT#2-2-22MBL25AT001 -E01 |  |  | 1 | 2029 | 22BFA51.HA001-P2014 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-02 | 5.2 | 400 | N | 110 | GT PKG | 22BFA51.HA001 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, L2, L3, N, PE | 22MBL25AT001 -E01 | STANDSTL AIR DEHUMI | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, L2, L3, N, PE | B212-013BT0001 → B212-013BT0002 → B212-013BT0003 → B212-013BT0004 → B212-993BT0021 → M0304 → D0304-L24 → M0303 → D0303-L35 → M0302 → B261-006BC0005 → B261-007BC0001 → END | B212-013BT0001 → B212-013BT0002 → B212-013BT0003 → B212-013BT0004 → B212-993BT0021 → M0304 → D0304-L24 → M0303 → D0303-L33 → M0302 → B261-006BC0006 → B261-016BC0103 → END | 1 | A2F-S-25-N34 | 12 - 18 | 15
22BFA03.JB001 | -P20 | 15 |  | PE-L1-5C25/16-02 | PE-L1-5C25/16-02 | GT#2-2-22MBL30GH001 -E01 |  |  | 1 | 2030 | 22BFA03.JB001-P2015 | 0.6/1kV CU/XLPE/LSZH | 4C x 25sqmm + 1C X 16sqmm | PE-L1-5C25/16-02 | 40 | 400 | N | 85 | GT PKG | 22BFA03.JB001 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, L2, L3, N, PE | 22MBL30GH001 -E01 | CAB PULS-AIR | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, L2, L3, N, PE | B212-013BT0001 → B212-013BT0002 → B212-013BT0003 → B212-013BT0004 → B212-993BT0021 → M0304 → D0304-L21 → M0303 → D0303-L35 → M0302 → B261-006BC0007 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MBL30GH001 -X01 (001, 002, 003, 004, 005) | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5
22BFA53.HA004 | -P20 | 16 |  | PE-L1-5C6-02 | PE-L1-5C6-02 | GT#2-2-22MBL40GH001 -E01 |  |  | 1 | 2031 | 22BFA53.HA004-P2016 | 0.6/1kV CU/XLPE/LSZH | 5C x 6sqmm | PE-L1-5C6-02 | 18 | 400 | N | 110 | GT PKG | 22BFA53.HA004 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, L2, L3, N, PE | 22MBL40GH001 -E01 | CAB EVAP COOL | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, L2, L3, N, PE | B212-013BT0001 → B212-013BT0002 → B212-013BT0003 → B212-013BT0004 → B212-993BT0021 → M0304 → D0304-L24 → M0303 → D0303-L33 → M0302 → B261-006BC0006 → B161-016BC0103 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MBL40GH001 -X01 (001, 002, 003, 004, 005) | 1 | A2F-S-25a-N34 | 16 - 20.5 | 17
22BFA03.CB004 | -P20 | 17 |  | PE-L1-3C4-24 | PE-L1-3C4-24 | GT#2-2-22MBM12GT100 -E01 |  |  | 1 | 2032 | 22BFA03.CB004-P2017 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-24 | 1.6 | 230 | N | 120 | GT PKG | 22BFA03.CB004 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, N, PE | 22MBM12GT100 -E01 | IGNITION TRANSFORMERS | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, N, PE | B212-016CT0001 → B212-016CT0002 → B212-016CT0003 → B212-016CT0004 → B212-996CT0021 → M0304 → D0304-L23 → M0303 → D0303-L32 → M0302 → B261-006BC0005 → B261-006BC0003 → B261-017BC0103 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MYB30GF202 -X03 | 1 | A2F-S-25-N34 | 12 - 18 | 13
22BUA01.EA001 | -P20 | 18 |  | PE-L1-2C4-07 | PE-L1-2C4-07 | GT#2-2-22MBN12AA505 -Y01 |  |  | 1 | 2033 | 22BUA01.EA001-P2018 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-07 | 0.055 | 220 | D | 90 | GT PKG | 22BUA01.EA001 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L+, L- | 22MBN12AA505 -Y01 | RL-VLV FEED FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #22 | L+, L- | B212-016CT0001 → B212-016CT0010 → B212-016CT0009 → B212-016CT0008 → B212-016CT0007 → B212-016CT0024 → B212-996CT0023 → M0305 → B261-006BC0014 → B261-017BC0132 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MBY08GF001 -X04 (401, 402) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
22BUA01.EA002 | -P20 | 19 |  | PE-L1-2C4-07 | PE-L1-2C4-07 | GT#2-2-22MBN13AA501 -Y01 |  |  | 1 | 2034 | 22BUA01.EA002-P2019 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-07 | 0.048 | 220 | D | 80 | GT PKG | 22BUA01.EA002 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L+, L- | 22MBN13AA501 -Y01 | STOP-VLV FUEL OIL SUPPLY | 1.1_MAIN BUILDING COMPLEX / GT #22 | L+, L- | B212-016CT0001 → B212-016CT0010 → B212-016CT0009 → B212-016CT0008 → B212-016CT0007 → B212-016CT0024 → B212-996CT0023 → M0305 → B261-006BC0014 → B261-017BC0133 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MYB30GF010 -X03 (403, 404) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
22BUA01.EA003 | -P20 | 20 |  | PE-L1-2C4-07 | PE-L1-2C4-07 | GT#2-2-22MBN13AA502 -Y01 |  |  | 1 | 2035 | 22BUA01.EA003-P2020 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-07 | 0.048 | 220 | D | 80 | GT PKG | 22BUA01.EA003 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L+, L- | 22MBN13AA502 -Y01 | RL-VLV RETN DIFFU FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #22 | L+, L- | B212-016CT0001 → B212-016CT0010 → B212-016CT0009 → B212-016CT0008 → B212-016CT0007 → B212-016CT0024 → B212-996CT0023 → M0305 → B261-006BC0014 → B261-017BC0134 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MYB30GF010 -X03 (401, 402) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
22BUA51.JA001 | -P20 | 21 |  | PE-L1-5C4-03 | PE-L1-5C4-03 | GT#2-2-22MBN21AA001 -Y02 |  |  | 1 | 2036 | 22BUA51.JA001-P2021 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-03 | 0.13 | 220 | D | 120 | GT PKG | 22BUA51.JA001 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 22MBN21AA001 -Y02 | BLL-VLV ASSY LFT FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #22 | RL, LL, L-, BR, PE | B212-016CT0001 → B212-016CT0002 → B212-016CT0003 → B212-016CT0004 → B212-996CT0021 → M0304 → D0304-L23 → M0303 → D0303-L32 → M0302 → B261-006BC0005 → B261-006BC0003 → B261-017BC0104 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 15
22BUA01.EA004 | -P20 | 22 |  | PE-L1-2C4-09 | PE-L1-2C4-09 | GT#2-2-22MBN21AA002 -Y01 |  |  | 1 | 2037 | 22BUA01.EA004-P2022 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-09 | 0.048 | 220 | D | 120 | GT PKG | 22BUA01.EA004 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L+, L- | 22MBN21AA002 -Y01 | BYP-VLV LFT FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #22 | L+, L- | B212-016CT0001 → B212-016CT0002 → B212-016CT0003 → B212-016CT0004 → B212-996CT0021 → M0304 → D0304-L23 → M0303 → D0303-L32 → M0302 → B261-006BC0005 → B261-006BC0003 → B261-017BC0105 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MYB30GF102 -X03 (429, 430) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
22BUA51.KB001 | -P20 | 23 |  | PE-L1-5C4-03 | PE-L1-5C4-03 | GT#2-2-22MBN22AA001 -Y02 |  |  | 1 | 2038 | 22BUA51.KB001-P2023 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-03 | 0.13 | 220 | D | 120 | GT PKG | 22BUA51.KB001 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 22MBN22AA001 -Y02 | BLL-VLV ASSY RGHT FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #22 | RL, LL, L-, BR, PE | B212-016CT0001 → B212-016CT0002 → B212-016CT0003 → B212-016CT0004 → B212-996CT0021 → M0304 → D0304-L23 → M0303 → D0303-L32 → M0302 → B261-006BC0005 → B261-006BC0003 → B261-017BC0106 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 15
22BUA01.FB001 | -P20 | 24 |  | PE-L1-2C4-09 | PE-L1-2C4-09 | GT#2-2-22MBN22AA002 -Y01 |  |  | 1 | 2039 | 22BUA01.FB001-P2024 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-09 | 0.048 | 220 | D | 120 | GT PKG | 22BUA01.FB001 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L+, L- | 22MBN22AA002 -Y01 | BYP-VLV RGHT FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #22 | L+, L- | B212-016CT0001 → B212-016CT0002 → B212-016CT0003 → B212-016CT0004 → B212-996CT0021 → M0304 → D0304-L23 → M0303 → D0303-L32 → M0302 → B261-006BC0005 → B261-006BC0003 → B261-017BC0107 → END | SWGR to J/B : Doosan J/B to consumer : SE 21MYB30GF202 -X03 (429, 430) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
22BUA01.FB002 | -P20 | 25 |  | PE-L1-2C4-09 | PE-L1-2C4-09 | GT#2-2-22MBN23AA501 -Y01 |  |  | 1 | 2040 | 22BUA01.FB002-P2025 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-09 | 0.048 | 220 | D | 120 | GT PKG | 22BUA01.FB002 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L+, L- | 22MBN23AA501 -Y01 | DRN-VLV FEED PREM FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #22 | L+, L- | B212-016CT0001 → B212-016CT0002 → B212-016CT0003 → B212-016CT0004 → B212-996CT0021 → M0304 → D0304-L23 → M0303 → D0303-L32 → M0302 → B261-006BC0005 → B261-006BC0003 → B261-017BC0108 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MYB30GF010 -X03 (405, 406) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
22BUA51.MA001 | -P20 | 26 |  | PE-L1-5C4-03 | PE-L1-5C4-03 | GT#2-2-22MBN25AA001 -Y02 |  |  | 1 | 2041 | 22BUA51.MA001-P2026 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-03 | 0.13 | 220 | D | 120 | GT PKG | 22BUA51.MA001 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 22MBN25AA001 -Y02 | BLL-VLV PREM LFT FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #22 | RL, LL, L-, BR, PE | B212-016CT0001 → B212-016CT0002 → B212-016CT0003 → B212-016CT0004 → B212-996CT0021 → M0304 → D0304-L23 → M0303 → D0303-L32 → M0302 → B261-006BC0005 → B261-006BC0003 → B261-017BC0109 → END | SWGR to J/B : Doosan J/B to consumer : SE 11MYB30GF102 -X03 (401, 402, 403, 404, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
22BUA01.FB003 | -P20 | 27 |  | PE-L1-2C4-09 | PE-L1-2C4-09 | GT#2-2-22MBN25AA501 -Y01 |  |  | 1 | 2042 | 22BUA01.FB003-P2027 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-09 | 0.053 | 220 | D | 120 | GT PKG | 22BUA01.FB003 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L+, L- | 22MBN25AA501 -Y01 | FIL-VLV PREM LFT FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #22 | L+, L- | B212-016CT0001 → B212-016CT0002 → B212-016CT0003 → B212-016CT0004 → B212-996CT0021 → M0304 → D0304-L23 → M0303 → D0303-L32 → M0302 → B261-006BC0005 → B261-006BC0003 → B261-017BC0110 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MYB30GF102 -X03 (701, 702) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
22BUA51.NB001 | -P20 | 28 |  | PE-L1-5C4-03 | PE-L1-5C4-03 | GT#2-2-22MBN26AA001 -Y02 |  |  | 1 | 2043 | 22BUA51.NB001-P2028 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-03 | 0.13 | 220 | D | 120 | GT PKG | 22BUA51.NB001 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 22MBN26AA001 -Y02 | BLL-VLV PREM RGHT FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #22 | RL, LL, L-, BR, PE | B212-016CT0001 → B212-016CT0002 → B212-016CT0003 → B212-016CT0004 → B212-996CT0021 → M0304 → D0304-L23 → M0303 → D0303-L32 → M0302 → B261-006BC0005 → B261-006BC0003 → B261-017BC0111 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MYB30GF202 -X03 (401, 402, 403, 404, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
22BUA01.FB004 | -P20 | 29 |  | PE-L1-2C4-09 | PE-L1-2C4-09 | GT#2-2-22MBN26AA501 -Y01 |  |  | 1 | 2044 | 22BUA01.FB004-P2029 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-09 | 0.053 | 220 | D | 70 | GT PKG | 22BUA01.FB004 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L+, L- | 22MBN26AA501 -Y01 | FIL-VLV PREM RGHT FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #22 | L+, L- | B212-016CT0001 → B212-016CT0010 → B212-016CT0009 → B212-016CT0015 → B212-016CT0016 → B261-017BC0006 → B261-017BC0116 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MYB30GF202 -X03 (701, 702) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
22BUA01.HA001 | -P20 | 30 |  | PE-L1-2C4-09 | PE-L1-2C4-09 | GT#2-2-22MBN27AA501 -Y01 |  |  | 1 | 2045 | 22BUA01.HA001-P2030 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-09 | 0.048 | 220 | D | 70 | GT PKG | 22BUA01.HA001 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L+, L- | 22MBN27AA501 -Y01 | LKG VLV PREM FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #22 | L+, L- | B212-016CT0001 → B212-016CT0010 → B212-016CT0009 → B212-016CT0015 → B212-016CT0016 → B261-017BC0006 → B261-017BC0117 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MYB30GF010 -X03 (407, 408) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
22BFA02.CB004 | -P20 | 31 |  | PE-L1-4C4-23 | PE-L1-4C4-23 | GT#2-2-22MBN60AP001 -M01 |  |  | 1 | 2046 | 22BFA02.CB004-P2031 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-23 | 1.1 | 400 | N | 80 | GT PKG | 22BFA02.CB004 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, L2, L3, PE | 22MBN60AP001 -M01 | DRNG PP AUX-TNK 1 FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, L2, L3, PE | B212-016CT0001 → B212-016CT0010 → B212-016CT0009 → B212-016CT0008 → B212-016CT0007 → B212-016CT0024 → B212-996CT0023 → M0305 → B261-006BC0014 → B261-016BC0105 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
22BFA03.EA003 | -P20 | 32 |  | PE-L1-4C6-02 | PE-L1-4C6-02 | GT#2-2-22MBN81AP001 -M01 |  |  | 1 | 2047 | 22BFA03.EA003-P2032 | 0.6/1kV CU/XLPE/LSZH | 4C x 6sqmm | PE-L1-4C6-02 | 11 | 400 | N | 80 | GT PKG | 22BFA03.EA003 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, L2, L3, PE | 22MBN81AP001 -M01 | PP FLUSH-WTR FU-OIL | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, L2, L3, PE | B212-016CT0001 → B212-016CT0010 → B212-016CT0009 → B212-016CT0008 → B212-016CT0007 → B212-016CT0024 → B212-996CT0023 → M0305 → B261-006BC0014 → B261-016BC0106 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 15.5
22BUA01.HA002 | -P20 | 33 |  | PE-L1-2C4-08 | PE-L1-2C4-08 | GT#2-2-22MBN82AA001 -Y01 |  |  | 1 | 2048 | 22BUA01.HA002-P2033 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-08 | 0.078 | 220 | D | 90 | GT PKG | 22BUA01.HA002 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L+, L- | 22MBN82AA001 -Y01 | FLUSHING WATER VALVE 1 | 1.1_MAIN BUILDING COMPLEX / GT #22 | L+, L- | B212-016CT0001 → B212-016CT0010 → B212-016CT0009 → B212-016CT0008 → B212-016CT0007 → B212-016CT0024 → B212-996CT0023 → M0305 → B261-006BC0014 → B261-017BC0135 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MBY11GF001 -X01 (401, 402) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
22BUA01.HA003 | -P20 | 34 |  | PE-L1-2C4-08 | PE-L1-2C4-08 | GT#2-2-22MBN82AA002 -Y01 |  |  | 1 | 2049 | 22BUA01.HA003-P2034 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-08 | 0.078 | 220 | D | 90 | GT PKG | 22BUA01.HA003 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L+, L- | 22MBN82AA002 -Y01 | FLUSHING WATER VALVE 2 | 1.1_MAIN BUILDING COMPLEX / GT #22 | L+, L- | B212-016CT0001 → B212-016CT0010 → B212-016CT0009 → B212-016CT0008 → B212-016CT0007 → B212-016CT0024 → B212-996CT0023 → M0305 → B261-006BC0014 → B261-017BC0136 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MBY11GF001 -X01 (403, 404) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
22BUB01.EA001 | -P20 | 35 |  | PE-L1-2C4-08 | PE-L1-2C4-08 | GT#2-2-22MBP13AA501 -Y01 |  |  | 1 | 2050 | 22BUB01.EA001-P2035 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-08 | 0.205 | 220 | D | 40 | GT PKG | 22BUB01.EA001 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L+, L- | 22MBP13AA501 -Y01 | VENT-VLV MN SUP NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #22 | L+, L- | B212-016DT0001 → B212-016DT0002 → B212-016DT0012 → B212-996DT0026 → B261-017BC0137 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MBY09GF001 -X02 (401, 402) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
22BUB01.EA002 | -P20 | 36 |  | PE-L1-2C4-08 | PE-L1-2C4-08 | GT#2-2-22MBP14AA501 -Y01 |  |  | 1 | 2051 | 22BUB01.EA002-P2036 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-08 | 0.205 | 220 | D | 40 | GT PKG | 22BUB01.EA002 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L+, L- | 22MBP14AA501 -Y01 | SOL-VLV VENTG NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #22 | L+, L- | B212-016DT0001 → B212-016DT0002 → B212-016DT0012 → B212-996DT0026 → B261-017BC0138 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MBY09GF001 -X02 (403, 404) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
22BUB01.EA003 | -P20 | 37 |  | PE-L1-2C4-08 | PE-L1-2C4-08 | GT#2-2-22MBP15AA501 -Y01 |  |  | 1 | 2052 | 22BUB01.EA003-P2037 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-08 | 0.205 | 220 | D | 40 | GT PKG | 22BUB01.EA003 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L+, L- | 22MBP15AA501 -Y01 | VENT-VLV CLD SUP NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #22 | L+, L- | B212-016DT0001 → B212-016DT0002 → B212-016DT0012 → B212-996DT0026 → B261-017BC0139 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MBY09GF001 -X02 (405, 406) | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
22BUB51.JA001 | -P20 | 38 |  | PE-L1-3C4-29 | PE-L1-3C4-29 | GT#2-2-22MBP21AA001 -E01 |  |  | 1 | 2053 | 22BUB51.JA001-P2038 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-29 | 0.008 | 220 | D | 60 | GT PKG | 22BUB51.JA001 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | X19(D3, D4), PE | 22MBP21AA001 -E01 | SO-VLV LFT DIFFU NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #22 | L, N, PE | B212-016CT0001 → B212-016CT0010 → B212-016CT0009 → B212-016CT0015 → B212-016CT0016 → B261-017BC0006 → B261-017BC0118 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MYB30GF102 -X03 (412, 413, 414) | 1 | A2F-S-25-N34 | 12 - 18 | 13
22BUB51.JA001 | -P20 | 39 |  | PE-L1-5C4-03 | PE-L1-5C4-03 | GT#2-2-22MBP21AA001 -Y02 |  |  | 1 | 2054 | 22BUB51.JA001-P2039 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-03 | 0.13 | 220 | D | 60 | GT PKG | 22BUB51.JA001 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 22MBP21AA001 -Y02 | SO-VLV LFT DIFFU NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #22 | RL, LL, L-, BR, PE | B212-016CT0001 → B212-016CT0010 → B212-016CT0009 → B212-016CT0015 → B212-016CT0016 → B261-017BC0006 → B261-017BC0119 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MYB30GF102 -X03 (408, 409, 410, 411, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
22BUB51.KB001 | -P20 | 40 |  | PE-L1-3C4-29 | PE-L1-3C4-29 | GT#2-2-22MBP21AA002 -E01 |  |  | 1 | 2055 | 22BUB51.KB001-P2040 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-29 | 0.008 | 220 | D | 60 | GT PKG | 22BUB51.KB001 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | X19(D3, D4), PE | 22MBP21AA002 -E01 | SO-VLV LFT PREM NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #22 | L, N, PE | B212-016CT0001 → B212-016CT0010 → B212-016CT0009 → B212-016CT0015 → B212-016CT0016 → B261-017BC0006 → B261-017BC0120 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MYB30GF102 -X03 (419, 420, 421) | 1 | A2F-S-25-N34 | 12 - 18 | 13
22BUB51.KB001 | -P20 | 41 |  | PE-L1-5C4-03 | PE-L1-5C4-03 | GT#2-2-22MBP21AA002 -Y02 |  |  | 1 | 2056 | 22BUB51.KB001-P2041 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-03 | 0.13 | 220 | D | 60 | GT PKG | 22BUB51.KB001 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 22MBP21AA002 -Y02 | SO-VLV LFT PREM NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #22 | RL, LL, L-, BR, PE | B212-016CT0001 → B212-016CT0010 → B212-016CT0009 → B212-016CT0015 → B212-016CT0016 → B261-017BC0006 → B261-017BC0121 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MYB30GF102 -X03 (415, 416, 417, 418, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
22BUB51.MA001 | -P20 | 42 |  | PE-L1-3C4-29 | PE-L1-3C4-29 | GT#2-2-22MBP21AA003 -E01 |  |  | 1 | 2057 | 22BUB51.MA001-P2042 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-29 | 0.008 | 220 | D | 60 | GT PKG | 22BUB51.MA001 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | X19(D3, D4), PE | 22MBP21AA003 -E01 | SO-VLV LFT PILOT NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #22 | L, N, PE | B212-016CT0001 → B212-016CT0010 → B212-016CT0009 → B212-016CT0015 → B212-016CT0016 → B261-017BC0006 → B261-017BC0122 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MYB30GF102 -X03 (426, 427, 428) | 1 | A2F-S-25-N34 | 12 - 18 | 13
22BUB51.MA001 | -P20 | 43 |  | PE-L1-5C4-03 | PE-L1-5C4-03 | GT#2-2-22MBP21AA003 -Y02 |  |  | 1 | 2058 | 22BUB51.MA001-P2043 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-03 | 0.13 | 220 | D | 60 | GT PKG | 22BUB51.MA001 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 22MBP21AA003 -Y02 | SO-VLV LFT PILOT NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #22 | RL, LL, L-, BR, PE | B212-016CT0001 → B212-016CT0010 → B212-016CT0009 → B212-016CT0015 → B212-016CT0016 → B261-017BC0006 → B261-017BC0123 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MYB30GF102 -X03 (422, 423, 424, 425, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
22BUB51.NB001 | -P20 | 44 |  | PE-L1-3C4-29 | PE-L1-3C4-29 | GT#2-2-22MBP22AA001 -E01 |  |  | 1 | 2059 | 22BUB51.NB001-P2044 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-29 | 0.008 | 220 | D | 60 | GT PKG | 22BUB51.NB001 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | X19(D3, D4), PE | 22MBP22AA001 -E01 | SO-VLV RGHT DIFFU NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #22 | L, N, PE | B212-016CT0001 → B212-016CT0010 → B212-016CT0009 → B212-016CT0015 → B212-016CT0016 → B261-017BC0006 → B261-017BC0124 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MYB30GF202 -X03 (412, 413, 414) | 1 | A2F-S-25-N34 | 12 - 18 | 13
22BUB51.NB001 | -P20 | 45 |  | PE-L1-5C4-03 | PE-L1-5C4-03 | GT#2-2-22MBP22AA001 -Y02 |  |  | 1 | 2060 | 22BUB51.NB001-P2045 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-03 | 0.13 | 220 | D | 60 | GT PKG | 22BUB51.NB001 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 22MBP22AA001 -Y02 | SO-VLV RGHT DIFFU NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #22 | RL, LL, L-, BR, PE | B212-016CT0001 → B212-016CT0010 → B212-016CT0009 → B212-016CT0015 → B212-016CT0016 → B261-017BC0006 → B261-017BC0125 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MYB30GF202 -X03 (408, 409, 410, 411, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
22BUB51.QA001 | -P20 | 46 |  | PE-L1-3C4-29 | PE-L1-3C4-29 | GT#2-2-22MBP22AA002 -E01 |  |  | 1 | 2061 | 22BUB51.QA001-P2046 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-29 | 0.008 | 220 | D | 60 | GT PKG | 22BUB51.QA001 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | X19(D3, D4), PE | 22MBP22AA002 -E01 | SO-VLV RGHT PREM NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #22 | L, N, PE | B212-016CT0001 → B212-016CT0010 → B212-016CT0009 → B212-016CT0015 → B212-016CT0016 → B261-017BC0006 → B261-017BC0126 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MYB30GF202 -X03 (419, 420, 421) | 1 | A2F-S-25-N34 | 12 - 18 | 13
22BUB51.QA001 | -P20 | 47 |  | PE-L1-5C4-03 | PE-L1-5C4-03 | GT#2-2-22MBP22AA002 -Y02 |  |  | 1 | 2062 | 22BUB51.QA001-P2047 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-03 | 0.13 | 220 | D | 60 | GT PKG | 22BUB51.QA001 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 22MBP22AA002 -Y02 | SO-VLV RGHT PREM NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #22 | RL, LL, L-, BR, PE | B212-016CT0001 → B212-016CT0010 → B212-016CT0009 → B212-016CT0015 → B212-016CT0016 → B261-017BC0006 → B261-017BC0127 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MYB30GF202 -X03 (415, 416, 417, 418, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
22BUB51.RB001 | -P20 | 48 |  | PE-L1-3C4-29 | PE-L1-3C4-29 | GT#2-2-22MBP22AA003 -E01 |  |  | 1 | 2063 | 22BUB51.RB001-P2048 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-29 | 0.008 | 220 | D | 60 | GT PKG | 22BUB51.RB001 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | X19(D3, D4), PE | 22MBP22AA003 -E01 | SO-VLV RGHT PILOT NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #22 | L, N, PE | B212-016CT0001 → B212-016CT0010 → B212-016CT0009 → B212-016CT0015 → B212-016CT0016 → B261-017BC0006 → B261-017BC0128 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MYB30GF202 -X03 (426, 427, 428) | 1 | A2F-S-25-N34 | 12 - 18 | 13
22BUB51.RB001 | -P20 | 49 |  | PE-L1-5C4-03 | PE-L1-5C4-03 | GT#2-2-22MBP22AA003 -Y02 |  |  | 1 | 2064 | 22BUB51.RB001-P2049 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-03 | 0.13 | 220 | D | 60 | GT PKG | 22BUB51.RB001 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | X2(1(L+), 2(L+), 3(L-)), X19(C2), PE | 22MBP22AA003 -Y02 | SO-VLV RGHT PILOT NAT-GAS | 1.1_MAIN BUILDING COMPLEX / GT #22 | RL, LL, L-, BR, PE | B212-016CT0001 → B212-016CT0010 → B212-016CT0009 → B212-016CT0015 → B212-016CT0016 → B261-017BC0006 → B261-017BC0129 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MYB30GF202 -X03 (422, 423, 424, 425, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
22BFA03.EA001 | -P20 | 50 |  | PE-L1-3C4-24 | PE-L1-3C4-24 | GT#2-2-22MBQ11AA001 -Y01 |  |  | 1 | 2065 | 22BFA03.EA001-P2050 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-24 | 0.16 | 230 | N | 50 | GT PKG | 22BFA03.EA001 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, N, PE | 22MBQ11AA001 -Y01 | SOL-VLV 1 IGN-GAS | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, N, PE | B212-016CT0001 → B212-016CT0010 → B212-016CT0009 → B212-016CT0015 → B212-016CT0016 → B261-017BC0006 → B261-017BC0130 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MYB30GF021 -X01 (701, 702, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 13
22BFA03.EA002 | -P20 | 51 |  | PE-L1-3C4-24 | PE-L1-3C4-24 | GT#2-2-22MBQ11AA002 -Y01 |  |  | 1 | 2066 | 22BFA03.EA002-P2051 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-24 | 0.125 | 230 | N | 60 | GT PKG | 22BFA03.EA002 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, N, PE | 22MBQ11AA002 -Y01 | SOL-VLV 2 IGN-GAS | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, N, PE | B212-016CT0001 → B212-016CT0010 → B212-016CT0009 → B212-016CT0015 → B212-016CT0016 → B261-017BC0006 → B261-017BC0131 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MYB30GF021 -X01 (703, 704, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 13
22BMA52.PB001 | -P20 | 54 |  | PE-L1-4C10-01 | PE-L1-4C10-01 | GT#2-2-22MBV21AP001 -M01 |  |  | 1 | 2067 | 22BMA52.PB001-P2054 | 0.6/1kV CU/XLPE/LSZH | 4C x 10sqmm | PE-L1-4C10-01 | 22 | 400 | E | 55 | GT PKG | 22BMA52.PB001 | GTG #22 400V AC EMERGENCY SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, L2, L3, PE | 22MBV21AP001 -M01 | LUBRICATING OIL PUMP 1 | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, L2, L3, PE | B212-016BT0025 → B212-016BT0007 → B212-016BT0008 → B212-016BT0009 → B212-016BT0010 → B212-016BT0002 → B212-016BT0012 → B212-996BT0026 → B261-016BC0107 → END |  | 1 | A2F-S-25a-N34 | 16 - 20.5 | 18
22BFA02.PB001 | -P20 | 55 |  | PE-L1-4C10-01 | PE-L1-4C10-01 | GT#2-2-22MBV21AP002 -M01 |  |  | 1 | 2068 | 22BFA02.PB001-P2055 | 0.6/1kV CU/XLPE/LSZH | 4C x 10sqmm | PE-L1-4C10-01 | 22 | 400 | N | 55 | GT PKG | 22BFA02.PB001 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, L2, L3, PE | 22MBV21AP002 -M01 | LUBRICATING OIL PUMP 2 | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, L2, L3, PE | B212-016BT0025 → B212-016BT0007 → B212-016BT0008 → B212-016BT0009 → B212-016BT0010 → B212-016BT0002 → B212-016BT0012 → B212-996BT0026 → B261-016BC0108 → END |  | 1 | A2F-S-25a-N34 | 16 - 20.5 | 18
22BUA51.RA001 | -P20 | 56 |  | PE-L1-3C4-29 | PE-L1-3C4-29 | GT#2-2-22MBV21AP003 -E01 |  |  | 1 | 2069 | 22BUA51.RA001-P2056 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-29 | 0.1 | 220 | D | 40 | GT PKG | 22BUA51.RA001 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | X19(D03(L), D04(N)), PE | 22MBV21AP003 -E01 | EMERGENCY LUB-OIL-PP | 1.1_MAIN BUILDING COMPLEX / GT #22 | L, N, PE | B212-016DT0001 → B212-016DT0002 → B212-016DT0012 → B212-996DT0026 → B261-017BC0142 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
22BUA51.RA001 | -P20 | 57 |  | PE-L1-4C6-03 | PE-L1-4C6-03 | GT#2-2-22MBV21AP003 -M01 |  |  | 1 | 2070 | 22BUA51.RA001-P2057 | 0.6/1kV CU/XLPE/LSZH | 4C x 6sqmm | PE-L1-4C6-03 | 3.7 | 220 | D | 40 | GT PKG | 22BUA51.RA001 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | X2(1, 2, 3), PE | 22MBV21AP003 -M01 | EMERGENCY LUB-OIL-PP | 1.1_MAIN BUILDING COMPLEX / GT #22 | F1, A2, D2, PE | B212-016DT0001 → B212-016DT0002 → B212-016DT0012 → B212-996DT0026 → B261-017BC0143 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 15.5
22BUA51.RA001 | -P20 | 58 |  | PE-L1-3C95/50-01 | PE-L1-3C95/50-01 | GT#2-2-22MBV21AP003 -R01 |  |  | 1 | 2071 | 22BUA51.RA001-P2058 | 0.6/1kV CU/XLPE/LSZH | 2C x 95sqmm + 1C x 50sqmm | PE-L1-3C95/50-01 | 3.7 | 220 | D | 40 | GT PKG | 22BUA51.RA001 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | X2(1, 2), PE | 22MBV21AP003 -R01 | EMERGENCY LUB-OIL-PP | 1.1_MAIN BUILDING COMPLEX / GT #22 | 1, 2, PE | B212-016DT0001 → B212-016DT0002 → B212-016DT0012 → B212-996DT0026 → B261-017BC0144 → END |  | 1 | A2F-S-50-N1-12 | 32.1 - 40 | 34.5
22BMA51.SA001 | -P20 | 59 |  | PE-L1-4C35/25-02 | PE-L1-4C35/25-02 | GT#2-2-22MBV30AP001 -M01 |  |  | 1 | 2072 | 22BMA51.SA001-P2059 | 0.6/1kV CU/XLPE/LSZH | 3C x 35sqmm + 1C X 25sqmm | PE-L1-4C35/25-02 | 50.6 | 400 | E | 60 | GT PKG | 22BMA51.SA001 | GTG #22 400V AC EMERGENCY SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, L2, L3, PE | 22MBV30AP001 -M01 | LIFTING OIL PUMP 1 | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, L2, L3, PE | B212-016DT0025 → B212-016DT0007 → B212-016DT0008 → B212-016DT0009 → B212-016DT0010 → B212-016DT0002 → B212-016DT0012 → B212-996DT0026 → B261-016BC0111 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5
22BFA02.SA001 | -P20 | 60 |  | PE-L1-4C35/25-02 | PE-L1-4C35/25-02 | GT#2-2-22MBV30AP002 -M01 |  |  | 1 | 2073 | 22BFA02.SA001-P2060 | 0.6/1kV CU/XLPE/LSZH | 3C x 35sqmm + 1C X 25sqmm | PE-L1-4C35/25-02 | 50.6 | 400 | N | 40 | GT PKG | 22BFA02.SA001 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, L2, L3, PE | 22MBV30AP002 -M01 | LIFTING OIL PUMP 2 | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, L2, L3, PE | B212-016DT0001 → B212-016DT0002 → B212-016DT0012 → B212-996DT0026 → B261-016BC0112 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5
22BMA52.CB001 | -P20 | 61 |  | PE-L1-4C4-23 | PE-L1-4C4-23 | GT#2-2-22MBV50AN001 -M01 |  |  | 1 | 2074 | 22BMA52.CB001-P2061 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-23 | 2.2 | 400 | E | 60 | GT PKG | 22BMA52.CB001 | GTG #22 400V AC EMERGENCY SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, L2, L3, PE | 22MBV50AN001 -M01 | OIL-VAP-EXTR1 LUB-OIL-TNK | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, L2, L3, PE | B212-016DT0025 → B212-016DT0007 → B212-016DT0008 → B212-016DT0009 → B212-016DT0010 → B212-016DT0002 → B212-016DT0012 → B212-996DT0026 → B261-016BC0123 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
22BFA02.EA001 | -P20 | 62 |  | PE-L1-4C4-23 | PE-L1-4C4-23 | GT#2-2-22MBV50AN002 -M01 |  |  | 1 | 2075 | 22BFA02.EA001-P2062 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-23 | 2.2 | 400 | N | 50 | GT PKG | 22BFA02.EA001 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, L2, L3, PE | 22MBV50AN002 -M01 | OIL-VAP-EXTR2 LUB-OIL-TNK | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, L2, L3, PE | B212-016DT0001 → B212-016DT0002 → B212-016DT0012 → B212-996DT0026 → B261-016BC0121 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
22BFA02.FB001 | -P20 | 63 |  | PE-L1-4C4-23 | PE-L1-4C4-23 | GT#2-2-22MBX01AH001 -E01 |  |  | 1 | 2076 | 22BFA02.FB001-P2063 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-23 | 1 | 400 | N | 50 | GT PKG | 22BFA02.FB001 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, L2, L3, PE | 22MBX01AH001 -E01 | TNK HTG 1 HYDRC OIL | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, L2, L3, PE | B212-016DT0001 → B212-016DT0002 → B212-016DT0012 → B212-996DT0026 → B261-016BC0124 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
22BFA02.FB002 | -P20 | 64 |  | PE-L1-4C4-23 | PE-L1-4C4-23 | GT#2-2-22MBX01AH002 -E01 |  |  | 1 | 2077 | 22BFA02.FB002-P2064 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-23 | 1 | 400 | N | 50 | GT PKG | 22BFA02.FB002 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, L2, L3, PE | 22MBX01AH002 -E01 | TNK HTG 2 HYDRC OIL | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, L2, L3, PE | B212-016DT0001 → B212-016DT0002 → B212-016DT0012 → B212-996DT0026 → B261-016BC0122 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
22BFA02.HA002 | -P20 | 65 |  | PE-L1-4C4-23 | PE-L1-4C4-23 | GT#2-2-22MBX02AP001 -M01 |  |  | 1 | 2078 | 22BFA02.HA002-P2065 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-23 | 7.5 | 400 | N | 60 | GT PKG | 22BFA02.HA002 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, L2, L3, PE | 22MBX02AP001 -M01 | MN PP 1 HYDRC OIL | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, L2, L3, PE | B212-016DT0025 → B212-016DT0007 → B212-016DT0008 → B212-016DT0009 → B212-016DT0010 → B212-016DT0002 → B212-016DT0012 → B212-996DT0026 → B261-016BC0114 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
22BFA02.HA003 | -P20 | 66 |  | PE-L1-4C4-23 | PE-L1-4C4-23 | GT#2-2-22MBX02AP002 -M01 |  |  | 1 | 2079 | 22BFA02.HA003-P2066 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-23 | 7.5 | 400 | N | 60 | GT PKG | 22BFA02.HA003 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, L2, L3, PE | 22MBX02AP002 -M01 | MN PP 2 HYDRC OIL | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, L2, L3, PE | B212-016DT0025 → B212-016DT0007 → B212-016DT0008 → B212-016DT0009 → B212-016DT0010 → B212-016DT0002 → B212-016DT0012 → B212-996DT0026 → B261-016BC0115 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
22BFA02.HA001 | -P20 | 67 |  | PE-L1-4C4-24 | PE-L1-4C4-24 | GT#2-2-22MBX06AH001 -M01 |  |  | 1 | 2080 | 22BFA02.HA001-P2067 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-24 | 0.18 | 400 | N | 60 | GT PKG | 22BFA02.HA001 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, L2, L3, PE | 22MBX06AH001 -M01 | FAN COOL-CCT HYDRC OIL | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, L2, L3, PE | B212-016DT0025 → B212-016DT0007 → B212-016DT0008 → B212-016DT0009 → B212-016DT0010 → B212-016DT0002 → B212-016DT0012 → B212-996DT0026 → B261-016BC0116 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
22BFA02.JB001 | -P20 | 68 |  | PE-L1-4C16-02 | PE-L1-4C16-02 | GT#2-2-22MBY10GF002 -E01 |  |  | 1 | 2081 | 22BFA02.JB001-P2068 | 0.6/1kV CU/XLPE/LSZH | 4C X 16sqmm | PE-L1-4C16-02 | 28 | 400 | N | 50 | GT PKG | 22BFA02.JB001 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, L2, L3, PE | 22MBY10GF002 -E01 | JUNCT BOX HTG LUB-OIL TNK | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, L2, L3, PE | B212-016DT0001 → B212-016DT0002 → B212-016DT0012 → B212-996DT0026 → B261-016BC0113 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MBY10GF002 -X01 (701, 702, 703, PE) | 1 | A2F-S-25a-N34 | 16 - 20.5 | 19.5
22BFA52.HA001 | -P20 | 69 |  | PE-L1-5C4-04 | PE-L1-5C4-04 | GT#2-2-22MBY40GH001 -E01 |  |  | 1 | 2082 | 22BFA52.HA001-P2069 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-04 | 9 | 400 | N | 90 | GT PKG | 22BFA52.HA001 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, L2, L3, N, PE | 22MBY40GH001 -E01 | JB INSTR AIR SYST | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, L2, L3, N, PE | B212-016CT0001 → B212-016CT0010 → B212-016CT0009 → B212-016CT0008 → B212-016CT0007 → B212-016CT0024 → B212-996CT0023 → M0304 → B261-006BC0012 → B261-016BC0104 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MBY40GH001 -X01 (701, 702, 703, 704, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
22BFA51.HA002 | -P20 | 70 |  | PE-L1-5C4-02 | PE-L1-5C4-02 | GT#2-2-22MBY80GH001 -E01 |  |  | 1 | 2083 | 22BFA51.HA002-P2070 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-02 | 7 | 400 | N | 60 | GT PKG | 22BFA51.HA002 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, L2, L3, N, PE | 22MBY80GH001 -E01 | TRACE HEATING CABINET | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, L2, L3, N, PE | B212-016CT0001 → B212-016CT0010 → B212-016CT0009 → B212-016CT0015 → B212-016CT0016 → B261-016BC0019 → B261-016BC0102 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MBY80GH001 -X02 (L1, L2, L3, N, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
22BFA02.EA002 | -P20 | 71 |  | PE-L1-4C4-24 | PE-L1-4C4-24 | GT#2-2-22MKA10AH010 -E01 |  |  | 1 | 2084 | 22BFA02.EA002-P2071 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-24 | 3.2 | 400 | N | 40 | GT PKG | 22BFA02.EA002 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, L2, L3, PE | 22MKA10AH010 -E01 | GENERATOR SPACE HEATER | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, L2, L3, PE | B212-016DT0025 → B212-016DT0007 → B212-016DT0019 → B212-016DT0020 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
22MKC01GT002 -E01 | -P20 | 74 |  | PE-L1-1C240-03 | PE-L1-1C240-03 | GT#2-2-22MKC01GT002 -E01 |  |  | 1 | 2085 | 22MKC1001 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-03 | 1100 | 550 | N | 50 | GT PKG | 22MKC01GT002 -E01 | GTG #22 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1 | 22CJT21 | GTG #22 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | L1 | B261-007BC0013 → M0303 → D0304-L32 → M0304 → B212-996DT0021 → B212-016DT0004 → B212-016DT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
22MKC01GT002 -E01 | -P20 | 75 |  | PE-L1-1C240-03 | PE-L1-1C240-03 | GT#2-2 |  |  | 1 | 2086 | 22MKC1004 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-03 | 1100 | 550 | N | 50 | GT PKG | 22MKC01GT002 -E01 | GTG #22 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #22 | L2 | 22CJT21 | GTG #22 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | L2 | B261-007BC0013 → M0303 → D0304-L32 → M0304 → B212-996DT0021 → B212-016DT0004 → B212-016DT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
22MKC01GT002 -E01 | -P20 | 76 |  | PE-L1-1C240-03 | PE-L1-1C240-03 | GT#2-2 |  |  | 1 | 2087 | 22MKC1007 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-03 | 1100 | 550 | N | 50 | GT PKG | 22MKC01GT002 -E01 | GTG #22 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #22 | L3 | 22CJT21 | GTG #22 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | L3 | B261-007BC0013 → M0303 → D0304-L32 → M0304 → B212-996DT0021 → B212-016DT0004 → B212-016DT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
22MKC01GT002 -E01 | -P20 | 77 |  | PE-L1-1C240-03 | PE-L1-1C240-03 | GT#2-2 |  |  | 1 | 2088 | 22MKC1002 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-03 | 1100 | 550 | N | 50 | GT PKG | 22MKC01GT002 -E01 | GTG #22 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1 | 22CJT21 | GTG #22 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | L1 | B261-007BC0014 → M0303 → D0304-L32 → M0304 → B212-996DT0021 → B212-016DT0004 → B212-016DT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
22MKC01GT002 -E01 | -P20 | 78 |  | PE-L1-1C240-03 | PE-L1-1C240-03 | GT#2-2 |  |  | 1 | 2089 | 22MKC1005 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-03 | 1100 | 550 | N | 50 | GT PKG | 22MKC01GT002 -E01 | GTG #22 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #22 | L2 | 22CJT21 | GTG #22 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | L2 | B261-007BC0014 → M0303 → D0304-L32 → M0304 → B212-996DT0021 → B212-016DT0004 → B212-016DT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
22MKC01GT002 -E01 | -P20 | 79 |  | PE-L1-1C240-03 | PE-L1-1C240-03 | GT#2-2 |  |  | 1 | 2090 | 22MKC1008 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-03 | 1100 | 550 | N | 50 | GT PKG | 22MKC01GT002 -E01 | GTG #22 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #22 | L3 | 22CJT21 | GTG #22 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | L3 | B261-007BC0014 → M0303 → D0304-L32 → M0304 → B212-996DT0021 → B212-016DT0004 → B212-016DT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
22MKC01GT002 -E01 | -P20 | 82 |  | PE-L1-1C240-03 | PE-L1-1C240-03 | GT#2-2 |  |  | 1 | 2091 | 22MKC1003 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-03 | 1100 | 550 | N | 50 | GT PKG | 22MKC01GT002 -E01 | GTG #22 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1 | 22CJT21 | GTG #22 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | L1 | B261-007BC0015 → M0303 → D0304-L32 → M0304 → B212-996DT0021 → B212-016DT0004 → B212-016DT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
22MKC01GT002 -E01 | -P20 | 83 |  | PE-L1-1C240-03 | PE-L1-1C240-03 | GT#2-2 |  |  | 1 | 2092 | 22MKC1006 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-03 | 1100 | 550 | N | 50 | GT PKG | 22MKC01GT002 -E01 | GTG #22 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #22 | L2 | 22CJT21 | GTG #22 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | L2 | B261-007BC0015 → M0303 → D0304-L32 → M0304 → B212-996DT0021 → B212-016DT0004 → B212-016DT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
22MKC01GT002 -E01 | -P20 | 84 |  | PE-L1-1C240-03 | PE-L1-1C240-03 | GT#2-2 |  |  | 1 | 2093 | 22MKC1009 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-03 | 1100 | 550 | N | 50 | GT PKG | 22MKC01GT002 -E01 | GTG #22 LV-SIDE EXCN TFR | 1.1_MAIN BUILDING COMPLEX / GT #22 | L3 | 22CJT21 | GTG #22 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | L3 | B261-007BC0015 → M0303 → D0304-L32 → M0304 → B212-996DT0021 → B212-016DT0004 → B212-016DT0003 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPET 0214-LR12 | 2 | 1 | PPEO 0114-SR12 | 1
22BFA52.DA002 | -P20 | 90 |  | PE-L1-3C4-24 | PE-L1-3C4-24 | GT#2-2-22MKC01GW035 -E01 |  |  | 1 | 2094 | 22BFA52.DA002-P2090 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-24 | 1.2 | 230 | N | 40 | GT PKG | 22BFA52.DA002 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3210) | L1, N, PE | 22MKC01GW035 -E01 | MKC 1AC AUX-VOLT SUP | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, N, PE | B212-016CT0001 → B212-016CT0002 → B212-016CT0003 → B212-016CT0004 → B212-996CT0021 → M0304 → D0304-L23 → M0303 → B261-007BC0012 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
22BFA51.HA003 | -P20 | 91 |  | PE-L1-5C4-04 | PE-L1-5C4-04 | GT#2-2-22MKC05GE001 -E01 |  |  | 1 | 2095 | 22BFA51.HA003-P2091 | 0.6/1kV CU/XLPE/LSZH | 5C x 4sqmm | PE-L1-5C4-04 | 1.15 | 400 | N | 60 | GT PKG | 22BFA51.HA003 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, L2, L3, N, PE | 22MKC05GE001 -E01 | TERBO POW-SUP SLRNGRM-VEN | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, L2, L3, N, PE | B212-016CT0001 → B212-016CT0002 → B212-016CT0003 → B212-016CT0004 → B212-996CT0021 → M0304 → D0304-L23 → M0303 → B261-007BC0012 → END | SWGR to J/B : Doosan J/B to consumer : SE 22MKC05GE001 -X0 (1, 2, 3, 4, N, PE) | 1 | A2F-S-25-N34 | 12 - 18 | 15
22BFA51.DA003 | -P20 | 92 |  | PE-L1-3C4-24 | PE-L1-3C4-24 | GT#2-2-22MKC10GP001 -E01 |  |  | 1 | 2096 | 22BFA51.DA003-P2092 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-24 | 0.22 | 230 | N | 40 | GT PKG | 22BFA51.DA003 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, N, PE | 22MKC10GP001 -E01 | LIGHTING EXCITER HOUSING | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, N, PE | B212-016CT0001 → B212-016CT0002 → B212-016CT0003 → B212-016CT0004 → B212-996CT0021 → M0304 → B261-007BC0012 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
22CJT21 | -P20 | 93 |  | PE-L1-1C240-03 | PE-L1-1C240-03 | GT#2-2-22MKC30GE001 -E01 |  |  | 1 | 2097 | 22CJT1001 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-03 | - | 700 | D | 40 | GT PKG | 22CJT21 | GTG #22 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | L+ | 22MKC30GE001 -E01 | GEN EXCN BRSH | 1.1_MAIN BUILDING COMPLEX / GT #22 | L+ | B212-016DT0005 → B212-016DT0006 → B212-016DT0007 → B212-016DT0019 → B212-016DT0020 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 | To 단자대 Hole 확인필요
22CJT21 | -P20 | 94 |  | PE-L1-1C240-03 | PE-L1-1C240-03 | GT#2-2 |  |  | 1 | 2098 | 22CJT1002 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-03 | - | 700 | D | 40 | GT PKG | 22CJT21 | GTG #22 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | L+ | 22MKC30GE001 -E01 | GEN EXCN BRSH | 1.1_MAIN BUILDING COMPLEX / GT #22 | L+ | B212-016DT0005 → B212-016DT0006 → B212-016DT0007 → B212-016DT0019 → B212-016DT0020 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 | To 단자대 Hole 확인필요
22CJT21 | -P20 | 95 |  | PE-L1-1C240-03 | PE-L1-1C240-03 | GT#2-2 |  |  | 1 | 2099 | 22CJT1003 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-03 | - | 700 | D | 40 | GT PKG | 22CJT21 | GTG #22 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | L+ | 22MKC30GE001 -E01 | GEN EXCN BRSH | 1.1_MAIN BUILDING COMPLEX / GT #22 | L+ | B212-016DT0005 → B212-016DT0006 → B212-016DT0007 → B212-016DT0019 → B212-016DT0020 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 | To 단자대 Hole 확인필요
22CJT21 | -P20 | 96 |  | PE-L1-1C240-03 | PE-L1-1C240-03 | GT#2-2 |  |  | 1 | 2100 | 22CJT1004 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-03 | - | 700 | D | 40 | GT PKG | 22CJT21 | GTG #22 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | L+ | 22MKC30GE001 -E01 | GEN EXCN BRSH | 1.1_MAIN BUILDING COMPLEX / GT #22 | L+ | B212-016DT0005 → B212-016DT0006 → B212-016DT0007 → B212-016DT0019 → B212-016DT0020 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 | To 단자대 Hole 확인필요
22CJT21 | -P20 | 97 |  | PE-L1-1C240-03 | PE-L1-1C240-03 | GT#2-2 |  |  | 1 | 2101 | 22CJT1005 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-03 | - | 700 | D | 40 | GT PKG | 22CJT21 | GTG #22 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | L- | 22MKC30GE001 -E01 | GEN EXCN BRSH | 1.1_MAIN BUILDING COMPLEX / GT #22 | L- | B212-016DT0005 → B212-016DT0006 → B212-016DT0007 → B212-016DT0019 → B212-016DT0020 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 | To 단자대 Hole 확인필요
22CJT21 | -P20 | 98 |  | PE-L1-1C240-03 | PE-L1-1C240-03 | GT#2-2 |  |  | 1 | 2102 | 22CJT1006 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-03 | - | 700 | D | 40 | GT PKG | 22CJT21 | GTG #22 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | L- | 22MKC30GE001 -E01 | GEN EXCN BRSH | 1.1_MAIN BUILDING COMPLEX / GT #22 | L- | B212-016DT0005 → B212-016DT0006 → B212-016DT0007 → B212-016DT0019 → B212-016DT0020 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 | To 단자대 Hole 확인필요
22CJT21 | -P20 | 98 |  | PE-L1-1C240-03 | PE-L1-1C240-03 | GT#2-2 |  |  | 1 | 2103 | 22CJT1007 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-03 | - | 700 | D | 40 | GT PKG | 22CJT21 | GTG #22 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | L- | 22MKC30GE001 -E01 | GEN EXCN BRSH | 1.1_MAIN BUILDING COMPLEX / GT #22 | L- | B212-016DT0005 → B212-016DT0006 → B212-016DT0007 → B212-016DT0019 → B212-016DT0020 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 | To 단자대 Hole 확인필요
22CJT21 | -P20 | 98 |  | PE-L1-1C240-03 | PE-L1-1C240-03 | GT#2-2 |  |  | 1 | 2104 | 22CJT1008 | 0.6/1kV CU/XLPE/LSZH | 1C x 240sqmm | PE-L1-1C240-03 | - | 700 | D | 40 | GT PKG | 22CJT21 | GTG #22 SEE CABINET | 1.1_MAIN BUILDING COMPLEX / PCC #22(UBA3310) | L- | 22MKC30GE001 -E01 | GEN EXCN BRSH | 1.1_MAIN BUILDING COMPLEX / GT #22 | L- | B212-016DT0005 → B212-016DT0006 → B212-016DT0007 → B212-016DT0019 → B212-016DT0020 → END |  | 1 | A2F-S-40(S)-N1-14 | 22 - 28 | 25.5 | 1 | PPEO 0114-SR12 | 1 | 1 | PPEO 0114-SR12 | 1 | To 단자대 Hole 확인필요
22BUA51.DA001 | -P20 | 99 |  | PE-L1-2C4-09 | PE-L1-2C4-09 | GT#2-2-22MPB10GW011 -E01 |  |  | 1 | 2105 | 22BUA51.DA001-P2099 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-09 | 1 | 220 | D | 120 | GT PKG | 22BUA51.DA001 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L+, L- | 22MPB10GW011 -E01 | GAS-TURB ENCL EMERG LITG | 1.1_MAIN BUILDING COMPLEX / GT #22 | L+, L- | B212-016CT0001 → B212-016CT0002 → B212-016CT0003 → B212-016CT0004 → B212-996CT0021 → M0304 → D0304-L23 → M0303 → D0303-L32 → M0302 → B261-006BC0005 → B261-006BC0003 → B261-017BC0101 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
22BFA51.DA004 | -P2 | 100 |  | PE-L1-3C4-24 | PE-L1-3C4-24 | GT#2-2-22MPB10GW023 -E01 |  |  | 1 | 2106 | 22BFA51.DA004-P2100 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-24 | 1 | 230 | N | 120 | GT PKG | 22BFA51.DA004 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, N, PE | 22MPB10GW023 -E01 | GAS-TURB ENCL LITG | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, N, PE | B212-016CT0001 → B212-016CT0002 → B212-016CT0003 → B212-016CT0004 → B212-996CT0021 → M0304 → D0304-L23 → M0303 → D0303-L32 → M0302 → B261-006BC0005 → B261-006BC0003 → B261-017BC0102 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
22BUA51.DA002 | -P2 | 101 |  | PE-L1-2C4-09 | PE-L1-2C4-09 | GT#2-2-22MPB13GW011 -E01 |  |  | 1 | 2107 | 22BUA51.DA002-P2101 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-09 | 0.22 | 220 | D | 40 | GT PKG | 22BUA51.DA002 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L+, L- | 22MPB13GW011 -E01 | FGS ENCL EMERG LITG | 1.1_MAIN BUILDING COMPLEX / GT #22 | L+, L- | B212-016DT0025 → B212-996DT0022 → M0305 → B261-006BC0021 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
22BFA51.DA005 | -P2 | 102 |  | PE-L1-3C4-24 | PE-L1-3C4-24 | GT#2-2-22MPB13GW023 -E01 |  |  | 1 | 2108 | 22BFA51.DA005-P2102 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-24 | 1 | 230 | N | 40 | GT PKG | 22BFA51.DA005 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, N, PE | 22MPB13GW023 -E01 | FGS ENCL LITG | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, N, PE | B212-016DT0025 → B212-996DT0022 → M0305 → B261-006BC0020 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
22BUA51.DA003 | -P2 | 103 |  | PE-L1-2C4-09 | PE-L1-2C4-09 | GT#2-2-22MPB16GW011 -E01 |  |  | 1 | 2109 | 22BUA51.DA003-P2103 | 0.6/1kV CU/XLPE/LSZH | 2C x 4sqmm | PE-L1-2C4-09 | 0.44 | 220 | D | 30 | GT PKG | 22BUA51.DA003 | GTG #22 220V DC SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L+, L- | 22MPB16GW011 -E01 | IMS + GEN ENCL EMERG LITG | 1.1_MAIN BUILDING COMPLEX / GT #22 | L+, L- | B212-016CT0011 → B212-016CT0010 → B212-016CT0009 → B212-016CT0015 → B212-016CT0016 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 12.5
22BFA51.DA006 | -P2 | 104 |  | PE-L1-3C4-24 | PE-L1-3C4-24 | GT#2-2-22MPB16GW023 -E01 |  |  | 1 | 2110 | 22BFA51.DA006-P2104 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-24 | 1 | 230 | N | 30 | GT PKG | 22BFA51.DA006 | GTG #22 400V AC UNIT SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, N, PE | 22MPB16GW023 -E01 | IMS + GEN ENCL LITG | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, N, PE | B212-016CT0011 → B212-016CT0010 → B212-016CT0009 → B212-016CT0015 → B212-016CT0016 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 13
22BMA51.CB001 | -P2 | 105 |  | PE-L1-4C4-24 | PE-L1-4C4-24 | GT#2-2-22SAM33AN001 -M01 |  |  | 1 | 2111 | 22BMA51.CB001-P2105 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-24 | 0.55 | 400 | E | 60 | GT PKG | 22BMA51.CB001 | GTG #22 400V AC EMERGENCY SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, L2, L3, PE | 22SAM33AN001 -M01 | EXH-AIR FAN FU-GAS ENCL | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, L2, L3, PE | B212-016BT0025 → B212-016BT0007 → B212-016BT0008 → B212-016BT0009 → B212-016BT0010 → B212-016BT0002 → B212-016BT0012 → B212-996BT0026 → B261-016BC0109 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
22BFA02.FB001 | -P2 | 106 |  | PE-L1-4C4-24 | PE-L1-4C4-24 | GT#2-2-22SAM33AN002 -M01 |  |  | 1 | 2112 | 22BFA02.FB001-P2106 | 0.6/1kV CU/XLPE/LSZH | 4C x 4sqmm | PE-L1-4C4-24 | 0.55 | 400 | N | 60 | GT PKG | 22BMA51.CB003 | GTG #22 400V AC EMERGENCY SWITCHGEAR | 1.1_MAIN BUILDING COMPLEX / PCC #22 | L1, L2, L3, PE | 22SAM33AN002 -M01 | EXH-AIR FAN FU-GAS ENCL | 1.1_MAIN BUILDING COMPLEX / GT #22 | L1, L2, L3, PE | B212-016BT0025 → B212-016BT0007 → B212-016BT0008 → B212-016BT0009 → B212-016BT0010 → B212-016BT0002 → B212-016BT0012 → B212-996BT0026 → B261-016BC0110 → END |  | 1 | A2F-S-25-N34 | 12 - 18 | 14
[5 empty] | PE-L1-3C4-27 | GTG-U1-010 | ADD |  |  | 2113 | INT-ACDB-1.3-P2201 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-27 | 1.54 | 230 | N | 65 | GTG | ЩГП-1.3 | INTEGRA AC DB PNL | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | 11CRY01GW022-E01 | GTG #11 SERVER/LAN CABINET (Cable Only) | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / SERVER ROOM | L1, N, PE | B073-017AC0004 → PSP/BCN(INTEGRA)TRAY → B073-017AC0008 → B073-016AT0001 → B073-016AT0014 → B073-016AT0011 → END
[5 empty] | PE-L1-3C4-27 | GTG-U2-010 | ADD |  |  | 2114 | INT-ACDB-1.3-P2202 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-27 | 1.54 | 230 | N | 65 | GTG | ЩГП-1.3 | INTEGRA AC DB PNL | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | 12CRY01GW022-E01 | GTG #12 SERVER/LAN CABINET (Cable Only) | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / SERVER ROOM | L1, N, PE | B073-017AC0004 → PSP/BCN(INTEGRA)TRAY → B073-017AC0008 → B073-016AT0001 → B073-016AT0014 → B073-016AT0011 → END
[5 empty] | PE-L1-3C4-27 | GTG-U3-010 | ADD |  |  | 2115 | INT-ACDB-1.3-P2203 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-27 | 1.54 | 230 | N | 70 | GTG | ЩГП-1.3 | INTEGRA AC DB PNL | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | 21CRY01GW022-E01 | GTG #21 SERVER/LAN CABINET (Cable Only) | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / SERVER ROOM | L1, N, PE | B073-017AC0004 → PSP/BCN(INTEGRA)TRAY → B073-017AC0008 → B073-016AT0001 → B073-016AT0014 → B073-016AT0015 → B073-016AT0013 → END
[5 empty] | PE-L1-3C4-27 | GTG-U4-010 | ADD |  |  | 2116 | INT-ACDB-1.3-P2204 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-27 | 1.54 | 230 | N | 70 | GTG | ЩГП-1.3 | INTEGRA AC DB PNL | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | 22CRY01GW022-E01 | GTG #22 SERVER/LAN CABINET (Cable Only) | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / SERVER ROOM | L1, N, PE | B073-017AC0004 → PSP/BCN(INTEGRA)TRAY → B073-017AC0008 → B073-016AT0001 → B073-016AT0014 → B073-016AT0015 → B073-016AT0013 → END
[5 empty] | PE-L1-3C4-27 | STG-B1-067-002 | ADD |  |  | 2117 | INT-ACDB-1.3-P2205 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-27 | 2.5 | 230 | N | 65 | STG | ЩГП-1.3 | INTEGRA AC DB PNL | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B1-TCS-1320 | TCS SERVER(TLCS) CABINET (AUX. POWER) (Cable Only) | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / SERVER ROOM | L1, N, PE | B073-017AC0004 → PSP/BCN(INTEGRA)TRAY → B073-017AC0008 → B073-016AT0001 → B073-016AT0014 → B073-016AT0011 → END
[5 empty] | PE-L1-3C4-27 | STG-B2-067-002 | ADD |  |  | 2118 | INT-ACDB-1.3-P2206 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-27 | 2.5 | 230 | N | 70 | STG | ЩГП-1.3 | INTEGRA AC DB PNL | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B2-TCS-1320 | TCS SERVER(TLCS) CABINET (AUX. POWER) (Cable Only) | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / SERVER ROOM | L1, N, PE | B073-017AC0004 → PSP/BCN(INTEGRA)TRAY → B073-017AC0008 → B073-016AT0001 → B073-016AT0014 → B073-016AT0015 → B073-016AT0013 → END
[5 empty] | PE-L1-3C4-27 | HRSG-U1-020 | ADD |  |  | 2119 | INT-UDB-1.2-P2201 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-27 | 0.5 | 230 | U | 75 | HRSG | UDB-1.2 | INTEGRA UPS DB PNL | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B0-C-0001A | CEMS SWITCH PANEL - Line 1 (Cable Only) | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / CCR | L1, N, PE | B073-017AC0002 → PSP/BCN(INTEGRA)TRAY → B073-017AC0006 → B073-016AT0001 → B073-016AT0002 → B073-016AT0003 → B073-016AT0004 → END
[5 empty] | PE-L1-3C4-27 | HRSG-U1-021 | ADD |  |  | 2120 | INT-UDB-1.1-P2201 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-27 | 0.5 | 230 | U | 75 | HRSG | UDB-1.1 | INTEGRA UPS DB PNL | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B0-C-0001B | CEMS SWITCH PANEL - Line 2 (Cable Only) | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / CCR | L1, N, PE | B073-017AC0001 → PSP/BCN(INTEGRA)TRAY → B073-017AC0006 → B073-016AT0001 → B073-016AT0002 → B073-016AT0003 → B073-016AT0004 → END
|  |  |  | PE-L1-3C25/16-01 | PE-L1-3C25/16-01 | INC-0012 | ADD |  |  | 2121 | INT-ACDB-1.3-P2207 | 0.6/1kV CU/XLPE/LSZH | 2C x 25sqmm + 1C X 16sqmm | PE-L1-3C25/16-01 | 11 | 230 | N | 63 | DCS | ЩГП-1.3 | INTEGRA AC DB PNL | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B1-PDP-0001 | BLOCK #1 DCS (SERVER ROOM) PDP NORMAL (Cable Only) | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B073-017AC0004 → PSP/BCN(INTEGRA)TRAY → B073-017AC0008 → B073-016AT0001 → B073-016AT0014 → B073-016AT0015 → B073-016AT0013 → END
|  |  | Drum 재배정(10/12) | PE-L1-3C25/16-03 | PE-L1-3C25/16-02 | INC-0015 | ADD |  |  | 2122 | INT-ACDB-1.3-P2208 | 0.6/1kV CU/XLPE/LSZH | 2C x 25sqmm + 1C X 16sqmm | PE-L1-3C25/16-02 | 11 | 230 | N | 65 | DCS | ЩГП-1.3 | INTEGRA AC DB PNL | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B2-PDP-0001 | BLOCK #2 DCS (SERVER ROOM) PDP NORMAL (Cable Only) | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B073-017AC0004 → PSP/BCN(INTEGRA)TRAY → B073-017AC0008 → B073-016AT0001 → B073-016AT0014 → B073-016AT0015 → B073-016AT0013 → END
|  |  |  | PE-L1-3C25/16-01 | PE-L1-3C25/16-01 | INC-0015-001 | ADD |  |  | 2123 | INT-UDB-1.2-P2202 | 0.6/1kV CU/XLPE/LSZH | 2C x 25sqmm + 1C X 16sqmm | PE-L1-3C25/16-01 | 10 | 230 | U | 63 | DCS | UDB-1.2 | INTEGRA UPS DB PNL | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B0-PDP-0001 | COMMON DCS (SERVER ROOM) PDP PRIMARY (Cable Only) | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B073-017AC0002 → PSP/BCN(INTEGRA)TRAY → B073-017AC0006 → B073-016AT0001 → B073-016AT0014 → B073-016AT0015 → B073-016AT0013 → END
|  |  | Drum 재배정(10/12) | PE-L1-3C25/16-03 | PE-L1-3C25/16-02 | INC-0015-002 | ADD |  |  | 2124 | INT-UDB-1.1-P2202 | 0.6/1kV CU/XLPE/LSZH | 2C x 25sqmm + 1C X 16sqmm | PE-L1-3C25/16-02 | 10 | 230 | U | 65 | DCS | UDB-1.1 | INTEGRA UPS DB PNL | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B0-PDP-0001 | COMMON DCS (SERVER ROOM) PDP SECONDARY (Cable Only) | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B073-017AC0001 → PSP/BCN(INTEGRA)TRAY → B073-017AC0006 → B073-016AT0001 → B073-016AT0014 → B073-016AT0015 → B073-016AT0013 → END
|  |  |  | PE-L1-3C25/16-01 | PE-L1-3C25/16-01 | INC-0015-003 | ADD |  |  | 2125 | INT-ACDB-1.3-P2209 | 0.6/1kV CU/XLPE/LSZH | 2C x 25sqmm + 1C X 16sqmm | PE-L1-3C25/16-01 | 13 | 230 | N | 63 | DCS | ЩГП-1.3 | INTEGRA AC DB PNL | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B0-PDP-0001 | COMMON DCS (SERVER ROOM) PDP NORMAL (Cable Only) | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B073-017AC0005 → PSP/BCN(INTEGRA)TRAY → B073-017AC0007 → B073-016AT0001 → B073-016AT0014 → B073-016AT0015 → B073-016AT0013 → END
[5 empty] | PE-L1-3C4-27 | INC-0034 | ADD |  |  | 2126 | INT-UDB-1.2-P2203 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-27 | 0.5 | 230 | U | 105 | WEATHER STATION | UDB-1.2 | INTEGRA UPS DB PNL | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B0-P-0081 | WEATHER STATION (Cable Only) | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / ROOF | L1, N, PE | PSP/BCN(INTEGRA)TRAY → B073-017AC0003
[5 empty] | PE-L1-3C4-27 | INC-0044 | ADD |  |  | 2127 | INT-UDB-1.2-P2204 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-27 | 1.5 | 230 | U | 75 | VMS | UDB-1.2 | INTEGRA UPS DB PNL | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B0-K-0001 | COMMON VMS (CCR) PANEL PRIMARY (Cable Only) | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / COMPUTER ROOM | L1, N, PE | B073-017AC0002 → PSP/BCN(INTEGRA)TRAY → B073-017AC0006 → B073-016AT0001 → B073-016AT0002 → B073-016AT0003 → B073-016AT0004 → END
[5 empty] | PE-L1-3C4-27 | INC-0045 | ADD |  |  | 2128 | INT-UDB-1.1-P2203 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-27 | 1.5 | 230 | U | 75 | VMS | UDB-1.1 | INTEGRA UPS DB PNL | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B0-K-0001 | COMMON VMS (CCR) PANEL SECONDARY (Cable Only) | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / COMPUTER ROOM | L1, N, PE | B073-017AC0001 → PSP/BCN(INTEGRA)TRAY → B073-017AC0006 → B073-016AT0001 → B073-016AT0002 → B073-016AT0003 → B073-016AT0004 → END
[5 empty] | PE-L1-3C4-27 | INC-0046 | ADD |  |  | 2129 | INT-ACDB-1.3-P2210 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-27 | 0.5 | 230 | N | 75 | VMS | ЩГП-1.3 | INTEGRA AC DB PNL | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B0-K-0001 | COMMON VMS (CCR) PANEL NORMAL (Cable Only) | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / COMPUTER ROOM | L1, N, PE | B073-017AC0005 → PSP/BCN(INTEGRA)TRAY → B073-017AC0007 → B073-016AT0001 → B073-016AT0002 → B073-016AT0003 → B073-016AT0004 → END
[5 empty] | PE-L1-3C4-27 | ELE-DU-6018 | ADD |  |  | 2130 | INT-ACDB-1.3-P2211 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-27 | 0.3 | 230 | N | 70 | DC & UPS | ЩГП-1.3 | INTEGRA AC DB PNL | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B1-UPSP-73701 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ADMIN. - BLOCK#1 - A | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / SERVER ROOM | L1, N, PE | B073-017AC0005 → PSP/BCN(INTEGRA)TRAY → B073-017AC0007 → B073-016AT0001 → B073-016AT0014 → B073-016AT0015 → B073-016AT0013 → END
[5 empty] | PE-L1-3C4-27 | ELE-DU-7018 | ADD |  |  | 2131 | INT-ACDB-1.3-P2212 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-27 | 0.3 | 230 | N | 70 | DC & UPS | ЩГП-1.3 | INTEGRA AC DB PNL | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | B2-UPSP-73701 | 400/230V AC UPS LOCAL DISTRIBUTION PANEL FOR ADMIN. - BLOCK#2 - A | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / SERVER ROOM | L1, N, PE | B073-017AC0005 → PSP/BCN(INTEGRA)TRAY → B073-017AC0007 → B073-016AT0001 → B073-016AT0014 → B073-016AT0015 → B073-016AT0013 → END
|  |  |  | PE-L1-2C4-07 | PE-L1-3C4-15 | ELE-AIS-0009 | ADD |  |  | 2132 | INT-ACDB-1.3-P2213 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 1.2 | 230 | N | 70 | AIS | ЩГП-1.3 | INTEGRA AC DB PNL | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | PA+R4P | SHC GRAM CABINET (Cable Only) | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / SERVER ROOM | L1, N, PE | B073-017AC0005 → PSP/BCN(INTEGRA)TRAY → B073-017AC0007 → B073-016AT0001 → B073-016AT0014 → B073-016AT0015 → B073-016AT0013 → END
|  |  |  | PE-L1-2C4-07 | PE-L1-3C4-27 | ELE-AIS-0010 | ADD |  |  | 2133 | INT-UDB-1.2-P2205 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-27 | 1.2 | 230 | U | 70 | AIS | UDB-1.2 | INTEGRA UPS DB PNL | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | PA+R4P | SHC GRAM CABINET (Cable Only) | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / SERVER ROOM | L1, N, PE | B073-017AC0003 → PSP/BCN(INTEGRA)TRAY → B073-017AC0006 → B073-016AT0001 → B073-016AT0014 → B073-016AT0015 → B073-016AT0013 → END
|  |  |  | PE-L1-2C4-07 | PE-L1-3C4-15 | ELE-AIS-0011 | ADD |  |  | 2134 | INT-ACDB-1.3-P2214 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 0.01 | 230 | N | 70 | AIS | ЩГП-1.3 | INTEGRA AC DB PNL | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | PA+R4P | SHC GRAM CABINET (Cable Only) | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / SERVER ROOM | L1, N, PE | B073-017AC0005 → PSP/BCN(INTEGRA)TRAY → B073-017AC0007 → B073-016AT0001 → B073-016AT0014 → B073-016AT0015 → B073-016AT0013 → END
|  |  |  | PE-L1-2C4-07 | PE-L1-3C4-15 | ELE-AIS-0012 | ADD |  |  | 2135 | INT-ACDB-1.3-P2215 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 2 | 230 | N | 55 | AIS | ЩГП-1.3 | INTEGRA AC DB PNL | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | TK31 | NETWORK EQUIPMENT CABINET (Cable Only) | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / SERVER ROOM | L1, N, PE | B073-017AC0005 → PSP/BCN(INTEGRA)TRAY → B073-017AC0007 → B073-016AT0001 → END
|  |  |  | PE-L1-2C4-07 | PE-L1-3C4-27 | ELE-AIS-0013 | ADD |  |  | 2136 | INT-UDB-1.2-P2206 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-27 | 2 | 230 | U | 55 | AIS | UDB-1.2 | INTEGRA UPS DB PNL | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | TK31 | NETWORK EQUIPMENT CABINET (Cable Only) | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / SERVER ROOM | L1, N, PE | B073-017AC0003 → PSP/BCN(INTEGRA)TRAY → B073-017AC0006 → B073-016AT0001 → END
|  |  |  | PE-L1-2C4-07 | PE-L1-3C4-15 | ELE-AIS-0014 | ADD |  |  | 2137 | INT-ACDB-1.3-P2216 | 0.6/1kV CU/XLPE/LSZH | 3C x 4sqmm | PE-L1-3C4-15 | 0.14 | 230 | N | 55 | AIS | ЩГП-1.3 | INTEGRA AC DB PNL | 25_ADMINSTRATIVE AND HOUSEHOLD BUILDING | L1, N, PE | TK31 | NETWORK EQUIPMENT CABINET (Cable Only) | 25_ADMINISTRATIVE AND HOUSEHOLD BUILDING / SERVER ROOM | L1, N, PE | B073-017AC0005 → PSP/BCN(INTEGRA)TRAY → B073-017AC0007 → B073-016AT0001 → END
[5 empty] | PE-L1-1C185-05 | BAT-B0-001 | DONE(10/27) | DONE |  | 2138 | B0-CH-64701-P2001 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 264 | 220 | D | 30 | DC & UPS | B0-CH-64701 | COMMON BATTERY CHARGER - A | 1.2_LEB FOR BLOCK #1 | L+ | B0-FC-64701 | COMMON BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L+ | B164-006GT0207 → B164-006GT0208 → B164-006GT0009 → END
[5 empty] | PE-L1-1C185-05 |  | DONE(10/27) | DONE |  | 2139 | B0-CH-64701-P2002 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 264 | 220 | D | 30 | DC & UPS | B0-CH-64701 | COMMON BATTERY CHARGER - A | 1.2_LEB FOR BLOCK #1 | L+ | B0-FC-64701 | COMMON BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L+ | B164-006GT0207 → B164-006GT0208 → B164-006GT0009 → END
[5 empty] | PE-L1-1C185-05 |  | DONE(10/27) | DONE |  | 2140 | B0-CH-64701-P2003 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 264 | 220 | D | 30 | DC & UPS | B0-CH-64701 | COMMON BATTERY CHARGER - A | 1.2_LEB FOR BLOCK #1 | L+ | B0-FC-64701 | COMMON BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L+ | B164-006GT0207 → B164-006GT0208 → B164-006GT0009 → END
[5 empty] | PE-L1-1C185-05 |  | DONE(10/27) | DONE |  | 2141 | B0-CH-64701-P2004 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 264 | 220 | D | 30 | DC & UPS | B0-CH-64701 | COMMON BATTERY CHARGER - A | 1.2_LEB FOR BLOCK #1 | L+ | B0-FC-64701 | COMMON BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L+ | B164-006GT0207 → B164-006GT0208 → B164-006GT0009 → END
[5 empty] | PE-L1-1C185-05 |  | DONE(10/27) | DONE |  | 2142 | B0-CH-64701-P2005 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 264 | 220 | D | 30 | DC & UPS | B0-CH-64701 | COMMON BATTERY CHARGER - A | 1.2_LEB FOR BLOCK #1 | L- | B0-FC-64701 | COMMON BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L- | B164-006GT0207 → B164-006GT0208 → B164-006GT0009 → END
[5 empty] | PE-L1-1C185-05 |  | DONE(10/27) | DONE |  | 2143 | B0-CH-64701-P2006 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 264 | 220 | D | 30 | DC & UPS | B0-CH-64701 | COMMON BATTERY CHARGER - A | 1.2_LEB FOR BLOCK #1 | L- | B0-FC-64701 | COMMON BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L- | B164-006GT0207 → B164-006GT0208 → B164-006GT0009 → END
[5 empty] | PE-L1-1C185-05 |  | DONE(10/27) | DONE |  | 2144 | B0-CH-64701-P2007 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 264 | 220 | D | 30 | DC & UPS | B0-CH-64701 | COMMON BATTERY CHARGER - A | 1.2_LEB FOR BLOCK #1 | L- | B0-FC-64701 | COMMON BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L- | B164-006GT0207 → B164-006GT0208 → B164-006GT0009 → END
[5 empty] | PE-L1-1C185-05 |  | DONE(10/27) | DONE |  | 2145 | B0-CH-64701-P2008 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 264 | 220 | D | 30 | DC & UPS | B0-CH-64701 | COMMON BATTERY CHARGER - A | 1.2_LEB FOR BLOCK #1 | L- | B0-FC-64701 | COMMON BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L- | B164-006GT0207 → B164-006GT0208 → B164-006GT0009 → END
[5 empty] | PE-L1-1C185-05 | BAT-B0-002 | DONE(10/27) | DONE |  | 2146 | B0-FC-64701-P2001 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 264 | 220 | D | 40 | DC & UPS | B0-FC-64701 | COMMON BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L+ | B0-BAT-64701 | COMMON BATTERY RACK-1 | 1.2_LEB FOR BLOCK #1 | L+ | B064-007AC0005 → END
[5 empty] | PE-L1-1C185-05 |  | DONE(10/27) | DONE |  | 2147 | B0-FC-64701-P2002 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 264 | 220 | D | 40 | DC & UPS | B0-FC-64701 | COMMON BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L+ | B0-BAT-64701 | COMMON BATTERY RACK-1 | 1.2_LEB FOR BLOCK #1 | L+ | B064-007AC0005 → END
[5 empty] | PE-L1-1C185-05 |  | DONE(10/27) | DONE |  | 2148 | B0-FC-64701-P2003 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 264 | 220 | D | 30 | DC & UPS | B0-FC-64701 | COMMON BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L+ | B0-BAT-64702 | COMMON BATTERY RACK-2 | 1.2_LEB FOR BLOCK #1 | L+ | B064-007AC0008 → END
[5 empty] | PE-L1-1C185-05 |  | DONE(10/27) | DONE |  | 2149 | B0-FC-64701-P2004 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 264 | 220 | D | 30 | DC & UPS | B0-FC-64701 | COMMON BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L+ | B0-BAT-64702 | COMMON BATTERY RACK-2 | 1.2_LEB FOR BLOCK #1 | L+ | B064-007AC0008 → END
[5 empty] | PE-L1-1C185-05 |  | DONE(10/27) | DONE |  | 2150 | B0-FC-64701-P2005 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 264 | 220 | D | 30 | DC & UPS | B0-FC-64701 | COMMON BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L- | B0-BAT-64701 | COMMON BATTERY RACK-1 | 1.2_LEB FOR BLOCK #1 | L- | B064-007AC0007 → END
[5 empty] | PE-L1-1C185-05 |  | DONE(10/27) | DONE |  | 2151 | B0-FC-64701-P2006 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 264 | 220 | D | 30 | DC & UPS | B0-FC-64701 | COMMON BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L- | B0-BAT-64701 | COMMON BATTERY RACK-1 | 1.2_LEB FOR BLOCK #1 | L- | B064-007AC0007 → END
[5 empty] | PE-L1-1C185-05 |  | DONE(10/27) | DONE |  | 2152 | B0-FC-64701-P2007 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 264 | 220 | D | 30 | DC & UPS | B0-FC-64701 | COMMON BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L- | B0-BAT-64702 | COMMON BATTERY RACK-2 | 1.2_LEB FOR BLOCK #1 | L- | B064-007AC0006 → END
[5 empty] | PE-L1-1C185-05 |  | DONE(10/27) | DONE |  | 2153 | B0-FC-64701-P2008 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 264 | 220 | D | 30 | DC & UPS | B0-FC-64701 | COMMON BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L- | B0-BAT-64702 | COMMON BATTERY RACK-2 | 1.2_LEB FOR BLOCK #1 | L- | B064-007AC0006 → END
[5 empty] | PE-L1-1C185-05 | BAT-B1-001 | DONE(10/27) | DONE |  | 2154 | B1-CH-64701-P2001 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 300 | 220 | D | 30 | DC & UPS | B1-CH-64701 | BLOCK #1 BATTERY CHARGER - A | 1.2_LEB FOR BLOCK #1 | L+ | B1-FC-64701 | BLOCK #1 BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L+ | B164-006HT0203 → B164-006HT0204 → B164-006HT0007 → END
[5 empty] | PE-L1-1C185-05 |  | DONE(10/27) | DONE |  | 2155 | B1-CH-64701-P2002 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 300 | 220 | D | 30 | DC & UPS | B1-CH-64701 | BLOCK #1 BATTERY CHARGER - A | 1.2_LEB FOR BLOCK #1 | L+ | B1-FC-64701 | BLOCK #1 BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L+ | B164-006HT0203 → B164-006HT0204 → B164-006HT0007 → END
[5 empty] | PE-L1-1C185-05 |  | DONE(10/27) | DONE |  | 2156 | B1-CH-64701-P2003 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 300 | 220 | D | 30 | DC & UPS | B1-CH-64701 | BLOCK #1 BATTERY CHARGER - A | 1.2_LEB FOR BLOCK #1 | L+ | B1-FC-64701 | BLOCK #1 BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L+ | B164-006HT0203 → B164-006HT0204 → B164-006HT0007 → END
[5 empty] | PE-L1-1C185-05 |  | DONE(10/27) | DONE |  | 2157 | B1-CH-64701-P2004 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 300 | 220 | D | 30 | DC & UPS | B1-CH-64701 | BLOCK #1 BATTERY CHARGER - A | 1.2_LEB FOR BLOCK #1 | L+ | B1-FC-64701 | BLOCK #1 BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L+ | B164-006HT0203 → B164-006HT0204 → B164-006HT0007 → END
[5 empty] | PE-L1-1C185-05 |  | DONE(10/27) | DONE |  | 2158 | B1-CH-64701-P2005 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 300 | 220 | D | 30 | DC & UPS | B1-CH-64701 | BLOCK #1 BATTERY CHARGER - A | 1.2_LEB FOR BLOCK #1 | L- | B1-FC-64701 | BLOCK #1 BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L- | B164-006HT0203 → B164-006HT0204 → B164-006HT0007 → END
[5 empty] | PE-L1-1C185-05 |  | DONE(10/27) | DONE |  | 2159 | B1-CH-64701-P2006 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 300 | 220 | D | 30 | DC & UPS | B1-CH-64701 | BLOCK #1 BATTERY CHARGER - A | 1.2_LEB FOR BLOCK #1 | L- | B1-FC-64701 | BLOCK #1 BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L- | B164-006HT0203 → B164-006HT0204 → B164-006HT0007 → END
[5 empty] | PE-L1-1C185-05 |  | DONE(10/27) | DONE |  | 2160 | B1-CH-64701-P2007 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 300 | 220 | D | 30 | DC & UPS | B1-CH-64701 | BLOCK #1 BATTERY CHARGER - A | 1.2_LEB FOR BLOCK #1 | L- | B1-FC-64701 | BLOCK #1 BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L- | B164-006HT0203 → B164-006HT0204 → B164-006HT0007 → END
[5 empty] | PE-L1-1C185-05 |  | DONE(10/27) | DONE |  | 2161 | B1-CH-64701-P2008 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 300 | 220 | D | 30 | DC & UPS | B1-CH-64701 | BLOCK #1 BATTERY CHARGER - A | 1.2_LEB FOR BLOCK #1 | L- | B1-FC-64701 | BLOCK #1 BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L- | B164-006HT0203 → B164-006HT0204 → B164-006HT0007 → END
[5 empty] | PE-L1-1C185-05 | BAT-B1-002 | DONE(10/27) | DONE |  | 2162 | B1-FC-64701-P2001 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 300 | 220 | D | 40 | DC & UPS | B1-FC-64701 | BLOCK #1 BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L+ | B1-BAT-64701 | BLOCK #1 BATTERY RACK-1 | 1.2_LEB FOR BLOCK #1 | L+ | B064-007AC0004 → END
[5 empty] | PE-L1-1C185-05 |  | DONE(10/27) | DONE |  | 2163 | B1-FC-64701-P2002 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 300 | 220 | D | 40 | DC & UPS | B1-FC-64701 | BLOCK #1 BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L+ | B1-BAT-64701 | BLOCK #1 BATTERY RACK-1 | 1.2_LEB FOR BLOCK #1 | L+ | B064-007AC0004 → END
[5 empty] | PE-L1-1C185-05 |  | DONE(10/27) | DONE |  | 2164 | B1-FC-64701-P2003 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 300 | 220 | D | 30 | DC & UPS | B1-FC-64701 | BLOCK #1 BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L+ | B1-BAT-64702 | BLOCK #1 BATTERY RACK-2 | 1.2_LEB FOR BLOCK #1 | L+ | B064-007AC0001 → END
[5 empty] | PE-L1-1C185-05 |  | DONE(10/27) | DONE |  | 2165 | B1-FC-64701-P2004 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 300 | 220 | D | 30 | DC & UPS | B1-FC-64701 | BLOCK #1 BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L+ | B1-BAT-64702 | BLOCK #1 BATTERY RACK-2 | 1.2_LEB FOR BLOCK #1 | L+ | B064-007AC0001 → END
[5 empty] | PE-L1-1C185-05 |  | DONE(10/27) | DONE |  | 2166 | B1-FC-64701-P2005 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 300 | 220 | D | 30 | DC & UPS | B1-FC-64701 | BLOCK #1 BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L- | B1-BAT-64701 | BLOCK #1 BATTERY RACK-1 | 1.2_LEB FOR BLOCK #1 | L- | B064-007AC0002 → END
[5 empty] | PE-L1-1C185-05 |  | DONE(10/27) | DONE |  | 2167 | B1-FC-64701-P2006 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 300 | 220 | D | 30 | DC & UPS | B1-FC-64701 | BLOCK #1 BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L- | B1-BAT-64701 | BLOCK #1 BATTERY RACK-1 | 1.2_LEB FOR BLOCK #1 | L- | B064-007AC0002 → END
[5 empty] | PE-L1-1C185-05 |  | DONE(10/27) | DONE |  | 2168 | B1-FC-64701-P2007 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 300 | 220 | D | 40 | DC & UPS | B1-FC-64701 | BLOCK #1 BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L- | B1-BAT-64702 | BLOCK #1 BATTERY RACK-2 | 1.2_LEB FOR BLOCK #1 | L- | B064-007AC0003 → END
[5 empty] | PE-L1-1C185-05 |  | DONE(10/27) | DONE |  | 2169 | B1-FC-64701-P2008 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 300 | 220 | D | 40 | DC & UPS | B1-FC-64701 | BLOCK #1 BATTERY FUSE BOX | 1.2_LEB FOR BLOCK #1 | L- | B1-BAT-64702 | BLOCK #1 BATTERY RACK-2 | 1.2_LEB FOR BLOCK #1 | L- | B064-007AC0003 → END
[5 empty] | PE-L1-1C185-05 | BAT-B2-001 | ADD |  |  | 2170 | B2-CH-64701-P2001 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 300 | 220 | D | 40 | DC & UPS | B2-CH-64701 | BLOCK #2 BATTERY CHARGER - A | 1.3_LEB FOR BLOCK #2 | L+ | B2-FC-64701 | BLCOK #2 BATTERY FUSE BOX | 1.3_LEB FOR BLOCK #2 | L+ | B264-016DT0061 → B264-016DT0060 → END
[5 empty] | PE-L1-1C185-05 |  | ADD |  |  | 2171 | B2-CH-64701-P2002 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 300 | 220 | D | 40 | DC & UPS | B2-CH-64701 | BLOCK #2 BATTERY CHARGER - A | 1.3_LEB FOR BLOCK #2 | L+ | B2-FC-64701 | BLCOK #2 BATTERY FUSE BOX | 1.3_LEB FOR BLOCK #2 | L+ | B264-016DT0061 → B264-016DT0060 → END
[5 empty] | PE-L1-1C185-05 |  | ADD |  |  | 2172 | B2-CH-64701-P2003 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 300 | 220 | D | 40 | DC & UPS | B2-CH-64701 | BLOCK #2 BATTERY CHARGER - A | 1.3_LEB FOR BLOCK #2 | L+ | B2-FC-64701 | BLCOK #2 BATTERY FUSE BOX | 1.3_LEB FOR BLOCK #2 | L+ | B264-016DT0061 → B264-016DT0060 → END
[5 empty] | PE-L1-1C185-05 |  | ADD |  |  | 2173 | B2-CH-64701-P2004 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 300 | 220 | D | 40 | DC & UPS | B2-CH-64701 | BLOCK #2 BATTERY CHARGER - A | 1.3_LEB FOR BLOCK #2 | L+ | B2-FC-64701 | BLCOK #2 BATTERY FUSE BOX | 1.3_LEB FOR BLOCK #2 | L+ | B264-016DT0061 → B264-016DT0060 → END
[5 empty] | PE-L1-1C185-05 |  | ADD |  |  | 2174 | B2-CH-64701-P2005 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 300 | 220 | D | 40 | DC & UPS | B2-CH-64701 | BLOCK #2 BATTERY CHARGER - A | 1.3_LEB FOR BLOCK #2 | L- | B2-FC-64701 | BLCOK #2 BATTERY FUSE BOX | 1.3_LEB FOR BLOCK #2 | L- | B264-016DT0061 → B264-016DT0060 → END
[5 empty] | PE-L1-1C185-05 |  | ADD |  |  | 2175 | B2-CH-64701-P2006 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 300 | 220 | D | 40 | DC & UPS | B2-CH-64701 | BLOCK #2 BATTERY CHARGER - A | 1.3_LEB FOR BLOCK #2 | L- | B2-FC-64701 | BLCOK #2 BATTERY FUSE BOX | 1.3_LEB FOR BLOCK #2 | L- | B264-016DT0061 → B264-016DT0060 → END
[5 empty] | PE-L1-1C185-05 |  | ADD |  |  | 2176 | B2-CH-64701-P2007 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 300 | 220 | D | 40 | DC & UPS | B2-CH-64701 | BLOCK #2 BATTERY CHARGER - A | 1.3_LEB FOR BLOCK #2 | L- | B2-FC-64701 | BLCOK #2 BATTERY FUSE BOX | 1.3_LEB FOR BLOCK #2 | L- | B264-016DT0061 → B264-016DT0060 → END
[5 empty] | PE-L1-1C185-05 |  | ADD |  |  | 2177 | B2-CH-64701-P2008 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 300 | 220 | D | 40 | DC & UPS | B2-CH-64701 | BLOCK #2 BATTERY CHARGER - A | 1.3_LEB FOR BLOCK #2 | L- | B2-FC-64701 | BLCOK #2 BATTERY FUSE BOX | 1.3_LEB FOR BLOCK #2 | L- | B264-016DT0061 → B264-016DT0060 → END
[5 empty] | PE-L1-1C185-05 | BAT-B2-002 | ADD |  |  | 2178 | B2-FC-64701-P2001 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 300 | 220 | D | 40 | DC & UPS | B2-FC-64701 | BLCOK #2 BATTERY FUSE BOX | 1.3_LEB FOR BLOCK #2 | L+ | B2-BAT-64701 | BLCOK #2 BATTERY RACK-1 | 1.3_LEB FOR BLOCK #2 | L+ | B264-007AC0001 → END
[5 empty] | PE-L1-1C185-05 |  | ADD |  |  | 2179 | B2-FC-64701-P2002 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 300 | 220 | D | 40 | DC & UPS | B2-FC-64701 | BLCOK #2 BATTERY FUSE BOX | 1.3_LEB FOR BLOCK #2 | L+ | B2-BAT-64701 | BLCOK #2 BATTERY RACK-1 | 1.3_LEB FOR BLOCK #2 | L+ | B264-007AC0001 → END
[5 empty] | PE-L1-1C185-05 |  | ADD |  |  | 2180 | B2-FC-64701-P2003 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 300 | 220 | D | 30 | DC & UPS | B2-FC-64701 | BLCOK #2 BATTERY FUSE BOX | 1.3_LEB FOR BLOCK #2 | L+ | B2-BAT-64702 | BLCOK #2 BATTERY RACK-2 | 1.3_LEB FOR BLOCK #2 | L+ | B264-007AC0004 → END
[5 empty] | PE-L1-1C185-05 |  | ADD |  |  | 2181 | B2-FC-64701-P2004 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-05 | 300 | 220 | D | 30 | DC & UPS | B2-FC-64701 | BLCOK #2 BATTERY FUSE BOX | 1.3_LEB FOR BLOCK #2 | L+ | B2-BAT-64702 | BLCOK #2 BATTERY RACK-2 | 1.3_LEB FOR BLOCK #2 | L+ | B264-007AC0004 → END
[5 empty] | PE-L1-1C185-02 |  | ADD |  |  | 2182 | B2-FC-64701-P2005 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-02 | 300 | 220 | D | 30 | DC & UPS | B2-FC-64701 | BLCOK #2 BATTERY FUSE BOX | 1.3_LEB FOR BLOCK #2 | L- | B2-BAT-64701 | BLCOK #2 BATTERY RACK-1 | 1.3_LEB FOR BLOCK #2 | L- | B264-007AC0002 → END
[5 empty] | PE-L1-1C185-04 |  | ADD |  |  | 2183 | B2-FC-64701-P2006 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-04 | 300 | 220 | D | 30 | DC & UPS | B2-FC-64701 | BLCOK #2 BATTERY FUSE BOX | 1.3_LEB FOR BLOCK #2 | L- | B2-BAT-64701 | BLCOK #2 BATTERY RACK-1 | 1.3_LEB FOR BLOCK #2 | L- | B264-007AC0002 → END
[5 empty] | PE-L1-1C185-02 |  | ADD |  |  | 2184 | B2-FC-64701-P2007 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-02 | 300 | 220 | D | 40 | DC & UPS | B2-FC-64701 | BLCOK #2 BATTERY FUSE BOX | 1.3_LEB FOR BLOCK #2 | L- | B2-BAT-64702 | BLCOK #2 BATTERY RACK-2 | 1.3_LEB FOR BLOCK #2 | L- | B264-007AC0003 → END
[5 empty] | PE-L1-1C185-04 |  | ADD |  |  | 2185 | B2-FC-64701-P2008 | 0.6/1kV CU/XLPE/LSZH | 1C x 185sqmm | PE-L1-1C185-04 | 300 | 220 | D | 40 | DC & UPS | B2-FC-64701 | BLCOK #2 BATTERY FUSE BOX | 1.3_LEB FOR BLOCK #2 | L- | B2-BAT-64702 | BLCOK #2 BATTERY RACK-2 | 1.3_LEB FOR BLOCK #2 | L- | B264-007AC0003 → END