## Table 1
DOCUMENT TITLE: / НАЗВАНИЕ ДОКУМЕНТА: FIN FAN COOLER_ WIRING DIAGRAM
ABSTRACT / АННОТАЦИЯ This document provides applicable to Fin Fan Cooler_ Wiring diagram
R01 | [7 empty] | Y.G.OH
Rev. Реви зия | [7 empty] | Approved Утвердил |  | Adapted by PSP LLP Адаптирова но ТОО
«ПСП»
REVISION DESCRIPTION SHEET
Rev.
R01
Hold No.
TURKISTAN CCGT PROJECT
REVISION DESCRIPTION SHEET ЛИСТ ОПИСАНИЯ РЕВИЗИИ
Rev. Рев.
R01
Hold No. Номер док-та «До уточнени я»
GENERAL NOTE
NOTE
1. THIS DOCUMENT AIMS TO INDICATED ALL CABLE TYPE AND VOLUME FOR USED IN THE FFC. 2. ALSO, THE SCOPE OF SUPPLY BETWEEN DOOSAN AND DTS IS MARKED AS SCOPE OD SUPPLY. 3. ALL TYPE OF CABLE QUANTITY CALCULATIONS FOR CONSIDERING ACC INSTALLATION STATUS AND CABLE TRAY ROUTE BY DTS. 4. THE QUANTITY CALCULATION FORMULA IS INCLUDED IN THE NATIVE FILE AND SUBMITTED. 5. REFERENCE DOCUMENT LIST 1) CCP-W-B182-09-ME-H05-0002 - Fin Fan Cooler_Raceway drawing (Typical & Install detail & BOM) 2) CCP-W-B182-09-ME-P14-0005 - Fin Fan Cooler_Cable Block Diagram 3) CCP-W-B182-09-ME-E02-0001 Fin Fan Cooler_Wiring diagrams 4) CCP-W-B182-09-ME-P14-0005 Fin Fan Cooler_Lighting Data Sheet & Outline Drawing 6. THE RED COLOR IS DESIGN & SUPPLIED BY DE
SUB TOTAL CABLE BOM LIST FOR DTS DESIGN & SUPPLY
S.N ITEM Cable Sepc TYPE VOLUME Unit Remark
1 | [5 empty] | T-CU/PVC/AMS/FRLS-PVC | [5 empty] | 1Px1.0mm2 |  | 621
2 | [11 empty] | by DE P x1.0mm2 |  | 144
3 | [11 empty] | by DE P x1.0mm2 |  | 44
4 | [11 empty] | 8Px1.0mm2 |  | 348
5 LIGHTING & EHT, REDUCER HEATER | [5 empty] | CU/XLPE/FR-PVC | [5 empty] | 2C+E |  | 3644
6 FAN MOTOR | [11 empty] | 3C+E |  | 968
7 DELUGE APRAY PUMP | [11 empty] | 3C+E |  | 308
8 FAN MOTOR SPACE HEATER | [11 empty] | 2C+E |  | 968
9 MOV POWER | [11 empty] | 3C+E |  | 378
10 |  |  |  |  | DE | 1Px1.0mm2
11 | [5 empty] | CU/FR-PVC | [5 empty] | Y/G 70mm2
12 | [5 empty] | CU/FR-PVC | [5 empty] | Y/G 16mm2
CABLE SCHEDULE FFC - CABLE SCHEDULE FOR SIGNAL CABLE PJT Name : Fin Fan Cooler Project, 104000
|  | CABLE | CABLE |  | SIGNAL | LENGTH |  |  |  |  | FROM |  |  |  |  | TO
S/N | SYSTEM | NUMBER | TYPE | SPEC. | TYPE | Calculated (M) | Cutting loss | Coner margin as route | Streat length | Design margin | KKS NO. | Cable number | DESCRIPTION | LOCATION / DWG NO | ELEVATION/GRID (mm) | KKS NO. | DESCRIPTION | LOCATION / DWG NO | ELEVATION/GRID | CABLE ROUTE
A1~A3 | FFC SYSTEM | B1-TT66001-5001 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | 4~20mA | 32 | 2 | 10 | 20 |  | B1-TT66001 | 5001 | TEMPERATURE TRANSMITTER | FIELD, Around Main pipe TP | EL. +1726.3 | B1-JBA-6601 | Analog Junction Box | FFC GROUND | EL. +1500 | TI-300-101 / TI-300-103 / TI-100-101 / TI-100-102 / TI-100-105
A4~A6 | FFC SYSTEM | B1-TT66002-5002 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | 4~20mA | 37 | 2 | 10 | 25 |  | B1-TT66002 | 5002 | TEMPERATURE TRANSMITTER | FIELD, Around Main pipe TP | EL. +1726.3 | B1-JBA-6601 | Analog Junction Box | FFC GROUND | EL. +1500 | TI-300-101 / TI-300-103 / TI-100-101 / TI-100-102 / TI-100-105
A7~A9 | FFC SYSTEM | B1-PT66001-5003 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | 4~20mA | 22 | 2 | 10 | 10 |  | B1-PT66001 | 5003 | PRESSURE TRANSMITTER | FIELD, Around Pump Discharge Pipe | EL. +1626.3 | B1-JBA-6601 | Analog Junction Box | FFC GROUND | EL. +1500 | TI-300-101 / TI-300-103 / TI-100-101
A10~A12 | FFC SYSTEM | B1-PT66002-5004 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | 4~20mA | 22 | 2 | 10 | 10 |  | B1-PT66002 | 5004 | PRESSURE TRANSMITTER | FIELD, Around Pump Discharge Pipe | EL. +1626.3 | B1-JBA-6601 | Analog Junction Box | FFC GROUND | EL. +1500 | TI-300-101 / TI-300-103 / TI-100-101
A13~A15 | FFC SYSTEM | B1-LT66001-5005 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | 4~20mA | 32 | 2 | 10 | 20 |  | B1-LT66001 | 5005 | LEVEL TRANSMITTER | FIELD, Deluge tank | EL. +1726.3 | B1-JBA-6601 | Analog Junction Box | FFC GROUND | EL. +1000 | TI-300-101 / TI-300-103 / TI-100-101
A16~A18 | FFC SYSTEM | B1-LT66002-5006 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | 4~20mA | 37 | 2 | 10 | 25 |  | B1-LT66002 | 5006 | LEVEL TRANSMITTER | FIELD, Deluge tank | EL. +1726.3 | B1-JBA-6601 | Analog Junction Box | FFC GROUND | EL. +1000 | TI-300-101 / TI-300-103 / TI-100-101
A1~A2 | FFC SYSTEM | B1-VS66001-5007 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 27 | 2 | 5 | 20 |  | B1-VS66001 | 5007 | FAN 01 VIB SWICH | FAN MOTOR AROUND OF FAN 01 | EL. +3726.3 | B1-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-101 / TI-300-102
A3~A4 | FFC SYSTEM | B1-VS66002-5008 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 37 | 2 | 5 | 30 |  | B1-VS66002 | 5008 | FAN 02 VIB SWICH | FAN MOTOR AROUND OF FAN 02 | EL. +3726.3 | B1-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-101 / TI-300-102
A5~A6 | FFC SYSTEM | B1-VS66003-5009 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 17 | 2 | 5 | 10 |  | B1-VS66003 | 5009 | FAN 03 VIB SWICH | FAN MOTOR AROUND OF FAN 03 | EL. +3726.3 | B1-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-101 / TI-300-102
A7~A8 | FFC SYSTEM | B1-VS66004-5010 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 27 | 2 | 5 | 20 |  | B1-VS66004 | 5010 | FAN 04 VIB SWICH | FAN MOTOR AROUND OF FAN 04 | EL. +3726.3 | B1-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-101 / TI-300-102
A9~A10 | FFC SYSTEM | B1-VS66005-5011 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 27 | 2 | 5 | 20 |  | B1-VS66005 | 5011 | FAN 05 VIB SWICH | FAN MOTOR AROUND OF FAN 05 | EL. +3726.3 | B1-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-101 / TI-300-103
A11~A12 | FFC SYSTEM | B1-VS66006-5012 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 37 | 2 | 5 | 30 |  | B1-VS66006 | 5012 | FAN 06 VIB SWICH | FAN MOTOR AROUND OF FAN 06 | EL. +3726.3 | B1-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-101 / TI-300-103
A13~A14 | FFC SYSTEM | B1-VS66007-5013 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 32 | 2 | 5 | 25 |  | B1-VS66007 | 5013 | FAN 07 VIB SWICH | FAN MOTOR AROUND OF FAN 07 | EL. +3726.3 | B1-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-101 / TI-300-103
A15~A16 | FFC SYSTEM | B1-VS66008-5014 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 42 | 2 | 5 | 35 |  | B1-VS66008 | 5014 | FAN 08 VIB SWICH | FAN MOTOR AROUND OF FAN 08 | EL. +3726.3 | B1-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-101 / TI-300-103
A17~A18 | FFC SYSTEM | B1-VS66009-5015 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 42 | 2 | 5 | 35 |  | B1-VS66009 | 5015 | FAN 09 VIB SWICH | FAN MOTOR AROUND OF FAN 09 | EL. +3726.3 | B1-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-101 / TI-300-103
A19~A20 | FFC SYSTEM | B1-VS66010-5016 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 47 | 2 | 5 | 40 |  | B1-VS66010 | 5016 | FAN 10 VIB SWICH | FAN MOTOR AROUND OF FAN 10 | EL. +3726.3 | B1-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-101 / TI-300-103
A21~A22 | FFC SYSTEM | B1-VS66011-5017 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 47 | 2 | 5 | 40 |  | B1-VS66011 | 5017 | FAN 11 VIB SWICH | FAN MOTOR AROUND OF FAN 11 | EL. +3726.3 | B1-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-101 / TI-300-103
A23~A24 | FFC SYSTEM | B1-VS66012-5018 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 57 | 2 | 5 | 50 |  | B1-VS66012 | 5018 | FAN 12 VIB SWICH | FAN MOTOR AROUND OF FAN 12 | EL. +3726.3 | B1-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-101 / TI-300-103
A1~A3 | FFC SYSTEM | B2-TT66001-5101 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | 4~20mA | 32 | 2 | 10 | 20 |  | B2-TT66001 | 5101 | TEMPERATURE TRANSMITTER | FIELD, Around Main pipe TP | EL. +1726.3 | B2-JBA-6601 | Analog Junction Box | FFC GROUND | EL. +1500 | TI-300-201 / TI-300-203 / TI-100-201 / TI-100-202 / TI-100-204
A4~A6 | FFC SYSTEM | B2-TT66002-5102 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | 4~20mA | 37 | 2 | 10 | 25 |  | B2-TT66002 | 5102 | TEMPERATURE TRANSMITTER | FIELD, Around Main pipe TP | EL. +1726.3 | B2-JBA-6601 | Analog Junction Box | FFC GROUND | EL. +1500 | TI-300-201 / TI-300-203 / TI-100-201 / TI-100-202 / TI-100-204
A7~A9 | FFC SYSTEM | B2-PT66001-5103 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | 4~20mA | 22 | 2 | 10 | 10 |  | B2-PT66001 | 5103 | PRESSURE TRANSMITTER | FIELD, Around Pump Discharge Pipe | EL. +1626.3 | B2-JBA-6601 | Analog Junction Box | FFC GROUND | EL. +1500 | TI-300-201 / TI-300-203 / TI-100-201 / TI-100-202 / TI-100-203
A10~A12 | FFC SYSTEM | B2-PT66002-5104 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | 4~20mA | 22 | 2 | 10 | 10 |  | B2-PT66002 | 5104 | PRESSURE TRANSMITTER | FIELD, Around Pump Discharge Pipe | EL. +1626.3 | B2-JBA-6601 | Analog Junction Box | FFC GROUND | EL. +1500 | TI-300-201 / TI-300-203 / TI-100-201 / TI-100-202 / TI-100-203
A13~A15 | FFC SYSTEM | B2-LT66001-5105 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | 4~20mA | 32 | 2 | 10 | 20 |  | B2-LT66001 | 5105 | LEVEL TRANSMITTER | FIELD, Deluge tank | EL. +1726.3 | B2-JBA-6601 | Analog Junction Box | FFC GROUND | EL. +1000 | TI-300-201 / TI-300-203 / TI-100-201 / TI-100-202 / TI-100-203
A16~A18 | FFC SYSTEM | B2-LT66002-5106 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | 4~20mA | 37 | 2 | 10 | 25 |  | B2-LT66002 | 5106 | LEVEL TRANSMITTER | FIELD, Deluge tank | EL. +1726.3 | B2-JBA-6601 | Analog Junction Box | FFC GROUND | EL. +1000 | TI-300-201 / TI-300-203 / TI-100-201 / TI-100-202 / TI-100-203
A1~A2 | FFC SYSTEM | B2-VS66001-5107 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 27 | 2 | 5 | 20 |  | B2-VS66001 | 5107 | FAN 01 VIB SWICH | FAN MOTOR AROUND OF FAN 01 | EL. +3726.3 | B2-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-201 / TI-300-202
A3~A4 | FFC SYSTEM | B2-VS66002-5108 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 37 | 2 | 5 | 30 |  | B2-VS66002 | 5108 | FAN 02 VIB SWICH | FAN MOTOR AROUND OF FAN 02 | EL. +3726.3 | B2-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-201 / TI-300-202
A5~A6 | FFC SYSTEM | B2-VS66003-5109 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 17 | 2 | 5 | 10 |  | B2-VS66003 | 5109 | FAN 03 VIB SWICH | FAN MOTOR AROUND OF FAN 03 | EL. +3726.3 | B2-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-201 / TI-300-202
A7~A8 | FFC SYSTEM | B2-VS66004-5110 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 27 | 2 | 5 | 20 |  | B2-VS66004 | 5110 | FAN 04 VIB SWICH | FAN MOTOR AROUND OF FAN 04 | EL. +3726.3 | B2-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-201 / TI-300-202
A9~A10 | FFC SYSTEM | B2-VS66005-5111 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 27 | 2 | 5 | 20 |  | B2-VS66005 | 5111 | FAN 05 VIB SWICH | FAN MOTOR AROUND OF FAN 05 | EL. +3726.3 | B2-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-201 / TI-300-203
A11~A12 | FFC SYSTEM | B2-VS66006-5112 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 37 | 2 | 5 | 30 |  | B2-VS66006 | 5112 | FAN 06 VIB SWICH | FAN MOTOR AROUND OF FAN 06 | EL. +3726.3 | B2-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-201 / TI-300-203
A13~A14 | FFC SYSTEM | B2-VS66007-5113 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 32 | 2 | 5 | 25 |  | B2-VS66007 | 5113 | FAN 07 VIB SWICH | FAN MOTOR AROUND OF FAN 07 | EL. +3726.3 | B2-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-201 / TI-300-203
A15~A16 | FFC SYSTEM | B2-VS66008-5114 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 42 | 2 | 5 | 35 |  | B2-VS66008 | 5114 | FAN 08 VIB SWICH | FAN MOTOR AROUND OF FAN 08 | EL. +3726.3 | B2-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-201 / TI-300-203
A17~A18 | FFC SYSTEM | B2-VS66009-5115 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 42 | 2 | 5 | 35 |  | B2-VS66009 | 5115 | FAN 09 VIB SWICH | FAN MOTOR AROUND OF FAN 09 | EL. +3726.3 | B2-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-201 / TI-300-203
A19~A20 | FFC SYSTEM | B2-VS66010-5116 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 47 | 2 | 5 | 40 |  | B2-VS66010 | 5116 | FAN 10 VIB SWICH | FAN MOTOR AROUND OF FAN 10 | EL. +3726.3 | B2-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-201 / TI-300-203
A21~A22 | FFC SYSTEM | B2-VS66011-5117 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 47 | 2 | 5 | 40 |  | B2-VS66011 | 5117 | FAN 11 VIB SWICH | FAN MOTOR AROUND OF FAN 11 | EL. +3726.3 | B2-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-201 / TI-300-203
A23~A24 | FFC SYSTEM | B2-VS66012-5118 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 57 | 2 | 5 | 50 |  | B2-VS66012 | 5118 | FAN 12 VIB SWICH | FAN MOTOR AROUND OF FAN 12 | EL. +3726.3 | B2-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-201 / TI-300-203
|  | Total add sum as 1Px1.0mm2 |  | 1Px1.0mm2 |  | 621
A19~A21 | FFC SYSTEM | B1-MOV32004-5050 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | 4~20mA | 42 | 2 | 10 | 30 |  | B1-MOV32004 | 5050 | MOV | SUUPPLIED BY DE, NOT INFORM, APPLIED ADD 10m FROM FTS MOV-66001 | EL. +1726.3 | B1-JBA-6601 | MARSHALLING PANEL | FFC GROUND | EL. +2426.3 | TI-300-101 / TI-300-103 / TI-100-101
A19~A21 | FFC SYSTEM | B2-MOV32004-5150 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | 4~20mA | 42 | 2 | 10 | 30 |  | B2-MOV32004 | 5150 | MOV | SUUPPLIED BY DE, NOT INFORM, APPLIED ADD 10m FROM FTS MOV-66001 | EL. +1726.3 | B1-JBA-6601 | MARSHALLING PANEL | FFC GROUND | EL. +2426.3 | TI-300-101 / TI-300-103 / TI-100-101
|  | Total add sum as 1Px1.0mm2 |  | 1Px1.0mm2 |  | 84
PJT Name : Fin Fan Cooler Project,
[12 empty] | FROM |  |  |  |  | TO
[7 empty] | Cutting loss |  |  | Streat length |  | KKS NO. | Cable number |  |  | ELEVATION/GRID (mm) | KKS NO.
[7 empty] | 2 |  |  | 60 |  | B1-JBA6601 | by DE |  |  | EL. +1726.3 | B1-PB-66001
[7 empty] | 2 |  |  | 60 |  | B2-JBA6601 | by DE |  |  | EL. +1726.3 | B2-PB-66001
THIS CABLE SUPPLY BY DOOSAN
[7 empty] | 2 |  |  | 15 |  | B1-JBY6601 | by DE |  |  | EL. +1726.3 | B1-PB-66001
[7 empty] | 2 |  |  | 15 |  | B2-JBY6601 | by DE |  |  | EL. +1726.3 | B2-PB-66001
THIS CABLE SUPPLY BY DOOSAN
[7 empty] | 2 |  |  | 85 |  | B1-MOV32004 | by DE |  |  | EL. +1726.3 | B1-PB-66001
[12 empty] | B1-MOV32004 |  |  |  | EL. +1726.3 | B1-PB-66001
[12 empty] | B1-MOV32004 |  |  |  | EL. +1726.3 | B1-PB-66001
[12 empty] | B1-MOV32004 |  |  |  | EL. +1726.3 | B1-PB-66001
[12 empty] | B1-MOV32004 |  |  |  | EL. +1726.3 | B1-PB-66001
[12 empty] | B1-MOV32004 |  |  |  | EL. +1726.3 | B1-PB-66001
[12 empty] | B1-MOV32004 |  |  |  | EL. +1726.3 | B1-PB-66001
[7 empty] | 2 |  |  | 75 |  | B1-MOV66001 | by DE |  |  | EL. +1726.3 | B2-PB-66001
[12 empty] | B1-MOV66001 |  |  |  | EL. +1726.3 | B2-PB-66001
[12 empty] | B1-MOV66001 |  |  |  | EL. +1726.3 | B2-PB-66001
[12 empty] | B1-MOV66001 |  |  |  | EL. +1726.3 | B2-PB-66001
[12 empty] | B1-MOV66001 |  |  |  | EL. +1726.3 | B2-PB-66001
[12 empty] | B1-MOV66001 |  |  |  | EL. +1726.3 | B2-PB-66001
[12 empty] | B1-MOV66001 |  |  |  | EL. +1726.3 | B2-PB-66001
[7 empty] | 2 |  |  | 85 |  | B2-MOV32004 | by DE |  |  | EL. +1726.3 | B1-PB-66001
[12 empty] | B2-MOV32004 |  |  |  | EL. +1726.3 | B1-PB-66001
[12 empty] | B2-MOV32004 |  |  |  | EL. +1726.3 | B1-PB-66001
[12 empty] | B2-MOV32004 |  |  |  | EL. +1726.3 | B1-PB-66001
[12 empty] | B2-MOV32004 |  |  |  | EL. +1726.3 | B1-PB-66001
[12 empty] | B2-MOV32004 |  |  |  | EL. +1726.3 | B1-PB-66001
[12 empty] | B2-MOV32004 |  |  |  | EL. +1726.3 | B1-PB-66001
[7 empty] | 2 |  |  | 75 |  | B2-MOV66001 | by DE |  |  | EL. +1726.3 | B2-PB-66001
[12 empty] | B2-MOV66001 |  |  |  | EL. +1726.3 | B2-PB-66001
[12 empty] | B2-MOV66001 |  |  |  | EL. +1726.3 | B2-PB-66001
[12 empty] | B2-MOV66001 |  |  |  | EL. +1726.3 | B2-PB-66001
[12 empty] | B2-MOV66001 |  |  |  | EL. +1726.3 | B2-PB-66001
[12 empty] | B2-MOV66001 |  |  |  | EL. +1726.3 | B2-PB-66001
[12 empty] | B2-MOV66001 |  |  |  | EL. +1726.3 | B2-PB-66001
THIS CABLE SUPPLY BY DOOSAN
PJT Name : Fin Fan Cooler Project,
Cable number
| SYSTEM | [10 empty] | 2001
| SYSTEM | [10 empty] | 2002
| SYSTEM | [10 empty] | 2003
| SYSTEM | [10 empty] | 2004
| SYSTEM | [10 empty] | 2005
| SYSTEM | [10 empty] | 2006
| SYSTEM | [10 empty] | 2007
| SYSTEM | [10 empty] | 2008
| SYSTEM | [10 empty] | 2009
| SYSTEM | [10 empty] | 2010
| SYSTEM | [10 empty] | 2011
| SYSTEM | [10 empty] | 2012
| SYSTEM | [10 empty] | 2013
| SYSTEM | [10 empty] | 2014
| SYSTEM | [10 empty] | 2015
| SYSTEM | [10 empty] | 2016
| SYSTEM | [10 empty] | 2101
| SYSTEM | [10 empty] | 2102
| SYSTEM | [10 empty] | 2103
| SYSTEM | [10 empty] | 2104
| SYSTEM | [10 empty] | 2105
| SYSTEM | [10 empty] | 2106
| SYSTEM | [10 empty] | 2107
| SYSTEM | [10 empty] | 2108
| SYSTEM | [10 empty] | 2109
| SYSTEM | [10 empty] | 2110
| SYSTEM | [10 empty] | 2111
| SYSTEM | [10 empty] | 2112
| SYSTEM | [10 empty] | 2113
| SYSTEM | [10 empty] | 2114
| SYSTEM | [10 empty] | 2115
| SYSTEM | [10 empty] | 2116
| SYSTEM | [10 empty] | 2201
| SYSTEM | [10 empty] | 2202
| SYSTEM | [10 empty] | 2203
| SYSTEM | [10 empty] | 2204
| SYSTEM | [10 empty] | 2205
| SYSTEM | [10 empty] | 2206
| SYSTEM | [10 empty] | 2207
| SYSTEM | [10 empty] | 2208
| SYSTEM | [10 empty] | 2209
| SYSTEM | [10 empty] | 2210
| SYSTEM | [10 empty] | 2211
| SYSTEM | [10 empty] | 2212
| SYSTEM | [10 empty] | 2213
| SYSTEM | [10 empty] | 2301
| SYSTEM | [10 empty] | 2302
| SYSTEM | [10 empty] | 2303
| SYSTEM | [10 empty] | 2304
| SYSTEM | [10 empty] | 2305
| SYSTEM | [10 empty] | 2306
| SYSTEM | [10 empty] | 2307
| SYSTEM | [10 empty] | 2308
| SYSTEM | [10 empty] | 2309
| SYSTEM | [10 empty] | 2310
| SYSTEM | [10 empty] | 2311
| SYSTEM | [10 empty] | 2312
| SYSTEM | [10 empty] | 2313
PJT Name : Fin Fan Cooler Project,
PJT Name : Fin Fan Cooler Project,
S/N | [5 empty] | Coner margin as route
3
1
1
3
1
1
0.5
0.5
0.5
0.5
0.5
0.5
0.5
0.5
0.5
0.5
0.5
0.5
0.5
0.5
0.5
0.5
0.5
0.5
0.5
0.5
0.5
0.5
0.5
0.5
0.5
0.5
0.5
0.5
0.5
0.5
0.5
0.5
0.5
0.5
0.5
0.5
Spec. No. GO 4133-KE11 Issued date : January 05, 2023
Specification FOR TFR-GV FR-PVC INSULATED GROUNDING WIRE
Prepared By S. H. CHO / Engineer
Checked By J. H. LEE / Manager
Approved By G. B. KIM / General Manager Cable Design Section
1. SCOPE
This specification covers copper conductor, FR-PVC insulated grounding wires mainly in accordance with IEC 60502 unless otherwise specified in this specification.
2. CONSTRUCTION AND MATERIAL 2.1 Conductor The conductor shall be plain annealed circular or compact stranded copper conductors complying with IEC 60228 and the attach table
2.2 Insulation The insulation shall be consist of extruded PVC compound complying with the requirements of IEC 60502. The average thickness of the insulation shall be not less than the value given in attached table and the minimum thickness at any point shall not fall below 90% of the specified value by more than 0.1 ㎜.
3.3 Color The color of insulation shall be yellow/green insulation. The ratio of yellow is about 30∼70%.
4. CHARACTERISTICS The characteristics of the wires shall comply with the following table.
* Treatment : Temperature 100±2℃, Duration 7days
5. TEST The following tests shall be conducted at manufacturer’s works. Testing method shall be in accordance with IEC 60502. 1) Construction test 2) Conductor resistance test 3) A.C withstand voltage test 4) Mechanical properties test before and after aging for insulation 5) Flame retardant test (IEC 60332-3-24) 6) Packing inspection
6. MARKING The following items shall be printed on the PVC insulation throughout the entire length of the cable. 1) Type of cable 2) Size of conductor 3) Manufacturer’s name 4) Year of manufacture 5) Length marking (every 1 meter) 7. PACKING The cable shall be wound on reel or coiled such as to prevent damage during transportation. The following description shall be marked by suitable method on the package. 1) Type of cable 2) Number of cores and size of conductor 3) Length of cable 4) Net and gross weight(when drum wound) 5) Manufacturer's name 6) Year of manufacture 7) Direction of rotation(when drum wound) 8) Number of cable drum
Attached table : TFR-GV
D2RAWING
Type of cable |  |  | TFR-GV
1 2 Not to scale
No.
1
2
Spec. No. GO 5569-KE11 Issued date : February 10, 2022
Specification FOR 0.6/1kV TFR-CV 0.6/1kV FR-PVC OVERSHEATHED POWER CABLE
Prepared By S. H. CHO / Engineer
Checked By M. H. YEOM / Manager
Approved By J. H. LEE / General Manager Cable Design Section
1. SCOPE
This specification covers 0.6/1KV copper conductor, cross-linked polyethylene(XLPE) insulated, flame retardant PVC oversheathed power cables mainly in accordance with IEC 60502 unless otherwise specified in this specification. This insulation is recommended for operation at maximum rated conductor temperature 90℃.
2. CONSTRUCTION AND MATERIAL
2.1 Conductor The conductor shall be of plain annealed circular stranded or plain annealed compacted circular stranded conductor in accordance with IEC 60228.
2.2 Insulation The insulation shall be of cross-linked polyethylene (XLPE). The average thickness shall be not less than the value given in the attached table and the minimum thickness at any point shall be not less than 90％ of the specified value by more than 0.1 mm. A suitable separator tape may be applied over the conductor.
2.3 Core identification The individual cores shall be identified by the colored tape over the conductor. and the color shall be in accordance with the following sequence.
1 core : White(natural) 2 core : Brown, Black
3 core : Brown, Black, Grey 3 core + PE : Brown, Black, Grey + Green/Yellow
4 core : Brown, Black, Grey, Blue 4 core + PE : Brown, Black, Grey, Blue+Green/Yellow
2.4 Cabling of cores The required number of cores shall be cabled with suitable fillers in round shape and a suitable tape shall be applied helically over the cabled cores.
2.5 Oversheath The oversheath shall be an extruded layer of flame retardant PVC compound. The minimum thickness at any point shall be not less than 80％ of the specified value by more than 0.2 mm.
3. MARKING
The following items shall be marked on the PVC oversheath throughout the entire length of the cable. 1) Rated Voltage 2) Type of Cable 3) Number of core and size of conductor 4) Manufacturer's name 5) Year of manufacture 6) Length marking 4. TEST The following test shall be conducted at manufacturer’s works. Testing method shall be in accordance with IEC 60502-1. 4.1 Routine tests 1) Measurement of the electrical resistance of conductors 2) Voltage test 4.2 Sample tests 1) Conductor examination 2) Check of dimensions 3) Hot set test for XLPE insulations 4.3 Type tests 1) Flame retardant test (IEC 60332-3-24) 5. PACKING AND MARKING The cable shall be wound on reel so as to prevent damage during transportation. The following description shall be marked on a flange of the reel. (1) Rated voltage (2) Type of cable (3) Number of cores and size of conductor (4) Length of cable (5) Net and gross weight (6) Manufacturer's name (7) Year of manufacture (8) Direction of rolling
Attached table : 0.6/1kV TFR-CV (2Core+PE) |  |  |  |  | Spec No. : GO 5569-KE11 Date : February 10, 2022 Page : 8 / 11
Thick. Of sheath ㎜
1.8
1.8
1.8
1.8
1.8
1.8
1.8
1.8
2
2.1
2.2
2.4
2.5
Spec. No. GO 4133-KE11 Issued date : January 05, 2023
Specification FOR TFR-GV FR-PVC INSULATED GROUNDING WIRE
Prepared By S. H. CHO / Engineer
Checked By J. H. LEE / Manager
Approved By G. B. KIM / General Manager Cable Design Section
1. SCOPE
This specification covers copper conductor, FR-PVC insulated grounding wires mainly in accordance with IEC 60502 unless otherwise specified in this specification.
2. CONSTRUCTION AND MATERIAL 2.1 Conductor The conductor shall be plain annealed circular or compact stranded copper conductors complying with IEC 60228 and the attach table
2.2 Insulation The insulation shall be consist of extruded PVC compound complying with the requirements of IEC 60502. The average thickness of the insulation shall be not less than the value given in attached table and the minimum thickness at any point shall not fall below 90% of the specified value by more than 0.1 ㎜.
3.3 Color The color of insulation shall be yellow/green insulation. The ratio of yellow is about 30∼70%.
4. CHARACTERISTICS The characteristics of the wires shall comply with the following table.
* Treatment : Temperature 100±2℃, Duration 7days
5. TEST The following tests shall be conducted at manufacturer’s works. Testing method shall be in accordance with IEC 60502. 1) Construction test 2) Conductor resistance test 3) A.C withstand voltage test 4) Mechanical properties test before and after aging for insulation 5) Flame retardant test (IEC 60332-3-24) 6) Packing inspection
6. MARKING The following items shall be printed on the PVC insulation throughout the entire length of the cable. 1) Type of cable 2) Size of conductor 3) Manufacturer’s name 4) Year of manufacture 5) Length marking (every 1 meter) 7. PACKING The cable shall be wound on reel or coiled such as to prevent damage during transportation. The following description shall be marked by suitable method on the package. 1) Type of cable 2) Number of cores and size of conductor 3) Length of cable 4) Net and gross weight(when drum wound) 5) Manufacturer's name 6) Year of manufacture 7) Direction of rotation(when drum wound) 8) Number of cable drum
Spec. No. HS 445R-3611 rev.2 Issued date : April 23, 2009 Revised 1 date : November 16 , 2011 Revised 2 date : February 18, 2013
Specification FOR 0.6/1KV TFR-CVV-I/C AMS PVC INSULATED ALUMINUM MYLAR TAPE INDIVIDUAL/COMMON SHIELDING FR-PVC OVERSHEATHED CONTROL CABLE
Prepared By S. M. PARK
Checked By J. H., LEE Approved By G. B. KIM
1. SCOPE
Rev.1→
Rev.2→ | A tinned copper wire(0.5 ㎟) or a tinned coated copper claded aluminum wire(0.75 ㎟) shall be inserted throughout the length, to contact with the aluminium side of this tape, for electrical grounding.
2.5 Assembly The required number of pairs or triads shall be assembled together with, suitable fillers if necessary, to form the compact circular form and a suitable binder tape may be applied helically over the cabled cores.
2.6 Common shielding
Rev.2→ | An aluminium-laminated plastic tape of the thickness about 0.06mm shall be applied over the assembled pairs or triads. A tinned copper wire(0.5 ㎟) or a tinned coated copper claded aluminum wire(0.75 ㎟) shall be inserted throughout the length, to contact with the aluminium side of this tape, for electrical grounding.
2.7 Outer sheath The outer sheath shall be an extruded layer of FR-PVC compound complying with the requirements of IEC 60502. The minimum thickness at any point shall be not fall below 80％ of the specified nominal value by more than 0.2 mm. 3. MARKING The following items shall be marked on the PVC oversheath throughout the entire length of the cable. 1) Type of cable 2) Number of core and size of conductor 3) Manufacturer's name 4) Year of manufacture 5) Length marking 4. TEST The following test shall be conducted at manufacturer’s works. Testing method shall be in accordance with IEC 60502-1. 4.1 Routine Tests 1) Conductor resistance test 2) A.C withstand voltage test 4.2 Sample Tests 1) Conductor examination and check of dimensions 2) Flame retardant of cable(IEC 60332-3-24)
Spec No. : HS 445R-3611rev.2 Date : February 18, 2013 Page : 4 / 7
5. PACKING The cable shall be wound on reel so as to prevent damage during transportation. The following description shall be marked on a flange of the reel. a) Direction of rotation of the reel b) Type of cable c) Number of conductors and conductor size d) Length e) Net weight f) Gross weight g) Manufacturer's name h) Year of manufacture i) Reel No. (if required)
Spec No. : HS 445R-3611rev.2 Date : February 18, 2013 Page : 5 / 7
● Structuer
7P 7T
6. DRAWING -- Pair or triad
-- Multi-pair or triad
P T Pair or Triad Filler P/S Tape Drain wire Al-mylar tape Sheath
● Att
No. of pairs
4 P
6 P
12 P
24 P
1 P
2 P
3 P
4 P
5 P
6 P
7 P
10 P
12 P
14 P
15 P
16 P
20 P
24 P
25 P
30 P
1P
2P
3P
4P
5P
6P
8P
10P
12P
16P
20P
1T
2T
3T
4T
5T
6T
7T
8T
10T
12T
15T
1T
2T
3T
4T
5T
6T
10T
☞ P : PAIR TYPE T : TRIAD TYPE Drain Wire : 0.5SQ(20/0.18)
2
7
3
1
6
4
5
2
7
3
1
6
4
5
P,T

## Sheet1
CABLE SCHEDULE FFC - CABLE SCHEDULE FOR SIGNAL CABLE PJT Name : Fin Fan Cooler Project, 104000
|  | CABLE | CABLE |  | SIGNAL | LENGTH |  |  |  |  | FROM |  |  |  |  | TO
S/N | SYSTEM | NUMBER | TYPE | SPEC. | TYPE | Calculated (M) | Cutting loss | Coner margin as route | Streat length | Design margin | KKS NO. | Cable number | DESCRIPTION | LOCATION / DWG NO | ELEVATION/GRID (mm) | KKS NO. | DESCRIPTION | LOCATION / DWG NO | ELEVATION/GRID | CABLE ROUTE
A1~A3 | FFC SYSTEM | B1-TT66001-5001 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | 4~20mA | 32 | 2 | 10 | 20 |  | B1-TT66001 | 5001 | TEMPERATURE TRANSMITTER | FIELD, Around Main pipe TP | EL. +1726.3 | B1-JBA-6601 | Analog Junction Box | FFC GROUND | EL. +1500 | TI-300-101 / TI-300-103 / TI-100-101 / TI-100-102 / TI-100-105
A4~A6 | FFC SYSTEM | B1-TT66002-5002 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | 4~20mA | 37 | 2 | 10 | 25 |  | B1-TT66002 | 5002 | TEMPERATURE TRANSMITTER | FIELD, Around Main pipe TP | EL. +1726.3 | B1-JBA-6601 | Analog Junction Box | FFC GROUND | EL. +1500 | TI-300-101 / TI-300-103 / TI-100-101 / TI-100-102 / TI-100-105
A7~A9 | FFC SYSTEM | B1-PT66001-5003 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | 4~20mA | 22 | 2 | 10 | 10 |  | B1-PT66001 | 5003 | PRESSURE TRANSMITTER | FIELD, Around Pump Discharge Pipe | EL. +1626.3 | B1-JBA-6601 | Analog Junction Box | FFC GROUND | EL. +1500 | TI-300-101 / TI-300-103 / TI-100-101
A10~A12 | FFC SYSTEM | B1-PT66002-5004 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | 4~20mA | 22 | 2 | 10 | 10 |  | B1-PT66002 | 5004 | PRESSURE TRANSMITTER | FIELD, Around Pump Discharge Pipe | EL. +1626.3 | B1-JBA-6601 | Analog Junction Box | FFC GROUND | EL. +1500 | TI-300-101 / TI-300-103 / TI-100-101
A13~A15 | FFC SYSTEM | B1-LT66001-5005 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | 4~20mA | 32 | 2 | 10 | 20 |  | B1-LT66001 | 5005 | LEVEL TRANSMITTER | FIELD, Deluge tank | EL. +1726.3 | B1-JBA-6601 | Analog Junction Box | FFC GROUND | EL. +1000 | TI-300-101 / TI-300-103 / TI-100-101
A16~A18 | FFC SYSTEM | B1-LT66002-5006 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | 4~20mA | 37 | 2 | 10 | 25 |  | B1-LT66002 | 5006 | LEVEL TRANSMITTER | FIELD, Deluge tank | EL. +1726.3 | B1-JBA-6601 | Analog Junction Box | FFC GROUND | EL. +1000 | TI-300-101 / TI-300-103 / TI-100-101
A1~A2 | FFC SYSTEM | B1-VS66001-5007 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 27 | 2 | 5 | 20 |  | B1-VS66001 | 5007 | FAN 01 VIB SWICH | FAN MOTOR AROUND OF FAN 01 | EL. +3726.3 | B1-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-101 / TI-300-102
A3~A4 | FFC SYSTEM | B1-VS66002-5008 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 37 | 2 | 5 | 30 |  | B1-VS66002 | 5008 | FAN 02 VIB SWICH | FAN MOTOR AROUND OF FAN 02 | EL. +3726.3 | B1-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-101 / TI-300-102
A5~A6 | FFC SYSTEM | B1-VS66003-5009 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 17 | 2 | 5 | 10 |  | B1-VS66003 | 5009 | FAN 03 VIB SWICH | FAN MOTOR AROUND OF FAN 03 | EL. +3726.3 | B1-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-101 / TI-300-102
A7~A8 | FFC SYSTEM | B1-VS66004-5010 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 27 | 2 | 5 | 20 |  | B1-VS66004 | 5010 | FAN 04 VIB SWICH | FAN MOTOR AROUND OF FAN 04 | EL. +3726.3 | B1-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-101 / TI-300-102
A9~A10 | FFC SYSTEM | B1-VS66005-5011 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 27 | 2 | 5 | 20 |  | B1-VS66005 | 5011 | FAN 05 VIB SWICH | FAN MOTOR AROUND OF FAN 05 | EL. +3726.3 | B1-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-101 / TI-300-103
A11~A12 | FFC SYSTEM | B1-VS66006-5012 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 37 | 2 | 5 | 30 |  | B1-VS66006 | 5012 | FAN 06 VIB SWICH | FAN MOTOR AROUND OF FAN 06 | EL. +3726.3 | B1-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-101 / TI-300-103
A13~A14 | FFC SYSTEM | B1-VS66007-5013 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 32 | 2 | 5 | 25 |  | B1-VS66007 | 5013 | FAN 07 VIB SWICH | FAN MOTOR AROUND OF FAN 07 | EL. +3726.3 | B1-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-101 / TI-300-103
A15~A16 | FFC SYSTEM | B1-VS66008-5014 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 42 | 2 | 5 | 35 |  | B1-VS66008 | 5014 | FAN 08 VIB SWICH | FAN MOTOR AROUND OF FAN 08 | EL. +3726.3 | B1-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-101 / TI-300-103
A17~A18 | FFC SYSTEM | B1-VS66009-5015 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 42 | 2 | 5 | 35 |  | B1-VS66009 | 5015 | FAN 09 VIB SWICH | FAN MOTOR AROUND OF FAN 09 | EL. +3726.3 | B1-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-101 / TI-300-103
A19~A20 | FFC SYSTEM | B1-VS66010-5016 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 47 | 2 | 5 | 40 |  | B1-VS66010 | 5016 | FAN 10 VIB SWICH | FAN MOTOR AROUND OF FAN 10 | EL. +3726.3 | B1-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-101 / TI-300-103
A21~A22 | FFC SYSTEM | B1-VS66011-5017 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 47 | 2 | 5 | 40 |  | B1-VS66011 | 5017 | FAN 11 VIB SWICH | FAN MOTOR AROUND OF FAN 11 | EL. +3726.3 | B1-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-101 / TI-300-103
A23~A24 | FFC SYSTEM | B1-VS66012-5018 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 57 | 2 | 5 | 50 |  | B1-VS66012 | 5018 | FAN 12 VIB SWICH | FAN MOTOR AROUND OF FAN 12 | EL. +3726.3 | B1-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-101 / TI-300-103
A1~A3 | FFC SYSTEM | B2-TT66001-5101 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | 4~20mA | 32 | 2 | 10 | 20 |  | B2-TT66001 | 5101 | TEMPERATURE TRANSMITTER | FIELD, Around Main pipe TP | EL. +1726.3 | B2-JBA-6601 | Analog Junction Box | FFC GROUND | EL. +1500 | TI-300-201 / TI-300-203 / TI-100-201 / TI-100-202 / TI-100-204
A4~A6 | FFC SYSTEM | B2-TT66002-5102 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | 4~20mA | 37 | 2 | 10 | 25 |  | B2-TT66002 | 5102 | TEMPERATURE TRANSMITTER | FIELD, Around Main pipe TP | EL. +1726.3 | B2-JBA-6601 | Analog Junction Box | FFC GROUND | EL. +1500 | TI-300-201 / TI-300-203 / TI-100-201 / TI-100-202 / TI-100-204
A7~A9 | FFC SYSTEM | B2-PT66001-5103 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | 4~20mA | 22 | 2 | 10 | 10 |  | B2-PT66001 | 5103 | PRESSURE TRANSMITTER | FIELD, Around Pump Discharge Pipe | EL. +1626.3 | B2-JBA-6601 | Analog Junction Box | FFC GROUND | EL. +1500 | TI-300-201 / TI-300-203 / TI-100-201 / TI-100-202 / TI-100-203
A10~A12 | FFC SYSTEM | B2-PT66002-5104 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | 4~20mA | 22 | 2 | 10 | 10 |  | B2-PT66002 | 5104 | PRESSURE TRANSMITTER | FIELD, Around Pump Discharge Pipe | EL. +1626.3 | B2-JBA-6601 | Analog Junction Box | FFC GROUND | EL. +1500 | TI-300-201 / TI-300-203 / TI-100-201 / TI-100-202 / TI-100-203
A13~A15 | FFC SYSTEM | B2-LT66001-5105 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | 4~20mA | 32 | 2 | 10 | 20 |  | B2-LT66001 | 5105 | LEVEL TRANSMITTER | FIELD, Deluge tank | EL. +1726.3 | B2-JBA-6601 | Analog Junction Box | FFC GROUND | EL. +1000 | TI-300-201 / TI-300-203 / TI-100-201 / TI-100-202 / TI-100-203
A16~A18 | FFC SYSTEM | B2-LT66002-5106 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | 4~20mA | 37 | 2 | 10 | 25 |  | B2-LT66002 | 5106 | LEVEL TRANSMITTER | FIELD, Deluge tank | EL. +1726.3 | B2-JBA-6601 | Analog Junction Box | FFC GROUND | EL. +1000 | TI-300-201 / TI-300-203 / TI-100-201 / TI-100-202 / TI-100-203
A1~A2 | FFC SYSTEM | B2-VS66001-5107 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 27 | 2 | 5 | 20 |  | B2-VS66001 | 5107 | FAN 01 VIB SWICH | FAN MOTOR AROUND OF FAN 01 | EL. +3726.3 | B2-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-201 / TI-300-202
A3~A4 | FFC SYSTEM | B2-VS66002-5108 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 37 | 2 | 5 | 30 |  | B2-VS66002 | 5108 | FAN 02 VIB SWICH | FAN MOTOR AROUND OF FAN 02 | EL. +3726.3 | B2-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-201 / TI-300-202
A5~A6 | FFC SYSTEM | B2-VS66003-5109 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 17 | 2 | 5 | 10 |  | B2-VS66003 | 5109 | FAN 03 VIB SWICH | FAN MOTOR AROUND OF FAN 03 | EL. +3726.3 | B2-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-201 / TI-300-202
A7~A8 | FFC SYSTEM | B2-VS66004-5110 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 27 | 2 | 5 | 20 |  | B2-VS66004 | 5110 | FAN 04 VIB SWICH | FAN MOTOR AROUND OF FAN 04 | EL. +3726.3 | B2-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-201 / TI-300-202
A9~A10 | FFC SYSTEM | B2-VS66005-5111 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 27 | 2 | 5 | 20 |  | B2-VS66005 | 5111 | FAN 05 VIB SWICH | FAN MOTOR AROUND OF FAN 05 | EL. +3726.3 | B2-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-201 / TI-300-203
A11~A12 | FFC SYSTEM | B2-VS66006-5112 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 37 | 2 | 5 | 30 |  | B2-VS66006 | 5112 | FAN 06 VIB SWICH | FAN MOTOR AROUND OF FAN 06 | EL. +3726.3 | B2-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-201 / TI-300-203
A13~A14 | FFC SYSTEM | B2-VS66007-5113 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 32 | 2 | 5 | 25 |  | B2-VS66007 | 5113 | FAN 07 VIB SWICH | FAN MOTOR AROUND OF FAN 07 | EL. +3726.3 | B2-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-201 / TI-300-203
A15~A16 | FFC SYSTEM | B2-VS66008-5114 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 42 | 2 | 5 | 35 |  | B2-VS66008 | 5114 | FAN 08 VIB SWICH | FAN MOTOR AROUND OF FAN 08 | EL. +3726.3 | B2-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-201 / TI-300-203
A17~A18 | FFC SYSTEM | B2-VS66009-5115 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 42 | 2 | 5 | 35 |  | B2-VS66009 | 5115 | FAN 09 VIB SWICH | FAN MOTOR AROUND OF FAN 09 | EL. +3726.3 | B2-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-201 / TI-300-203
A19~A20 | FFC SYSTEM | B2-VS66010-5116 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 47 | 2 | 5 | 40 |  | B2-VS66010 | 5116 | FAN 10 VIB SWICH | FAN MOTOR AROUND OF FAN 10 | EL. +3726.3 | B2-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-201 / TI-300-203
A21~A22 | FFC SYSTEM | B2-VS66011-5117 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 47 | 2 | 5 | 40 |  | B2-VS66011 | 5117 | FAN 11 VIB SWICH | FAN MOTOR AROUND OF FAN 11 | EL. +3726.3 | B2-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-201 / TI-300-203
A23~A24 | FFC SYSTEM | B2-VS66012-5118 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | Dry contact | 57 | 2 | 5 | 50 |  | B2-VS66012 | 5118 | FAN 12 VIB SWICH | FAN MOTOR AROUND OF FAN 12 | EL. +3726.3 | B2-JBY-6601 | Digital Junction Box | FFC GROUND | EL. +2500 | TI-300-201 / TI-300-203
|  | Total add sum as 1Px1.0mm2 |  | 1Px1.0mm2 |  | 621
A19~A21 | FFC SYSTEM | B1-MOV32004-5050 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | 4~20mA | 42 | 2 | 10 | 30 |  | B1-MOV32004 | 5050 | MOV | SUUPPLIED BY DE, NOT INFORM, APPLIED ADD 10m FROM FTS MOV-66001 | EL. +1726.3 | B1-JBA-6601 | MARSHALLING PANEL | FFC GROUND | EL. +2426.3 | TI-300-101 / TI-300-103 / TI-100-101
A19~A21 | FFC SYSTEM | B2-MOV32004-5150 | 0.6/1kV T-CU/PVC/AMS/FRLS-PVC | 1Px1.0mm2 | 4~20mA | 42 | 2 | 10 | 30 |  | B2-MOV32004 | 5150 | MOV | SUUPPLIED BY DE, NOT INFORM, APPLIED ADD 10m FROM FTS MOV-66001 | EL. +1726.3 | B1-JBA-6601 | MARSHALLING PANEL | FFC GROUND | EL. +2426.3 | TI-300-101 / TI-300-103 / TI-100-101
|  | Total add sum as 1Px1.0mm2 |  | 1Px1.0mm2 |  | 84