## Table 1
[16 empty] | COMPANY: Turkistan LLP | [20 empty] | DOCUMENT NUMBER: CCP-W-B114-02-ME-E10-0087
[16 empty] | ASSET: POWER PLANT | [20 empty] | REV NR C01 | [14 empty] | SHEET No 1 of 43
[16 empty] | PROJECT: Turkistan CCGT PROJECT | [20 empty] | REVISION DATE 14.10.24
[16 empty] | SUB PROJECT: | [20 empty] | CONTRACTOR’S DATA: Doosan Enerbility
DOCUMENT TITLE: HRSG_CABLE SCHEDULE
ABSTRACT This document provides HRSG Cable Schedule.
POWER PLANT PROJECT TURKISTAN LLP MASTER
|  |  |  | 1 | [12 empty] | APPROVED – NO COMMENT. СОГЛАСОВАНО-БЕЗ ЗАМЕЧАНИЙ. Relevant work can be proceeded, and the document shall be submitted for Design or Construction. Соответствующие работы могут быть продолжены, документ должен быть представлен для проектирования или строительства.
|  |  |  | 2 | [12 empty] | APPROVED – WITH COMMENT, FORWARD FINAL DOCUMENT. СОГЛАСОВАНО-С ЗАМЕЧАНИЯМИ. Relevant work can be proceeded with corrections and revised document shall be submitted along with response sheet for Design or Construction. Соответствующие работы могут быть продолжены с корректировками, документ должен быть представлен с листом ответов для проектирования или строительства.
|  |  |  | 3 | [12 empty] | REJECTED – WITH COMMENTS. ОТКЛОНЕНО-С ЗАМЕЧАНИЯМИ Only for IFR Revision. These documents shall be upgraded and revised in whole and resubmitted for Review. Только для рев. "выпущено для рассмотрения". Данные документы должны быть обновлены и пересмотрены в целом и повторно представлены на рассмотрение.
|  |  |  | 4 | [12 empty] | FOR INFORMATION ONLY. ТОЛЬКО ДЛЯ ИНФОРМАЦИИ. This document does not require review by Employer. Не требует рассмотрения данного документа Заказчиком.
CC NAME: CC SIGN: DATE
TURKISTAN LLP review or acceptance shall not carry any design responsibilities and shall not relieve the contractor from any contractual responsibilities.
C01 |  |  |  | 2024-10-14 | [5 empty] | Approved For Construction | [20 empty] | S.G.OH | [5 empty] | T.H.LEE |  |  |  | S.K.LEE
D01 |  |  |  | 2024-07-10 | [5 empty] | Approved For Design | [20 empty] | S.G.OH | [5 empty] | T.H.LEE |  |  |  | S.K.LEE
Rev. |  |  |  | Date | [5 empty] | Reason for Issue | [20 empty] | Prepared By | [5 empty] | Checked By |  |  |  | Approved By | [8 empty] | Adapted by PSP LLP | [6 empty] | Turkistan LLP Approval
REVISION DESCRIPTION SHEET
Rev. | [6 empty] | Para. | [7 empty] | Revision Description
D01 | [14 empty] | Approved For Design
C01 | [14 empty] | Approved For Construction
Hold No. | [6 empty] | Para. | [7 empty] | Description of Hold
[41 empty] | Document number: | [13 empty] | 234249-00-CAB531
CCP-W-B114-02-ME-E10-0087
[41 empty] | Revision : | [7 empty] | 1 |  | Date: |  |  |  | 2024-07-04 |  |  |  |  | Page
[41 empty] | Document type: | [13 empty] | LIST
POWER AND CONTROL CABLE LIST
Turkistan CCGT PROJECT
POWER AND CONTROL CABLE LIST
[6 empty] | 1 |  |  |  |  | 2024-07-04 | [43 empty] | NEME-E.D |  |  |  |  | BM |  |  | MM
[6 empty] | 0 |  |  |  |  | 2024-05-08 | [7 empty] | FIRST ISSUE | [35 empty] | NEME-E.D |  |  |  |  | BM |  |  | MM
[6 empty] | REV. |  |  |  |  | DATE | [7 empty] | DESCRIPTION | [35 empty] | Issued |  |  |  |  | Checked |  |  | Approved
SIGNATURES
THIS DOCUMENT IS THE PROPERTY OF NE SRL
AND MAY NOT BE REPRODUCED OR CIRCULATED UNLESS ON PRIOR WRITTEN AUTHORIZATION
[36 empty] | Document number: | [13 empty] | 234249-00-CAB531
CCP-W-B114-02-ME-E10-0087
[36 empty] | Revision : |  |  |  |  | 1 |  |  |  | Date: |  |  |  |  | 2024-07-04 | [5 empty] | Page
[36 empty] | Document type: | [13 empty] | LIST
INDEX
|  |  |  | SHEET |  |  |  |  | REV. | [5 empty] | DESCRIPTION | [29 empty] | NOTES
|  |  |  | 1 |  |  |  |  | 1 | [5 empty] | COVER
|  |  |  | 2 |  |  |  |  | 1 | [5 empty] | INDEX
|  |  |  | 3 |  |  |  |  | 1 | [5 empty] | GENERAL NOTES
|  |  |  | 4 |  |  |  |  | 1 | [5 empty] | I&C CABLE LIST
|  |  |  | 5 |  |  |  |  | 1 | [5 empty] | I&C CABLE LIST SUMMARY
|  |  |  | 6 |  |  |  |  | 1 | [5 empty] | POWER CABLE LIST
|  |  |  | 7 |  |  |  |  | 1 | [5 empty] | POWER CABLE LIST SUMMARY
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
THIS DOCUMENT IS THE PROPERTY OF NE SRL AND MAY NOT BE REPRODUCED OR CIRCULATED UNLESS ON PRIOR WRITTEN AUTHORIZATION
[28 empty] | Document number: | [15 empty] | 234249-00-CAB531 CCP-W-B114-02-ME-E10-0087
[28 empty] | Revision : 01 | [9 empty] | Date: 04/07/2024 | [15 empty] | Page
[28 empty] | Document type: | [15 empty] | LIST
GENERAL NOTES
1) Colour Legend: - = New Items - = Modified - = Deleted 2) All cable section are indicate in sqmm except where indicated 3) Abbreviation Legend CU COPPER XLPE CROSS LINKED POLYETHYLENE INSULATION PVC POLYVINYL CHLORIDE INSULATION FLR FLAME RETARDANT FIR FIRE LSZH LOW SMOKE - ZERO HALOGEN ISH INDIVIDIUAL SHIELD OSH OVERALL SHIELD SWA SPIRAL WIRES ARMOURED FRLS FIRE RETARDANT LOW SMOKE 4) The cable code will be formed by the following fields: B1-XXX-XXXXX-I6XXX B1-XXX-XXXXX-I7XXX B1-XXX-XXXXX-C4XXX B1-XXX-XXXXX-P2XXX Examples: Power cable for a MOV: B1-MOV-XXXX-P2XXX I&C cable for digital signal: B1-XXX-XXXX-C4XXX I&C cable for analogical signal: B1-XXX-XXXXX-I6XXX 5) For Terminal Block details refer Marshalling Cabiner - Wiring Diagram Doc. No. CCP-W-B114-02-ME-E14-0088 6) UNIT: B1 AND SUB-UNIT:14 SHALL BE USED FOR BLOCK#1 HRSG#1
7) UNIT: B1 AND SUB-UNIT:15 SHALL BE USED FOR BLOCK#1 HRSG#2 8) UNIT: B2 AND SUB-UNIT:14 SHALL BE USED FOR BLOCK#1 HRSG#1 9) UNIT: B2 AND SUB-UNIT:15 SHALL BE USED FOR BLOCK#1 HRSG#2 THIS DOCUMENT IS THE PROPERTY OF NE SRL AND MAY NOT BE REPRODUCED OR CIRCULATED UNLESS ON PRIOR WRITTEN AUTHORIZATION
CCP-W-B114-02-ME-E10-0087 HRSG_Cable Schedule C01
Cable Nr | [7 empty] | Supplier |  |  |  |  | FROM | [36 empty] | CABLE | [12 empty] | TO EQUIPMENT / SYSTEM | [5 empty] | Notes |  | Rev.
[13 empty] | Instrument or Local Panel tag | [10 empty] | Service | [13 empty] | Signal Type CIP ID | [6 empty] | Execution Type |  |  |  |  | Type | [7 empty] | Formation |  |  | Length |  | Tag |  | Description |  | System
B1-PIT-14050-I6001 | [7 empty] | NE |  |  |  |  | B1-PIT-14050 | [10 empty] | PR. TR. INLET DUCT (LEFT) | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 35 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  | IP-00-007 |  | 1
B1-TT-14051A-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14051A | [10 empty] | TEMP. TR. INLET DUCT (LEFT) | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 27 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TT-14051B-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14051B | [10 empty] | TEMP. TR. INLET DUCT (LEFT) | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 27 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TT-14051C-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14051C | [10 empty] | TEMP. TR. INLET DUCT (RIGHT) | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 35 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TT-14052-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14052 | [10 empty] | TEMP. TR. D/S MODULE 1 (LEFT) | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 21 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TT-14053A-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14053A | [10 empty] | TEMP. TR. STK (LEFT) | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 16 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TT-14053B-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14053B | [10 empty] | TEMP. TR. STK (LEFT) | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 16 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TT-14053C-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14053C | [10 empty] | TEMP. TR. STK (RIGHT) | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 28 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-PIT-14018A-I6001 | [7 empty] | NE |  |  |  |  | B1-PIT-14018A | [10 empty] | PR. TR. HP SH STEAM | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 61 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  | IR-00-001 |  | 1
B1-PIT-14018B-I6001 | [7 empty] | NE |  |  |  |  | B1-PIT-14018B | [10 empty] | PR. TR. HP SH STEAM | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 60 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  | IR-00-001 |  | 1
B1-TT-14015A-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14015A | [10 empty] | TEMP. TR. HP SH1 TO SH2 DR. | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 18 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TT-14015B-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14015B | [10 empty] | TEMP. TR. HP SH1 TO SH2 DR. | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 18 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TT-14014A-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14014A | [10 empty] | TEMP. TR. HP SH2 IN. | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 18 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TT-14014B-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14014B | [10 empty] | TEMP. TR. HP SH2 IN. | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 18 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TT-14013-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14013 | [10 empty] | TEMP. TR. HP SH1 OUT. | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 58 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-DPIT-14020-I6001 | [7 empty] | NE |  |  |  |  | B1-DPIT-14020 | [10 empty] | DIFF. PR. TR. HP INT. DSH | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 37 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  | IP-00-008 |  | 1
B1-DPIT-14025A-I6001 | [7 empty] | NE |  |  |  |  | B1-DPIT-14025A | [10 empty] | DIFF. PR. TR. REC. PUMP A | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 37 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  | IP-00-005 |  | 1
B1-DPIT-14025B-I6001 | [7 empty] | NE |  |  |  |  | B1-DPIT-14025B | [10 empty] | DIFF. PR. TR. REC. PUMP A | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 37 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  | IP-00-005 |  | 1
B1-DPIT-14044A-I6001 | [7 empty] | NE |  |  |  |  | B1-DPIT-14044A | [10 empty] | DIFF. PR. TR. BD. PUMP A | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 25 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  | IP-00-006 |  | 1
B1-DPIT-14044B-I6001 | [7 empty] | NE |  |  |  |  | B1-DPIT-14044B | [10 empty] | DIFF. PR. TR. BD. PUMP A | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 25 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  | IP-00-006 |  | 1
B1-LIT-14040A-I6001 | [7 empty] | NE |  |  |  |  | B1-LIT-14040A | [10 empty] | LEVEL. TR. CBD TANK | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 38 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  | IP-00-010 |  | 1
B1-LIT-14040B-I6001 | [7 empty] | NE |  |  |  |  | B1-LIT-14040B | [10 empty] | LEVEL. TR. CBD TANK | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 38 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  | IP-00-010 |  | 1
B1-PIT-14002-I6001 | [7 empty] | NE |  |  |  |  | B1-PIT-14002 | [10 empty] | PR. TR. HP FW | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 30 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  | IP-00-004 |  | 1
B1-PIT-14022-I6001 | [7 empty] | NE |  |  |  |  | B1-PIT-14022 | [10 empty] | PR. TR. LP FW | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 30 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  | IP-00-004 |  | 1
B1-PIT-14038A-I6001 | [7 empty] | NE |  |  |  |  | B1-PIT-14038A | [10 empty] | PR. TR. LP SH STEAM | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 62 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  | IR-00-001 |  | 1
B1-PIT-14038B-I6001 | [7 empty] | NE |  |  |  |  | B1-PIT-14038B | [10 empty] | PR. TR. LP SH STEAM | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 62 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  | IR-00-001 |  | 1
B1-PIT-14045-I6001 | [7 empty] | NE |  |  |  |  | B1-PIT-14045 | [10 empty] | PR. TR. BD PUMPS OUT | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 22 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  | IP-00-012 |  | 1
B1-TT-14001A-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14001A | [10 empty] | TEMP. TR. HP FW | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 20 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TT-14001B-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14001B | [10 empty] | TEMP. TR. HP FW | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 20 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TT-14003-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14003 | [10 empty] | TEMP. TR. D/S HP ECO | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 52 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TT-14021A-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14021A | [10 empty] | TEMP. TR. LP FW | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 24 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TT-14021B-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14021B | [10 empty] | TEMP. TR. LP FW | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 24 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TT-14023A-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14023A | [10 empty] | TEMP. TR. CPH IN | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 18 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TT-14023B-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14023B | [10 empty] | TEMP. TR. CPH IN | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 18 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TT-14024-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14024 | [10 empty] | TEMP. TR. CPH OUT | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 46 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TT-14026A-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14026A | [10 empty] | TEMP. TR. D/A IN. | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 62 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TT-14026B-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14026B | [10 empty] | TEMP. TR. D/A IN. | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 61 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TT-14038A-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14038A | [10 empty] | TEMP. TR. LP SH STEAM | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 50 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TT-14038B-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14038B | [10 empty] | TEMP. TR. LP SH STEAM | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 50 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TT-14042A-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14042A | [10 empty] | TEMP. TR. ABD TANK | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 22 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TT-14042B-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14042B | [10 empty] | TEMP. TR. ABD TANK | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 22 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
1 / 4
CCP-W-B114-02-ME-E10-0087 HRSG_Cable Schedule C01
Cable Nr | [7 empty] | Supplier |  |  |  |  | FROM | [36 empty] | CABLE | [12 empty] | TO EQUIPMENT / SYSTEM | [5 empty] | Notes |  | Rev.
[13 empty] | Instrument or Local Panel tag | [10 empty] | Service | [13 empty] | Signal Type CIP ID | [6 empty] | Execution Type |  |  |  |  | Type | [7 empty] | Formation |  |  | Length |  | Tag |  | Description |  | System
B1-TT-14043A-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14043A | [10 empty] | TEMP. TR. ABD TANK OUT | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 28 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TT-14043B-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14043B | [10 empty] | TEMP. TR. ABD TANK OUT | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 23 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-FIT-14019-I6001 | [7 empty] | NE |  |  |  |  | B1-FIT-14019 | [10 empty] | FLOW TR. HP INT. DSH | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 38 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  | IP-00-008 |  | 1
B1-LCV-14081-I6001 | [7 empty] | NE |  |  |  |  | B1-LCV-14081 | [10 empty] | HP DRM 100% LCV | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 60 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-LCV-14082-I6001 | [7 empty] | NE |  |  |  |  | B1-LCV-14082 | [10 empty] | HP DRM 30% LCV | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 61 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-LCV-14087-I6001 | [7 empty] | NE |  |  |  |  | B1-LCV-14087 | [10 empty] | LP DRM 100% LCV | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 53 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-LCV-14088-I6001 | [7 empty] | NE |  |  |  |  | B1-LCV-14088 | [10 empty] | LP DRM 30% LCV | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 53 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-LCV-14089-I6001 | [7 empty] | NE |  |  |  |  | B1-LCV-14089 | [10 empty] | CBD TK LCV | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 42 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-MOV-14002-I6001 | [7 empty] | NE |  |  |  |  | B1-MOV-14002 | [10 empty] | HP ECO INL ISOL BYP VLV | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 15 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-MOV-14006-I6001 | [7 empty] | NE |  |  |  |  | B1-MOV-14006 | [10 empty] | HP IBD VLV | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 46 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-MOV-14008-I6001 | [7 empty] | NE |  |  |  |  | B1-MOV-14008 | [10 empty] | HP SH1 TO SH2 DRN VLV | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 18 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-MOV-14009-I6001 | [7 empty] | NE |  |  |  |  | B1-MOV-14009 | [10 empty] | HP SH S/U VT VLV | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 60 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-MOV-14013-I6001 | [7 empty] | NE |  |  |  |  | B1-MOV-14013 | [10 empty] | LP FW STP BYP VLV | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 26 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-MOV-14014-I6001 | [7 empty] | NE |  |  |  |  | B1-MOV-14014 | [10 empty] | LP IBD VLV | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 47 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-MOV-14017-I6001 | [7 empty] | NE |  |  |  |  | B1-MOV-14017 | [10 empty] | LP SH1 DRN VLV | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 17 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-MOV-14018-I6001 | [7 empty] | NE |  |  |  |  | B1-MOV-14018 | [10 empty] | LP SH S/U VT VLV | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 51 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TCV-14083-I6001 | [7 empty] | NE |  |  |  |  | B1-TCV-14083 | [10 empty] | HP DSHTR TCV | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 28 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TCV-14084-I6001 | [7 empty] | NE |  |  |  |  | B1-TCV-14084 | [10 empty] | CPH INL TCV | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 26 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TCV-14085-I6001 | [7 empty] | NE |  |  |  |  | B1-TCV-14085 | [10 empty] | CPH BYP TCV | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 31 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TCV-14086-I6001 | [7 empty] | NE |  |  |  |  | B1-TCV-14086 | [10 empty] | CPH RCP TCV | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 33 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TCV-14090-I6001 | [7 empty] | NE |  |  |  |  | B1-TCV-14090 | [10 empty] | ABD TK CLG W TR TCV | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 24 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-PIT-14003-I6001 | [7 empty] | NE |  |  |  |  | B1-PIT-14003 | [10 empty] | P HP ECO OUTL | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 64 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  | IP-00-002 |  | 1
LATER-I6001 | [7 empty] | NE |  |  |  |  | LATER | [10 empty] | STKG SO2 (CEMS SYSTEM) | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 43 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TT-14011A-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14011A | [10 empty] | TEMP. TR. HP DRUM INNER | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 16 |  | B1-JBA-1401 |  | JUNCTION BOX |  | JB |  |  |  | 1
B1-JBA-1401-I6002 | [7 empty] | NE |  |  |  |  | B1-JBA-1401 | [10 empty] | JB TO MARSHALLING | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 58 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TT-14011B-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14011B | [10 empty] | TEMP. TR. HP DRUM MIDDLE | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 16 |  | B1-JBA-1401 |  | JUNCTION BOX |  | JB |  |  |  | 1
B1-JBA-1401-I6002 | [7 empty] | NE |  |  |  |  | B1-JBA-1401 | [10 empty] | JB TO MARSHALLING | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 58 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TT-14012A-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14012A | [10 empty] | TEMP. TR. HP DRUM INNER | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 16 |  | B1-JBA-1401 |  | JUNCTION BOX |  | JB |  |  |  | 1
B1-JBA-1401-I6002 | [7 empty] | NE |  |  |  |  | B1-JBA-1401 | [10 empty] | JB TO MARSHALLING | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 58 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TT-14012B-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14012B | [10 empty] | TEMP. TR. HP DRUM MIDDLE | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 16 |  | B1-JBA-1401 |  | JUNCTION BOX |  | JB |  |  |  | 1
B1-JBA-1401-I6002 | [7 empty] | NE |  |  |  |  | B1-JBA-1401 | [10 empty] | JB TO MARSHALLING | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 58 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TT-14016A-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14016A | [10 empty] | TEMP. TR. HP SH2 INNER | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 10 |  | B1-JBA-1401 |  | JUNCTION BOX |  | JB |  |  |  | 1
B1-JBA-1401-I6002 | [7 empty] | NE |  |  |  |  | B1-JBA-1401 | [10 empty] | JB TO MARSHALLING | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 58 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TT-14016B-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14016B | [10 empty] | TEMP. TR. HP SH2 MIDDLE | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 10 |  | B1-JBA-1401 |  | JUNCTION BOX |  | JB |  |  |  | 1
B1-JBA-1401-I6002 | [7 empty] | NE |  |  |  |  | B1-JBA-1401 | [10 empty] | JB TO MARSHALLING | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 58 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TT-14017A-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14017A | [10 empty] | TEMP. TR. HP SH2 INNER | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 10 |  | B1-JBA-1401 |  | JUNCTION BOX |  | JB |  |  |  | 1
B1-JBA-1401-I6002 | [7 empty] | NE |  |  |  |  | B1-JBA-1401 | [10 empty] | JB TO MARSHALLING | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 58 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TT-14017B-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14017B | [10 empty] | TEMP. TR. HP SH2 MIDDLE | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 10 |  | B1-JBA-1401 |  | JUNCTION BOX |  | JB |  |  |  | 1
B1-JBA-1401-I6002 | [7 empty] | NE |  |  |  |  | B1-JBA-1401 | [10 empty] | JB TO MARSHALLING | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 58 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-PIT-14010A-I6001 | [7 empty] | NE |  |  |  |  | B1-PIT-14010A | [10 empty] | PR. TR. HP DRUM | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 41 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | ESD |  | IR-00-001 |  | 1
B1-PIT-14010B-I6001 | [7 empty] | NE |  |  |  |  | B1-PIT-14010B | [10 empty] | PR. TR. HP DRUM | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 41 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | ESD |  | IR-00-001 |  | 1
2 / 4
CCP-W-B114-02-ME-E10-0087 HRSG_Cable Schedule C01
Cable Nr | [7 empty] | Supplier |  |  |  |  | FROM | [36 empty] | CABLE | [12 empty] | TO EQUIPMENT / SYSTEM | [5 empty] | Notes |  | Rev.
[13 empty] | Instrument or Local Panel tag | [10 empty] | Service | [13 empty] | Signal Type CIP ID | [6 empty] | Execution Type |  |  |  |  | Type | [7 empty] | Formation |  |  | Length |  | Tag |  | Description |  | System
B1-PIT-14010C-I6001 | [7 empty] | NE |  |  |  |  | B1-PIT-14010C | [10 empty] | PR. TR. HP DRUM | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 55 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | ESD |  | IP-00-002 |  | 1
B1-LIT-14010A-I6001 | [7 empty] | NE |  |  |  |  | B1-LIT-14010A | [10 empty] | PR. TR. LP DRUM | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 40 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | ESD |  | IR-00-002 |  | 1
B1-LIT-14010B-I6001 | [7 empty] | NE |  |  |  |  | B1-LIT-14010B | [10 empty] | PR. TR. LP DRUM | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 40 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | ESD |  | IR-00-002 |  | 1
B1-LIT-14010C-I6001 | [7 empty] | NE |  |  |  |  | B1-LIT-14010C | [10 empty] | PR. TR. LP DRUM | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 40 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | ESD |  | IR-00-002 |  | 1
B1-PIT-14030A-I6001 | [7 empty] | NE |  |  |  |  | B1-PIT-14030A | [10 empty] | PR. TR. LP DRUM | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 40 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | ESD |  | IR-00-002 |  | 1
B1-PIT-14030B-I6001 | [7 empty] | NE |  |  |  |  | B1-PIT-14030B | [10 empty] | PR. TR. LP DRUM | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 40 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | ESD |  | IR-00-002 |  | 1
B1-PIT-14030C-I6001 | [7 empty] | NE |  |  |  |  | B1-PIT-14030C | [10 empty] | PR. TR. LP DRUM | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 40 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | ESD |  | IR-00-002 |  | 1
B1-LIT-14030A-I6001 | [7 empty] | NE |  |  |  |  | B1-LIT-14030A | [10 empty] | LEVEL. TR. LP DRUM | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 40 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | ESD |  | IR-00-002 |  | 1
B1-LIT-14030B-I6001 | [7 empty] | NE |  |  |  |  | B1-LIT-14030B | [10 empty] | LEVEL. TR. LP DRUM | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 40 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | ESD |  | IR-00-002 |  | 1
B1-LIT-14030C-I6001 | [7 empty] | NE |  |  |  |  | B1-LIT-14030C | [10 empty] | LEVEL. TR. LP DRUM | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 40 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | ESD |  | IR-00-002 |  | 1
B1-TT-14018A-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14018A | [10 empty] | TEMP. TR. HP SH STEAM | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 56 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | ESD |  |  |  | 1
B1-TT-14018B-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14018B | [10 empty] | TEMP. TR. HP SH STEAM | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 56 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | ESD |  |  |  | 1
B1-TT-14018C-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14018C | [10 empty] | TEMP. TR. HP SH STEAM | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 56 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | ESD |  |  |  | 1
B1-LCV-14081-I7002 | [7 empty] | NE |  |  |  |  | B1-LCV-14081 | [10 empty] | HP DRM 100% LCV | [13 empty] | AO | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 60 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-LCV-14082-I7002 | [7 empty] | NE |  |  |  |  | B1-LCV-14082 | [10 empty] | HP DRM 30% LCV | [13 empty] | AO | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 61 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-LCV-14087-I7002 | [7 empty] | NE |  |  |  |  | B1-LCV-14087 | [10 empty] | LP DRM 100% LCV | [13 empty] | AO | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 53 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-LCV-14088-I7002 | [7 empty] | NE |  |  |  |  | B1-LCV-14088 | [10 empty] | LP DRM 30% LCV | [13 empty] | AO | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 53 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-LCV-14089-I7002 | [7 empty] | NE |  |  |  |  | B1-LCV-14089 | [10 empty] | CBD TK LCV | [13 empty] | AO | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 42 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TCV-14083-I7002 | [7 empty] | NE |  |  |  |  | B1-TCV-14083 | [10 empty] | HP DSHTR TCV | [13 empty] | AO | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 28 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TCV-14084-I7002 | [7 empty] | NE |  |  |  |  | B1-TCV-14084 | [10 empty] | CPH INL TCV | [13 empty] | AO | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 26 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TCV-14085-I7002 | [7 empty] | NE |  |  |  |  | B1-TCV-14085 | [10 empty] | CPH BYP TCV | [13 empty] | AO | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 31 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TCV-14086-I7002 | [7 empty] | NE |  |  |  |  | B1-TCV-14086 | [10 empty] | CPH RCP TCV | [13 empty] | AO | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 33 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-TCV-14090-I7002 | [7 empty] | NE |  |  |  |  | B1-TCV-14090 | [10 empty] | ABD TK CLG W TR TCV | [13 empty] | AO | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 24 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-LSH-14081-C4001 | [7 empty] | NE |  |  |  |  | B1-LSH-14081 | [10 empty] | LS LP SH1 DRN | [13 empty] | DI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 27 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-LSH-14082-C4001 | [7 empty] | NE |  |  |  |  | B1-LSH-14082 | [10 empty] | LS LP SH1 DRN | [13 empty] | DI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 27 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-ZSL-14083-C4001 | [7 empty] | NE |  |  |  |  | B1-ZSL-14083 | [10 empty] | STACK DAMPER - RIGHT SIDE CLOSED | [13 empty] | DI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 50 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-ZSL-14084-C4001 | [7 empty] | NE |  |  |  |  | B1-ZSL-14084 | [10 empty] | STACK DAMPER - LEFT SIDE CLOSED | [13 empty] | DI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 50 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-ZSH-14083A-C4001 | [7 empty] | NE |  |  |  |  | B1-ZSH-14083A | [10 empty] | STACK DAMPER - RIGHT SIDE OPEN | [13 empty] | DI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 50 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | ESD |  |  |  | 1
B1-ZSH-14083B-C4001 | [7 empty] | NE |  |  |  |  | B1-ZSH-14083B | [10 empty] | STACK DAMPER - RIGHT SIDE OPEN | [13 empty] | DI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 50 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | ESD |  |  |  | 1
B1-ZSH-14083C-C4001 | [7 empty] | NE |  |  |  |  | B1-ZSH-14083C | [10 empty] | STACK DAMPER - RIGHT SIDE OPEN | [13 empty] | DI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 50 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | ESD |  |  |  | 1
B1-ZSH-14084A-C4001 | [7 empty] | NE |  |  |  |  | B1-ZSH-14084A | [10 empty] | STACK DAMPER - LEFT SIDE OPEN | [13 empty] | DI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 50 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | ESD |  |  |  | 1
B1-ZSH-14084B-C4001 | [7 empty] | NE |  |  |  |  | B1-ZSH-14084B | [10 empty] | STACK DAMPER - LEFT SIDE OPEN | [13 empty] | DI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 50 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | ESD |  |  |  | 1
B1-ZSH-14084C-C4001 | [7 empty] | NE |  |  |  |  | B1-ZSH-14084C | [10 empty] | STACK DAMPER - LEFT SIDE OPEN | [13 empty] | DI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 50 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | ESD |  |  |  | 1
B1-MD-14001-C4001 | [7 empty] | NE |  |  |  |  | B1-MD-14001 | [10 empty] | STK DAMPER MOV | [13 empty] | DI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 15Cx1.5 mm² (OSH) |  |  | 50 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-MOV-14001-C4001 | [7 empty] | NE |  |  |  |  | B1-MOV-14001 | [10 empty] | HP ECO INL ISOL VLV | [13 empty] | DI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 15Cx1.5 mm² (OSH) |  |  | 20 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-MOV-14003-C4001 | [7 empty] | NE |  |  |  |  | B1-MOV-14003 | [10 empty] | HP DRM 100% ISOL VLV | [13 empty] | DI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 15Cx1.5 mm² (OSH) |  |  | 55 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-MOV14004-C4001 | [7 empty] | NE |  |  |  |  | B1-MOV14004 | [10 empty] | HP DRM 30% ISOL VLV | [13 empty] | DI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 15Cx1.5 mm² (OSH) |  |  | 56 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-MOV-14005-C4001 | [7 empty] | NE |  |  |  |  | B1-MOV-14005 | [10 empty] | HP CBD VLV | [13 empty] | DI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 15Cx1.5 mm² (OSH) |  |  | 56 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-MOV-14007-C4001 | [7 empty] | NE |  |  |  |  | B1-MOV-14007 | [10 empty] | HP DSHTR W TR ISOL VLV | [13 empty] | DI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 15Cx1.5 mm² (OSH) |  |  | 33 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-MOV-14012-C4001 | [7 empty] | NE |  |  |  |  | B1-MOV-14012 | [10 empty] | LP FW STP VLV | [13 empty] | DI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 15Cx1.5 mm² (OSH) |  |  | 34 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-MOV-14015-C4001 | [7 empty] | NE |  |  |  |  | B1-MOV-14015 | [10 empty] | DEAER VT VLV | [13 empty] | DI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 15Cx1.5 mm² (OSH) |  |  | 55 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
3 / 4
CCP-W-B114-02-ME-E10-0087 HRSG_Cable Schedule C01
Cable Nr | [7 empty] | Supplier |  |  |  |  | FROM | [36 empty] | CABLE | [12 empty] | TO EQUIPMENT / SYSTEM | [5 empty] | Notes |  | Rev.
[13 empty] | Instrument or Local Panel tag | [10 empty] | Service | [13 empty] | Signal Type CIP ID | [6 empty] | Execution Type |  |  |  |  | Type | [7 empty] | Formation |  |  | Length |  | Tag |  | Description |  | System
B1-MOV-14016-C4001 | [7 empty] | NE |  |  |  |  | B1-MOV-14016 | [10 empty] | DEAER S/U VT VLV | [13 empty] | DI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 15Cx1.5 mm² (OSH) |  |  | 55 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-MOV-14002-C4001 | [7 empty] | NE |  |  |  |  | B1-MOV-14002 | [10 empty] | HP ECO INL ISOL BYP VLV | [13 empty] | DI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 15Cx1.5 mm² (OSH) |  |  | 22 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-MOV-14006-C4001 | [7 empty] | NE |  |  |  |  | B1-MOV-14006 | [10 empty] | HP IBD VLV | [13 empty] | DI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 15Cx1.5 mm² (OSH) |  |  | 53 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-MOV-14008-C4001 | [7 empty] | NE |  |  |  |  | B1-MOV-14008 | [10 empty] | HP SH1 TO SH2 DRN VLV | [13 empty] | DI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 15Cx1.5 mm² (OSH) |  |  | 30 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-MOV-14009-C4001 | [7 empty] | NE |  |  |  |  | B1-MOV-14009 | [10 empty] | HP SH S/U VT VLV | [13 empty] | DI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 15Cx1.5 mm² (OSH) |  |  | 68 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-MOV-14013-C4001 | [7 empty] | NE |  |  |  |  | B1-MOV-14013 | [10 empty] | LP FW STP BYP VLV | [13 empty] | DI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 15Cx1.5 mm² (OSH) |  |  | 33 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-MOV-14014-C4001 | [7 empty] | NE |  |  |  |  | B1-MOV-14014 | [10 empty] | LP IBD VLV | [13 empty] | DI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 15Cx1.5 mm² (OSH) |  |  | 57 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-MOV-14017-C4001 | [7 empty] | NE |  |  |  |  | B1-MOV-14017 | [10 empty] | LP SH1 DRN VLV | [13 empty] | DI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 15Cx1.5 mm² (OSH) |  |  | 31 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-MOV-14018-C4001 | [7 empty] | NE |  |  |  |  | B1-MOV-14018 | [10 empty] | LP SH S/U VT VLV | [13 empty] | DI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 15Cx1.5 mm² (OSH) |  |  | 55 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-SV-14192-C4001 | [7 empty] | NE |  |  |  |  | B1-SV-14192 | [10 empty] | HP STEAM DRUM PSV | [13 empty] | DI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 15Cx1.5 mm² (OSH) |  |  | 68 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-SV-14192-C4002 | [7 empty] | NE |  |  |  |  | B1-SV-14192 | [10 empty] | HP STEAM DRUM PSV | [13 empty] | DO | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 68 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | ESD |  |  |  | 1
B1-SV-14193-C4001 | [7 empty] | NE |  |  |  |  | B1-SV-14193 | [10 empty] | HP SH PSV | [13 empty] | DI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 15Cx1.5 mm² (OSH) |  |  | 70 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-SV-14193-C4002 | [7 empty] | NE |  |  |  |  | B1-SV-14193 | [10 empty] | HP SH PSV | [13 empty] | DO | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 70 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | ESD |  |  |  | 1
B1-AWL-14001-C4001 | [7 empty] | NE |  |  |  |  | B1-AWL-14001 | [10 empty] | AIRCRAFT W ARNING LIGHT POW ER SUPPLY FAULT | [13 empty] | DI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 30 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-AWL-14001-C4001 | [7 empty] | NE |  |  |  |  | B1-AWL-14001 | [10 empty] | AIRCRAFT W ARINING LIGHT FAULT | [13 empty] | DI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 30 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
LATER-C4001 | [7 empty] | NE |  |  |  |  | LATER | [10 empty] | DCS TO CEMS | [13 empty] | DO | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 43 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
LATER-C4001 | [7 empty] | NE |  |  |  |  | LATER | [10 empty] | DCS TO CEMS | [13 empty] | DO | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 43 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
LATER-C4001 | [7 empty] | NE |  |  |  |  | LATER | [10 empty] | DCS TO CEMS | [13 empty] | DO | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 43 |  | B1-MAP-1401 |  | MARSHALLING CABINET |  | DCS |  |  |  | 1
B1-AT-14081-I6001 | [7 empty] | NE |  |  |  |  | B1-AT-14081 | [10 empty] | DUST METER | [13 empty] | AI | [11 empty] | CU/0H/FR/LS0H 0.6/1 Kv | [7 empty] | 8x(1Px0.75) mm² |  |  | 82 |  | B1-A-1481 |  | CEMS PANEL | [5 empty] | 1
B1-AE-14080-I6001 | [7 empty] | NE |  |  |  |  | B1-AE-14080 | [10 empty] | SAMPLE PROBE | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 85 |  | B1-A-1481 |  | CEMS PANEL | [5 empty] | 1
B1-FIT-14081-I6001 | [7 empty] | NE |  |  |  |  | B1-FIT-14081 | [10 empty] | PITOT TUBE (FLOW TRANSMITTER) | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 81 |  | B1-A-1481 |  | CEMS PANEL | [5 empty] | 1
B1-TT-14081-I6001 | [7 empty] | NE |  |  |  |  | B1-TT-14081 | [10 empty] | TEMPERATURE TRANSMITTER | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 81 |  | B1-A-1481 |  | CEMS PANEL | [5 empty] | 1
B1-PIT-14081-I6001 | [7 empty] | NE |  |  |  |  | B1-PIT-14081 | [10 empty] | PRESSURE TRANSMITTER | [13 empty] | AI | [11 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [7 empty] | 1x(1Px1.5) mm² (OSH) |  |  | 85 |  | B1-A-1481 |  | CEMS PANEL | [5 empty] | 1
4 / 4
I&C CABLES - BOM
|  | POS |  |  | SUPPLIER | [6 empty] | CABLE CHARACTERISTICS | [22 empty] | QUANTITIES | [17 empty] | NOTES
[12 empty] | TYPE | [10 empty] | FORMATION | [7 empty] | DIAMETER [mm] (+/-10%) |  |  |  | REQUIRED FOR 4 UNIT [m] |  |  |  | SPARE | [7 empty] | TOTAL ORDER FOR 4 UNIT [m]
|  | 1 |  |  | NE | [6 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [10 empty] | 1x(1Px1.5) mm² (OSH) | [7 empty] | Later |  |  |  | 5032 |  |  |  | 503.2 | [7 empty] | 22140.8
|  | 2 |  |  | NE | [6 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [10 empty] | 15Cx1.5 mm² (OSH) | [7 empty] | Later |  |  |  | 901 |  |  |  | 90.1 | [7 empty] | 3964.4
|  | 3 |  |  | NE | [6 empty] | CU/0H/FR/LS0H 0.6/1 Kv | [10 empty] | 8x(1Px0.75) mm² | [7 empty] | Later |  |  |  | 82 |  |  |  | 8.2 | [7 empty] | 360.8
THIS DOCUMENT IS THE PROPERTY OF NE SRL AND MAY NOT BE REPRODUCED OR CIRCULATED UNLESS ON PRIOR WRITTEN AUTHORIZATION
CCP-W-B114-02-ME-E10-0087 HRSG_Cable Schedule C01
Cable Nr | [11 empty] | Supplier |  |  |  | FROM | [34 empty] | CABLE | [12 empty] | TO EQUIPMENT / SYSTEM | [5 empty] | Notes |  | Rev.
[16 empty] | Instrument or Local Panel tag | [7 empty] | Service | [14 empty] | Signal Type CIP ID | [7 empty] | Execution Type |  |  |  | Type | [7 empty] | Formation |  |  | Length |  | Tag |  | Description |  | System
B1-MD-14001-P2001 | [11 empty] | NE |  |  |  | B1-MD-14001 | [7 empty] | STK DAMPER MOV / HRSG STACK DAMPER | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 4Gx4 mm² |  |  | 42 |  | B1-PDP-1401 |  | LV PANEL |  | NORMAL POWER |  |  |  | 1
B1-MOV-14001-P2001 | [11 empty] | NE |  |  |  | B1-MOV-14001 | [7 empty] | HP ECO INL ISOL VLV / HP BFW STOP VALVE - MOV | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 4Gx4 mm² |  |  | 20 |  | B1-PDP-1401 |  | LV PANEL |  | NORMAL POWER |  |  |  | 1
B1-MOV-14003-P2001 | [11 empty] | NE |  |  |  | B1-MOV-14003 | [7 empty] | HP DRM 100% ISOL VLV / HP BFW 100% ISOLATION VALVE - MOV | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 4Gx4 mm² |  |  | 55 |  | B1-PDP-1401 |  | LV PANEL |  | NORMAL POWER |  |  |  | 1
B1-MOV-14004-P2001 | [11 empty] | NE |  |  |  | B1-MOV-14004 | [7 empty] | HP DRM 30% ISOL VLV / HP BFW 30% ISOLATION VALVE - MOV | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 4Gx4 mm² |  |  | 56 |  | B1-PDP-1401 |  | LV PANEL |  | NORMAL POWER |  |  |  | 1
B1-MOV-14005-P2001 | [11 empty] | NE |  |  |  | B1-MOV-14005 | [7 empty] | HP CBD VLV / HP STEAM DRUM TO C.B.D - MOV | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 4Gx4 mm² |  |  | 56 |  | B1-PDP-1401 |  | LV PANEL |  | NORMAL POWER |  |  |  | 1
B1-MOV-14007-P2001 | [11 empty] | NE |  |  |  | B1-MOV-14007 | [7 empty] | HP DSHTR WTR ISOL VLV / DSH SPRAY WATER ISOLATION - MOV | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 4Gx4 mm² |  |  | 33 |  | B1-PDP-1401 |  | LV PANEL |  | NORMAL POWER |  |  |  | 1
B1-MOV-14012-P2001 | [11 empty] | NE |  |  |  | B1-MOV-14012 | [7 empty] | LP FW STP VLV / LP BFW STOP VALVE - MOV | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 4Gx4 mm² |  |  | 34 |  | B1-PDP-1401 |  | LV PANEL |  | NORMAL POWER |  |  |  | 1
B1-MOV-14015-P2001 | [11 empty] | NE |  |  |  | B1-MOV-14015 | [7 empty] | DEAER VT VLV / DEAERATOR VENT - MOV | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 4Gx4 mm² |  |  | 55 |  | B1-PDP-1401 |  | LV PANEL |  | NORMAL POWER |  |  |  | 1
B1-MOV-14016-P2001 | [11 empty] | NE |  |  |  | B1-MOV-14016 | [7 empty] | DEAER S/U VT VLV / DEAERATOR START-UP VENT - MOV | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 4Gx4 mm² |  |  | 55 |  | B1-PDP-1401 |  | LV PANEL |  | NORMAL POWER |  |  |  | 1
B1-MOV-14002-P2001 | [11 empty] | NE |  |  |  | B1-MOV-14002 | [7 empty] | HP ECO INL ISOL BYP VLV / HP BFW STOP BYPASS VALVE - MOV | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 4Gx4 mm² |  |  | 22 |  | B1-PDP-1401 |  | LV PANEL |  | NORMAL POWER |  |  |  | 1
B1-MOV-14006-P2001 | [11 empty] | NE |  |  |  | B1-MOV-14006 | [7 empty] | HP IBD VLV / HP STEAM DRUM TO I.B.D - MOV | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 4Gx4 mm² |  |  | 53 |  | B1-PDP-1401 |  | LV PANEL |  | NORMAL POWER |  |  |  | 1
B1-MOV-14008-P2001 | [11 empty] | NE |  |  |  | B1-MOV-14008 | [7 empty] | HP SH1 TO SH2 DRN VLV / HP DSH DRAIN - MOV | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 4Gx4 mm² |  |  | 30 |  | B1-PDP-1401 |  | LV PANEL |  | NORMAL POWER |  |  |  | 1
B1-MOV-14009-P2001 | [11 empty] | NE |  |  |  | B1-MOV-14009 | [7 empty] | HP SH S/U VT VLV | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 4Gx4 mm² |  |  | 68 |  | B1-PDP-1401 |  | LV PANEL |  | NORMAL POWER |  |  |  | 1
B1-MOV-14013-P2001 | [11 empty] | NE |  |  |  | B1-MOV-14013 | [7 empty] | LP FW STP BYP VLV / LP BFW STOP BYPASS VALVE - MOV | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 4Gx4 mm² |  |  | 33 |  | B1-PDP-1401 |  | LV PANEL |  | NORMAL POWER |  |  |  | 1
B1-MOV-14014-P2001 | [11 empty] | NE |  |  |  | B1-MOV-14014 | [7 empty] | LP IBD VLV /LP STEAM DRUM TO I.B.D - MOV | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 4Gx4 mm² |  |  | 57 |  | B1-PDP-1401 |  | LV PANEL |  | NORMAL POWER |  |  |  | 1
B1-MOV-14017-P2001 | [11 empty] | NE |  |  |  | B1-MOV-14017 | [7 empty] | LP SH1 DRN VLV / LP SH DRAIN - MOV | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 4Gx4 mm² |  |  | 31 |  | B1-PDP-1401 |  | LV PANEL |  | NORMAL POWER |  |  |  | 1
B1-MOV-14018-P2001 | [11 empty] | NE |  |  |  | B1-MOV-14018 | [7 empty] | LP SH S/U VT VLV / LP STEAM START-UP VENT - MOV | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 4Gx4 mm² |  |  | 55 |  | B1-PDP-1401 |  | LV PANEL |  | NORMAL POWER |  |  |  | 1
B1-SV-14192-P2001 | [11 empty] | NE |  |  |  | B1-SV-14192 | [7 empty] | HP STEAM DRUM PSV | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx4 mm² |  |  | 68 |  | B1-PDP-1401 |  | LV PANEL |  | NORMAL POWER |  |  |  | 1
B1-SV-14193-P2001 | [11 empty] | NE |  |  |  | B1-SV-14193 | [7 empty] | HP STEAM DRUM PSV | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx4 mm² |  |  | 70 |  | B1-PDP-1401 |  | LV PANEL |  | NORMAL POWER |  |  |  | 1
B1-HO-14001-P2001 | [11 empty] | NE |  |  |  | B1-HO-14001 | [7 empty] | HRSG STACK HOIST | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 4Gx4 mm² |  |  | 72 |  | B1-PDP-1401 |  | LV PANEL |  | NORMAL POWER |  |  |  | 1
B1-A-1481-P2001 | [11 empty] | NE |  |  |  | B1-A-1481 | [7 empty] | CEMS PANEL (Heated line and auxiliary) | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 5Gx6 mm² |  |  | 44 |  | B1-PDP-1401 |  | LV PANEL |  | NORMAL POWER |  |  |  | 1
B1-WO-1401-P2001 | [11 empty] | NE |  |  |  | B1-WO-1401 | [7 empty] | 32A, 3PH SOCKET | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 5Gx6 mm² |  |  | 29 |  | B1-PDP-1401 |  | LV PANEL |  | NORMAL POWER |  |  |  | 1
B1-WO-1402-P2001 | [11 empty] | NE |  |  |  | B1-WO-1402 | [7 empty] | 32A, 3PH SOCKET | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 5Gx6 mm² |  |  | 51 |  | B1-PDP-1401 |  | LV PANEL |  | NORMAL POWER |  |  |  | 1
B1-LP-1401 -P2001 | [11 empty] | NE |  |  |  | B1-LP-1401 | [7 empty] | NORMAL LIGHTING DB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx4 mm² |  |  | 15 |  | B1-PDP-1401 |  | LV PANEL |  | NORMAL POWER |  |  |  | 1
LG-14512-P2001 | [11 empty] | NE |  |  |  | LG-14512 | [7 empty] | HP STEAM DRUM LEVEL CONTROL UNIT | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx4 mm² |  |  | 60 |  | B1-UPSP-001 |  | UPS DISTRIBUTION BOARD |  | UPS POWER |  |  |  | 1
LG-14532-P2001 | [11 empty] | NE |  |  |  | LG-14532 | [7 empty] | LP STEAM DRUM LEVEL CONTROL UNIT | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx4 mm² |  |  | 60 |  | B1-UPSP-001 |  | UPS DISTRIBUTION BOARD |  | UPS POWER |  |  |  | 1
B1-SV-14192-P2001 | [11 empty] | NE |  |  |  | B1-SV-14192 | [7 empty] | HP STEAM DRUM PSV CONTROL UNIT | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx4 mm² |  |  | 60 |  | B1-UPSP-001 |  | UPS DISTRIBUTION BOARD |  | UPS POWER |  |  |  | 1
B1-SV-14193-P2001 | [11 empty] | NE |  |  |  | B1-SV-14193 | [7 empty] | HP SH STEAM PSV CONTROL UNIT | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx4 mm² |  |  | 60 |  | B1-UPSP-001 |  | UPS DISTRIBUTION BOARD |  | UPS POWER |  |  |  | 1
B1-AWL-14001-P2001 | [11 empty] | NE |  |  |  | B1-AWL-14001 | [7 empty] | AWL PANEL | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx4 mm² |  |  | 30 |  | B1-UPSP-001 |  | UPS DISTRIBUTION BOARD |  | UPS POWER |  |  |  | 1
B1-A-1481A-P2001 | [11 empty] | NE |  |  |  | B1-A-1481A | [7 empty] | CEMS PANEL - LINE 1 | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx4 mm² |  |  | 44 |  | B1-UPSP-001 |  | UPS DISTRIBUTION BOARD |  | UPS POWER |  |  |  | 1
B1-A-1481B-P2001 | [11 empty] | NE |  |  |  | B1-A-1481B | [7 empty] | CEMS PANEL - LINE 2 | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx4 mm² |  |  | 44 |  | B1-UPSP-001 |  | UPS DISTRIBUTION BOARD |  | UPS POWER |  |  |  | 1
B1-PC-1404A-P2001 | [11 empty] | NE |  |  |  | B1-PC-1404A | [7 empty] | HPU PLC PANEL - LINE 1 | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx4 mm² |  |  | 44 |  | B1-UPSP-001 |  | UPS DISTRIBUTION BOARD |  | UPS POWER |  |  |  | 1
B1-PC-1404B-P2001 | [11 empty] | NE |  |  |  | B1-PC-1404B | [7 empty] | HPU PLC PANEL - LINE 2 | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx4 mm² |  |  | 44 |  | B1-UPSP-001 |  | UPS DISTRIBUTION BOARD |  | UPS POWER |  |  |  | 1
B1-ELP-1401 -P2001 | [11 empty] | NE |  |  |  | B1-ELP-1401 | [7 empty] | EMERGENCY LIGHTING DB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx4 mm² |  |  | 18 |  | B1-UPSP-001 |  | UPS DISTRIBUTION BOARD |  | UPS POWER |  |  |  | 1
B1-JB-14700-P2001 | [11 empty] | NE |  |  |  | B1-JB-14700 | [7 empty] | LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx4 mm² |  |  | 39 |  | B1-LP-1401 |  | NORMAL LIGHTING DB |  | NORMAL POWER |  |  |  | 1
B1-JB-14705-P2001 | [11 empty] | NE |  |  |  | B1-JB-14705 | [7 empty] | LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx4 mm² |  |  | 19 |  | B1-LP-1401 |  | NORMAL LIGHTING DB |  | NORMAL POWER |  |  |  | 1
B1-JB-14707-P2001 | [11 empty] | NE |  |  |  | B1-JB-14707 | [7 empty] | LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx4 mm² |  |  | 54 |  | B1-LP-1401 |  | NORMAL LIGHTING DB |  | NORMAL POWER |  |  |  | 1
B1-JB-14713-P2001 | [11 empty] | NE |  |  |  | B1-JB-14713 | [7 empty] | LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx4 mm² |  |  | 46 |  | B1-LP-1401 |  | NORMAL LIGHTING DB |  | NORMAL POWER |  |  |  | 1
1 / 6
CCP-W-B114-02-ME-E10-0087 HRSG_Cable Schedule C01
Cable Nr | [11 empty] | Supplier |  |  |  | FROM | [34 empty] | CABLE | [12 empty] | TO EQUIPMENT / SYSTEM | [5 empty] | Notes |  | Rev.
[16 empty] | Instrument or Local Panel tag | [7 empty] | Service | [14 empty] | Signal Type CIP ID | [7 empty] | Execution Type |  |  |  | Type | [7 empty] | Formation |  |  | Length |  | Tag |  | Description |  | System
B1-JB-14717-P2001 | [11 empty] | NE |  |  |  | B1-JB-14717 | [7 empty] | LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx4 mm² |  |  | 76 |  | B1-LP-1401 |  | NORMAL LIGHTING DB |  | NORMAL POWER |  |  |  | 1
B1-LT-14700-P2001 | [11 empty] | NE |  |  |  | B1-LT-14700 | [7 empty] | NORMAL LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 12 |  | B1-JB-14700 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-LT-14701-P2001 | [11 empty] | NE |  |  |  | B1-LT-14701 | [7 empty] | NORMAL LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 6 |  | B1-JB-14700 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-JB-14701-P2001 | [11 empty] | NE |  |  |  | B1-JB-14701 | [7 empty] | LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 27 |  | B1-JB-14700 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-LT-14702-P2001 | [11 empty] | NE |  |  |  | B1-LT-14702 | [7 empty] | NORMAL LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 6 |  | B1-JB-14701 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-LT-14727-P2001 | [11 empty] | NE |  |  |  | B1-LT-14727 | [7 empty] | NORMAL LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 4 |  | B1-JB-14705 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-JB-14706-P2001 | [11 empty] | NE |  |  |  | B1-JB-14706 | [7 empty] | LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 26 |  | B1-JB-14705 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-LT-14718-P2001 | [11 empty] | NE |  |  |  | B1-LT-14718 | [7 empty] | NORMAL LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 18 |  | B1-JB-14706 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-LT-14705-P2001 | [11 empty] | NE |  |  |  | B1-LT-14705 | [7 empty] | NORMAL LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 10 |  | B1-JB-14706 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-JB-14704-P2001 | [11 empty] | NE |  |  |  | B1-JB-14704 | [7 empty] | LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 9 |  | B1-JB-14705 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-LT-14704-P2001 | [11 empty] | NE |  |  |  | B1-LT-14704 | [7 empty] | NORMAL LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 6 |  | B1-JB-14704 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-LT-14726-P2001 | [11 empty] | NE |  |  |  | B1-LT-14726 | [7 empty] | NORMAL LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 6 |  | B1-JB-14704 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-JB-14703-P2001 | [11 empty] | NE |  |  |  | B1-JB-14703 | [7 empty] | LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 9 |  | B1-JB-14704 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-LT-14703-P2001 | [11 empty] | NE |  |  |  | B1-LT-14703 | [7 empty] | NORMAL LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 6 |  | B1-JB-14703 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-JB-14702-P2001 | [11 empty] | NE |  |  |  | B1-JB-14702 | [7 empty] | LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 16 |  | B1-JB-14703 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-LT-14728-P2001 | [11 empty] | NE |  |  |  | B1-LT-14728 | [7 empty] | NORMAL LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 11 |  | B1-JB-14702 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-LT-14712-P2001 | [11 empty] | NE |  |  |  | B1-LT-14712 | [7 empty] | NORMAL LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14707 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-JB-14708-P2001 | [11 empty] | NE |  |  |  | B1-JB-14708 | [7 empty] | LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 29 |  | B1-JB-14707 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-LT-14713-P2001 | [11 empty] | NE |  |  |  | B1-LT-14713 | [7 empty] | NORMAL LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14708 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-JB-14709-P2001 | [11 empty] | NE |  |  |  | B1-JB-14709 | [7 empty] | LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 30 |  | B1-JB-14707 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-LT-14714-P2001 | [11 empty] | NE |  |  |  | B1-LT-14714 | [7 empty] | NORMAL LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14709 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-JB-14710-P2001 | [11 empty] | NE |  |  |  | B1-JB-14710 | [7 empty] | LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 11 |  | B1-JB-14709 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-LT-14717-P2001 | [11 empty] | NE |  |  |  | B1-LT-14717 | [7 empty] | NORMAL LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14710 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-JB-14711-P2001 | [11 empty] | NE |  |  |  | B1-JB-14711 | [7 empty] | LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 17 |  | B1-JB-14710 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-LT-14716-P2001 | [11 empty] | NE |  |  |  | B1-LT-14716 | [7 empty] | NORMAL LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14711 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-JB-14712-P2001 | [11 empty] | NE |  |  |  | B1-JB-14712 | [7 empty] | LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 11 |  | B1-JB-14711 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-LT-14715-P2001 | [11 empty] | NE |  |  |  | B1-LT-14715 | [7 empty] | NORMAL LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14712 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-LT-14710-P2001 | [11 empty] | NE |  |  |  | B1-LT-14710 | [7 empty] | NORMAL LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14713 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-LT-14711-P2001 | [11 empty] | NE |  |  |  | B1-LT-14711 | [7 empty] | NORMAL LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 14 |  | B1-JB-14713 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-JB-14714-P2001 | [11 empty] | NE |  |  |  | B1-JB-14714 | [7 empty] | LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 13 |  | B1-JB-14713 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-LT-14709-P2001 | [11 empty] | NE |  |  |  | B1-LT-14709 | [7 empty] | NORMAL LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14714 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-JB-14715-P2001 | [11 empty] | NE |  |  |  | B1-JB-14715 | [7 empty] | LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 11 |  | B1-JB-14714 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-LT-14708-P2001 | [11 empty] | NE |  |  |  | B1-LT-14708 | [7 empty] | NORMAL LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14715 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-JB-14716-P2001 | [11 empty] | NE |  |  |  | B1-JB-14716 | [7 empty] | LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 9 |  | B1-JB-14715 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-LT-14707-P2001 | [11 empty] | NE |  |  |  | B1-LT-14707 | [7 empty] | NORMAL LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14716 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-LT-14706-P2001 | [11 empty] | NE |  |  |  | B1-LT-14706 | [7 empty] | NORMAL LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 6 |  | B1-JB-14716 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-LT-14721-P2001 | [11 empty] | NE |  |  |  | B1-LT-14721 | [7 empty] | NORMAL LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 15 |  | B1-JB-14717 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-LT-14719-P2001 | [11 empty] | NE |  |  |  | B1-LT-14719 | [7 empty] | NORMAL LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14717 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
2 / 6
CCP-W-B114-02-ME-E10-0087 HRSG_Cable Schedule C01
Cable Nr | [11 empty] | Supplier |  |  |  | FROM | [34 empty] | CABLE | [12 empty] | TO EQUIPMENT / SYSTEM | [5 empty] | Notes |  | Rev.
[16 empty] | Instrument or Local Panel tag | [7 empty] | Service | [14 empty] | Signal Type CIP ID | [7 empty] | Execution Type |  |  |  | Type | [7 empty] | Formation |  |  | Length |  | Tag |  | Description |  | System
B1-JB-14722-P2001 | [11 empty] | NE |  |  |  | B1-JB-14722 | [7 empty] | LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14717 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-LT-14720-P2001 | [11 empty] | NE |  |  |  | B1-LT-14720 | [7 empty] | NORMAL LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 8 |  | B1-JB-14722 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-JB-14718-P2001 | [11 empty] | NE |  |  |  | B1-JB-14718 | [7 empty] | LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 30 |  | B1-JB-14722 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-LT-14722-P2001 | [11 empty] | NE |  |  |  | B1-LT-14722 | [7 empty] | NORMAL LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14718 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-JB-14719-P2001 | [11 empty] | NE |  |  |  | B1-JB-14719 | [7 empty] | LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 18 |  | B1-JB-14718 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-LT-14725-P2001 | [11 empty] | NE |  |  |  | B1-LT-14725 | [7 empty] | NORMAL LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14719 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-JB-14720-P2001 | [11 empty] | NE |  |  |  | B1-JB-14720 | [7 empty] | LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 12 |  | B1-JB-14719 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-LT-14724-P2001 | [11 empty] | NE |  |  |  | B1-LT-14724 | [7 empty] | NORMAL LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14720 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-JB-14721-P2001 | [11 empty] | NE |  |  |  | B1-JB-14721 | [7 empty] | LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 16 |  | B1-JB-14720 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-LT-14723-P2001 | [11 empty] | NE |  |  |  | B1-LT-14723 | [7 empty] | NORMAL LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14721 |  | LIGHTING JB |  | NORMAL POWER |  |  |  | 1
B1-LG-14530-P2001 | [11 empty] | NE |  |  |  | B1-LG-14530 | [7 empty] | HP STEAM DRUM LEVEL INDICATOR LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 61 |  | B1-JB-14721 |  | NORMAL LIGHTING DB |  | NORMAL POWER |  |  |  | 1
B1-MAP-1401-P2001 | [11 empty] | NE |  |  |  | B1-MAP-1401 | [7 empty] | MARSHALLING CABINET AUX LIGHT | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 15 |  | B1-JB-14721 |  | NORMAL LIGHTING DB |  | NORMAL POWER |  |  |  | 1
B1-SO-14700-P2001 | [11 empty] | NE |  |  |  | B1-SO-14700 | [7 empty] | 16A, 1PH SOCKET | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx4 mm² |  |  | 45 |  | B1-LP-1401 |  | NORMAL LIGHTING DB |  | NORMAL POWER |  |  |  | 1
B1-JB-14755-P2001 | [11 empty] | NE |  |  |  | B1-JB-14755 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx4 mm² |  |  | 45 |  | B1-ELP-1401 |  | EMERGENCY LIGHTING DB |  | UPS POWER |  |  |  | 1
B1-JB-14758-P2001 | [11 empty] | NE |  |  |  | B1-JB-14758 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx4 mm² |  |  | 20 |  | B1-ELP-1401 |  | EMERGENCY LIGHTING DB |  | UPS POWER |  |  |  | 1
B1-JB-14759-P2001 | [11 empty] | NE |  |  |  | B1-JB-14759 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx4 mm² |  |  | 9 |  | B1-ELP-1401 |  | EMERGENCY LIGHTING DB |  | UPS POWER |  |  |  | 1
B1-JB-14764-P2001 | [11 empty] | NE |  |  |  | B1-JB-14764 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx4 mm² |  |  | 18 |  | B1-ELP-1401 |  | EMERGENCY LIGHTING DB |  | UPS POWER |  |  |  | 1
B1-JB-14769-P2001 | [11 empty] | NE |  |  |  | B1-JB-14769 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx4 mm² |  |  | 49 |  | B1-ELP-1401 |  | EMERGENCY LIGHTING DB |  | UPS POWER |  |  |  | 1
B1-JB-14773-P2001 | [11 empty] | NE |  |  |  | B1-JB-14773 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx4 mm² |  |  | 61 |  | B1-ELP-1401 |  | EMERGENCY LIGHTING DB |  | UPS POWER |  |  |  | 1
B1-JB-14777-P2001 | [11 empty] | NE |  |  |  | B1-JB-14777 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx4 mm² |  |  | 75 |  | B1-ELP-1401 |  | EMERGENCY LIGHTING DB |  | UPS POWER |  |  |  | 1
B1-JB-14782-P2001 | [11 empty] | NE |  |  |  | B1-JB-14782 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx4 mm² |  |  | 53 |  | B1-ELP-1401 |  | EMERGENCY LIGHTING DB |  | UPS POWER |  |  |  | 1
B1-JB-14786-P2001 | [11 empty] | NE |  |  |  | B1-JB-14786 | [7 empty] | EXIT LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx4 mm² |  |  | 18 |  | B1-ELP-1401 |  | EMERGENCY LIGHTING DB |  | UPS POWER |  |  |  | 1
B1-JB-14790-P2001 | [11 empty] | NE |  |  |  | B1-JB-14790 | [7 empty] | EXIT LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx4 mm² |  |  | 48 |  | B1-ELP-1401 |  | EMERGENCY LIGHTING DB |  | UPS POWER |  |  |  | 1
B1-JB-14791-P2001 | [11 empty] | NE |  |  |  | B1-JB-14791 | [7 empty] | EXIT LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx4 mm² |  |  | 34 |  | B1-ELP-1401 |  | EMERGENCY LIGHTING DB |  | UPS POWER |  |  |  | 1
B1-JB-14798-P2001 | [11 empty] | NE |  |  |  | B1-JB-14798 | [7 empty] | EXIT LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx4 mm² |  |  | 60 |  | B1-ELP-1401 |  | EMERGENCY LIGHTING DB |  | UPS POWER |  |  |  | 1
B1-ELT-14702-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14702 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14755 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14752-P2001 | [11 empty] | NE |  |  |  | B1-JB-14752 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 15 |  | B1-JB-14755 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14703-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14703 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14752 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14750-P2001 | [11 empty] | NE |  |  |  | B1-JB-14750 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 12 |  | B1-JB-14752 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14701-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14701 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14750 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14700-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14700 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 8 |  | B1-JB-14750 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14751-P2001 | [11 empty] | NE |  |  |  | B1-JB-14751 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 18 |  | B1-JB-14750 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14743-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14743 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14751 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14753-P2001 | [11 empty] | NE |  |  |  | B1-JB-14753 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 13 |  | B1-JB-14752 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14704-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14704 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14753 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14754-P2001 | [11 empty] | NE |  |  |  | B1-JB-14754 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 14 |  | B1-JB-14753 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14705-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14705 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14754 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14719-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14719 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 7 |  | B1-JB-14758 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
3 / 6
CCP-W-B114-02-ME-E10-0087 HRSG_Cable Schedule C01
Cable Nr | [11 empty] | Supplier |  |  |  | FROM | [34 empty] | CABLE | [12 empty] | TO EQUIPMENT / SYSTEM | [5 empty] | Notes |  | Rev.
[16 empty] | Instrument or Local Panel tag | [7 empty] | Service | [14 empty] | Signal Type CIP ID | [7 empty] | Execution Type |  |  |  | Type | [7 empty] | Formation |  |  | Length |  | Tag |  | Description |  | System
B1-JB-14757-P2001 | [11 empty] | NE |  |  |  | B1-JB-14757 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 22 |  | B1-JB-14758 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14718-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14718 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14757 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14756-P2001 | [11 empty] | NE |  |  |  | B1-JB-14756 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 17 |  | B1-JB-14757 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14717-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14717 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14756 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14728-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14728 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14759 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14760-P2001 | [11 empty] | NE |  |  |  | B1-JB-14760 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 9 |  | B1-JB-14759 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14729-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14729 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14760 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14761-P2001 | [11 empty] | NE |  |  |  | B1-JB-14761 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 9 |  | B1-JB-14760 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14730-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14730 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14761 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14762-P2001 | [11 empty] | NE |  |  |  | B1-JB-14762 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 9 |  | B1-JB-14761 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14731-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14731 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14762 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14763-P2001 | [11 empty] | NE |  |  |  | B1-JB-14763 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 9 |  | B1-JB-14762 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14732-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14732 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14763 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14744-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14744 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 12 |  | B1-JB-14763 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14721-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14721 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14764 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14722-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14722 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14764 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14765-P2001 | [11 empty] | NE |  |  |  | B1-JB-14765 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 9 |  | B1-JB-14764 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14723-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14723 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14765 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14766-P2001 | [11 empty] | NE |  |  |  | B1-JB-14766 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 9 |  | B1-JB-14765 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14724-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14724 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14766 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14767-P2001 | [11 empty] | NE |  |  |  | B1-JB-14767 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 9 |  | B1-JB-14766 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14725-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14725 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14767 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14768-P2001 | [11 empty] | NE |  |  |  | B1-JB-14768 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 9 |  | B1-JB-14767 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14726-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14726 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 15 |  | B1-JB-14768 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14727-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14727 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14768 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14715-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14715 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14769 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14770-P2001 | [11 empty] | NE |  |  |  | B1-JB-14770 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 16 |  | B1-JB-14769 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14716-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14716 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14770 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14706-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14706 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 18 |  | B1-JB-14770 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14771-P2001 | [11 empty] | NE |  |  |  | B1-JB-14771 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 17 |  | B1-JB-14769 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14710-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14710 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 9 |  | B1-JB-14771 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14709-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14709 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 9 |  | B1-JB-14771 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14772-P2001 | [11 empty] | NE |  |  |  | B1-JB-14772 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14771 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14708-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14708 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 6 |  | B1-JB-14772 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14707-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14707 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 13 |  | B1-JB-14772 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14734-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14734 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 7 |  | B1-JB-14773 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14774-P2001 | [11 empty] | NE |  |  |  | B1-JB-14774 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 6 |  | B1-JB-14773 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14735-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14735 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 7 |  | B1-JB-14774 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
4 / 6
CCP-W-B114-02-ME-E10-0087 HRSG_Cable Schedule C01
Cable Nr | [11 empty] | Supplier |  |  |  | FROM | [34 empty] | CABLE | [12 empty] | TO EQUIPMENT / SYSTEM | [5 empty] | Notes |  | Rev.
[16 empty] | Instrument or Local Panel tag | [7 empty] | Service | [14 empty] | Signal Type CIP ID | [7 empty] | Execution Type |  |  |  | Type | [7 empty] | Formation |  |  | Length |  | Tag |  | Description |  | System
B1-ELT-14737-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14737 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 8 |  | B1-JB-14774 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14775-P2001 | [11 empty] | NE |  |  |  | B1-JB-14775 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14774 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14736-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14736 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 6 |  | B1-JB-14775 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14776-P2001 | [11 empty] | NE |  |  |  | B1-JB-14776 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 9 |  | B1-JB-14775 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14733-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14733 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 9 |  | B1-JB-14776 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14738-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14738 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 15 |  | B1-JB-14777 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14778-P2001 | [11 empty] | NE |  |  |  | B1-JB-14778 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 15 |  | B1-JB-14777 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14739-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14739 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14778 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14779-P2001 | [11 empty] | NE |  |  |  | B1-JB-14779 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 10 |  | B1-JB-14778 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14740-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14740 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14779 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14780-P2001 | [11 empty] | NE |  |  |  | B1-JB-14780 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 11 |  | B1-JB-14779 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14741-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14741 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14780 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14781-P2001 | [11 empty] | NE |  |  |  | B1-JB-14781 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 23 |  | B1-JB-14780 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14742-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14742 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14781 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14711-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14711 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 9 |  | B1-JB-14782 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14783-P2001 | [11 empty] | NE |  |  |  | B1-JB-14783 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 28 |  | B1-JB-14782 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14712-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14712 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14783 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14784-P2001 | [11 empty] | NE |  |  |  | B1-JB-14784 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 26 |  | B1-JB-14782 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14713-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14713 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14784 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14785-P2001 | [11 empty] | NE |  |  |  | B1-JB-14785 | [7 empty] | EMERGENCY LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 26 |  | B1-JB-14784 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14714-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14714 | [7 empty] | EMERGENCY LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14785 |  | EMERGENCY LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14753-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14753 | [7 empty] | EXIT LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 25 |  | B1-JB-14786 |  | EXIT LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14754-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14754 | [7 empty] | EXIT LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14786 |  | EXIT LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14787-P2001 | [11 empty] | NE |  |  |  | B1-JB-14787 | [7 empty] | EXIT LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 9 |  | B1-JB-14786 |  | EXIT LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14755-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14755 | [7 empty] | EXIT LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14787 |  | EXIT LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14788-P2001 | [11 empty] | NE |  |  |  | B1-JB-14788 | [7 empty] | EXIT LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 9 |  | B1-JB-14787 |  | EXIT LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14756-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14756 | [7 empty] | EXIT LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14788 |  | EXIT LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14789-P2001 | [11 empty] | NE |  |  |  | B1-JB-14789 | [7 empty] | EXIT LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 9 |  | B1-JB-14788 |  | EXIT LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14757-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14757 | [7 empty] | EXIT LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14789 |  | EXIT LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14758-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14758 | [7 empty] | EXIT LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 14 |  | B1-JB-14789 |  | EXIT LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14760-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14760 | [7 empty] | EXIT LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14790 |  | EXIT LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14759-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14759 | [7 empty] | EXIT LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 23 |  | B1-JB-14790 |  | EXIT LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14750-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14750 | [7 empty] | EXIT LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14791 |  | EXIT LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14792-P2001 | [11 empty] | NE |  |  |  | B1-JB-14792 | [7 empty] | EXIT LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 41 |  | B1-JB-14791 |  | EXIT LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14751-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14751 | [7 empty] | EXIT LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14792 |  | EXIT LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14793-P2001 | [11 empty] | NE |  |  |  | B1-JB-14793 | [7 empty] | EXIT LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 29 |  | B1-JB-14792 |  | EXIT LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14752-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14752 | [7 empty] | EXIT LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14793 |  | EXIT LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14763-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14763 | [7 empty] | EXIT LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14798 |  | EXIT LIGHTING JB |  | UPS POWER |  |  |  | 1
5 / 6
CCP-W-B114-02-ME-E10-0087 HRSG_Cable Schedule C01
Cable Nr | [11 empty] | Supplier |  |  |  | FROM | [34 empty] | CABLE | [12 empty] | TO EQUIPMENT / SYSTEM | [5 empty] | Notes |  | Rev.
[16 empty] | Instrument or Local Panel tag | [7 empty] | Service | [14 empty] | Signal Type CIP ID | [7 empty] | Execution Type |  |  |  | Type | [7 empty] | Formation |  |  | Length |  | Tag |  | Description |  | System
B1-JB-14796-P2001 | [11 empty] | NE |  |  |  | B1-JB-14796 | [7 empty] | EXIT LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 6 |  | B1-JB-14798 |  | EXIT LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14764-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14764 | [7 empty] | EXIT LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14796 |  | EXIT LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14765-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14765 | [7 empty] | EXIT LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 7 |  | B1-JB-14796 |  | EXIT LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14797-P2001 | [11 empty] | NE |  |  |  | B1-JB-14797 | [7 empty] | EXIT LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 16 |  | B1-JB-14796 |  | EXIT LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14766-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14766 | [7 empty] | EXIT LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14797 |  | EXIT LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14767-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14767 | [7 empty] | EXIT LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14797 |  | EXIT LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14794-P2001 | [11 empty] | NE |  |  |  | B1-JB-14794 | [7 empty] | EXIT LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 16 |  | B1-JB-14797 |  | EXIT LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14761-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14761 | [7 empty] | EXIT LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14794 |  | EXIT LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-JB-14795-P2001 | [11 empty] | NE |  |  |  | B1-JB-14795 | [7 empty] | EXIT LIGHTING JB | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 38 |  | B1-JB-14794 |  | EXIT LIGHTING JB |  | UPS POWER |  |  |  | 1
B1-ELT-14762-P2001 | [11 empty] | NE |  |  |  | B1-ELT-14762 | [7 empty] | EXIT LAMP | [14 empty] | POWER FEEDING | [7 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 5 |  | B1-JB-14795 |  | EXIT LIGHTING JB |  | UPS POWER |  |  |  | 1
SEI1230AC_CUTR-P2001 | [11 empty] | NE |  |  |  | SEI1230AC_CUTR | [7 empty] | PHOTOELECTRIC SWITCH | [22 empty] | N/A |  |  |  | CU/0H/FR/LS0H 0.6/1 kV | [7 empty] | 5C+PE x 2.5 mm² |  |  | 75 |  | B1-AWL-14001 |  | AWL PANEL |  | UPS POWER |  |  |  | 1
W24_0202_GPS_ANT-P2001 | [11 empty] | NE |  |  |  | W24_0202_GPS_ANT | [7 empty] | GPS ANTENNA | [22 empty] | N/A |  |  |  | CU/0H/FR/LS0H 0.6/1 kV | [7 empty] | 5C+PE x 2.5 mm² |  |  | 75 |  | B1-AWL-14001 |  | AWL PANEL |  | UPS POWER |  |  |  | 1
W24_0202_SCSD05-P2001 | [11 empty] | NE |  |  |  | W24_0202_SCSD05 | [7 empty] | MAIN STACK JUNCTION BOX | [22 empty] | N/A |  |  |  | CU/0H/FR/LS0H 0.6/1 kV | [7 empty] | 5C+PE x 2.5 mm² |  |  | 75 |  | B1-AWL-14001 |  | AWL PANEL |  | UPS POWER |  |  |  | 1
B1-LT-14791-P2001 | [11 empty] | NE |  |  |  | B1-LT-14791 | [7 empty] | MIOLB-E1_24202 FLASHING LIGHT | [22 empty] | N/A |  |  |  | CU/0H/FR/LS0H 0.6/1 kV | [7 empty] | 5C+PE x 2.5 mm² |  |  | 12 |  | W24_0202_SCSD05 |  | MAIN STACK JUNCTION BOX |  | UPS POWER |  |  |  | 1
B1-LT-14792-P2001 | [11 empty] | NE |  |  |  | B1-LT-14792 | [7 empty] | MIOLB-E1_24202 FLASHING LIGHT | [22 empty] | N/A |  |  |  | CU/0H/FR/LS0H 0.6/1 kV | [7 empty] | 5C+PE x 2.5 mm² |  |  | 20 |  | W24_0202_SCSD05 |  | MAIN STACK JUNCTION BOX |  | UPS POWER |  |  |  | 1
B1-LT-14793-P2001 | [11 empty] | NE |  |  |  | B1-LT-14793 | [7 empty] | MIOLB-E1_24202 FLASHING LIGHT | [22 empty] | N/A |  |  |  | CU/0H/FR/LS0H 0.6/1 kV | [7 empty] | 5C+PE x 2.5 mm² |  |  | 21 |  | W24_0202_SCSD05 |  | MAIN STACK JUNCTION BOX |  | UPS POWER |  |  |  | 1
B1-LT-14794-P2001 | [11 empty] | NE |  |  |  | B1-LT-14794 | [7 empty] | MIOLB-E1_24202 FLASHING LIGHT | [22 empty] | N/A |  |  |  | CU/0H/FR/LS0H 0.6/1 kV | [7 empty] | 5C+PE x 2.5 mm² |  |  | 18 |  | W24_0202_SCSD05 |  | MAIN STACK JUNCTION BOX |  | UPS POWER |  |  |  | 1
W24_0202_SCSD05-P2001 | [11 empty] | NE |  |  |  | W24_0202_SCSD05 | [7 empty] | BY-PASS STACK JUNCTION BOX | [22 empty] | N/A |  |  |  | CU/0H/FR/LS0H 0.6/1 kV | [7 empty] | 5C+PE x 2.5 mm² |  |  | 72 |  | B1-AWL-14001 |  | AWL PANEL |  | UPS POWER |  |  |  | 1
B1-LT-14795-P2001 | [11 empty] | NE |  |  |  | B1-LT-14795 | [7 empty] | MIOLB-E1_24202 FLASHING LIGHT | [22 empty] | N/A |  |  |  | CU/0H/FR/LS0H 0.6/1 kV | [7 empty] | 5C+PE x 2.5 mm² |  |  | 13 |  | W24_0202_SCSD05 |  | BY-PASS STACK JUNCTION BOX |  | UPS POWER |  |  |  | 1
B1-LT-14796-P2001 | [11 empty] | NE |  |  |  | B1-LT-14796 | [7 empty] | MIOLB-E1_24202 FLASHING LIGHT | [22 empty] | N/A |  |  |  | CU/0H/FR/LS0H 0.6/1 kV | [7 empty] | 5C+PE x 2.5 mm² |  |  | 19 |  | W24_0202_SCSD05 |  | BY-PASS STACK JUNCTION BOX |  | UPS POWER |  |  |  | 1
B1-LT-14797-P2001 | [11 empty] | NE |  |  |  | B1-LT-14797 | [7 empty] | MIOLB-E1_24202 FLASHING LIGHT | [22 empty] | N/A |  |  |  | CU/0H/FR/LS0H 0.6/1 kV | [7 empty] | 5C+PE x 2.5 mm² |  |  | 21 |  | W24_0202_SCSD05 |  | BY-PASS STACK JUNCTION BOX |  | UPS POWER |  |  |  | 1
B1-LT-14798-P2001 | [11 empty] | NE |  |  |  | B1-LT-14798 | [7 empty] | MIOLB-E1_24202 FLASHING LIGHT | [22 empty] | N/A |  |  |  | CU/0H/FR/LS0H 0.6/1 kV | [7 empty] | 5C+PE x 2.5 mm² |  |  | 20 |  | W24_0202_SCSD05 |  | BY-PASS STACK JUNCTION BOX |  | UPS POWER |  |  |  | 1
B1-AT-14081-P2001 | [11 empty] | NE |  |  |  | B1-AT-14081 | [7 empty] | DUST METER | [22 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 82 |  | B1-A-1481 |  | CEMS PANEL |  | UPS POWER |  |  |  | 1
B1-AE-14080A-P2001 | [11 empty] | NE |  |  |  | B1-AE-14080A | [7 empty] | SAMPLE PROBE | [22 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 85 |  | B1-A-1481 |  | CEMS PANEL |  | UPS POWER |  |  |  | 1
B1-AE-14080B-P2001 | [11 empty] | NE |  |  |  | B1-AE-14080B | [7 empty] | SAMPLE PROBE | [22 empty] | N/A |  |  |  | CU/XLPE/FR/0HLS 0.6/1 kV | [7 empty] | 3Gx2.5 mm² |  |  | 85 |  | B1-A-1481 |  | CEMS PANEL |  | UPS POWER |  |  |  | 1
6 / 6
POWER CABLES - BOM
|  | POS |  |  |  | SUPPLIER | [7 empty] | CABLE CHARACTERISTICS | [18 empty] | QUANTITIES | [19 empty] | NOTES
[14 empty] | TYPE | [9 empty] | FORMATION |  |  | DIAMETER [mm] (+/-10%) | [5 empty] | REQUIRED FOR 4 UNIT [m] |  |  |  |  | SPARE | [7 empty] | TOTAL ORDER FOR 4 UNIT [m]
|  | 1 |  |  |  | NE | [7 empty] | CU/XLPE/FR/0HLS 0.6/1 kV | [9 empty] | 4Gx4 mm² |  |  | Later | [5 empty] | 827 |  |  |  |  | 82.7 | [7 empty] | 3638.8
|  | 2 |  |  |  | NE | [7 empty] | CU/XLPE/FR/0HLS 0.6/1 kV | [9 empty] | 3Gx4 mm² |  |  | Later | [5 empty] | 1386 |  |  |  |  | 138.6 | [7 empty] | 6098.4
|  | 3 |  |  |  | NE | [7 empty] | CU/XLPE/FR/0HLS 0.6/1 kV | [9 empty] | 3Gx2.5 mm² |  |  | Later | [5 empty] | 1820 |  |  |  |  | 182 | [7 empty] | 8008
|  | 4 |  |  |  | NE | [7 empty] | CU/XLPE/FR/0HLS 0.6/1 kV | [9 empty] | 5Gx6 mm² |  |  | Later | [5 empty] | 124 |  |  |  |  | 12.4 | [7 empty] | 545.6
|  | 5 |  |  |  | NE | [7 empty] | CU/0H/FR/LS0H 0.6/1 kV | [9 empty] | 5C+PE x 2.5 mm² |  |  | Later | [5 empty] | 441 |  |  |  |  | 44.1 | [7 empty] | 1940.4
THIS DOCUMENT IS THE PROPERTY OF NE SRL AND MAY NOT BE REPRODUCED OR CIRCULATED UNLESS ON PRIOR WRITTEN AUTHORIZATION
Document Number: 234249-00-CAB001
[35 empty] | Revision 01 | [6 empty] | Date: 02/07/2024 | [15 empty] | Page 2 of 14
[35 empty] | Document Type: | [14 empty] | SPECIFICATION
POWER & CONTROL CABLE TECHNICAL SPECIFICATION
POWER AND CONTROL CABLE - TECHNICAL SPECIFICATION
REV |  |  |  |  | DATE | [9 empty] | DESCRIPTION | [29 empty] | SIGNATURES | [13 empty] | QAM
[45 empty] | Issued | [7 empty] | Approved | [5 empty] | Review
00 |  |  |  |  | 2024-03-08 | [9 empty] | PRELIMINARY ISSUE | [29 empty] | ED | [7 empty] | MM | [5 empty] | -
01 |  |  |  |  | 2024-07-02 | [9 empty] | COMMENTS ON CABLE CONFIGURATIONS | [29 empty] | ED | [7 empty] | MM | [5 empty] | -
Document Number: 234249-00-CAB001
[34 empty] | Revision 01 | [6 empty] | Date: 02/07/2024 | [15 empty] | Page 3 of 14
[34 empty] | Document Type: | [14 empty] | SPECIFICATION
POWER & CONTROL CABLE TECHNICAL SPECIFICATION
INDEX
SCOPE 4
GENERAL 4
AMBIENT CONDITIONS 4
LANGUAGE 4
CODES, REGULATIONS AND STANDARDS 5
MARKING 6
I&C MULTICORE / SINGLE & MULTI PAIRS CABLE TYPES 8 Single-pair - I&C Cables for NOT I.S. circuits 8 Multicore I&C Cables for NOT I.S. circuits 9
Multicore cables - LV Power Cables (0.4kV and below) 10 Without Ground (PE) Conductor 10 With Ground (PE) Conductor 11
CABLES USED FORMATIONS 12 Single-pair - I/C Cables for not I.S. circuits 14 Multicore - I&C Cables for NOT I.S. circuits 14 Multicore cables - LV Power Cables (0.4kV and below) 14
Document Number: 234249-00-CAB001
[34 empty] | Revision 01 | [6 empty] | Date: 02/07/2024 | [15 empty] | Page 4 of 14
[34 empty] | Document Type: | [14 empty] | SPECIFICATION
POWER & CONTROL CABLE TECHNICAL SPECIFICATION
SCOPE The scope of this technical specification is to describe technical requirements regarding the power and instrument / control cables relevant to the cabling system of four (4) HRSGs of Shymkent, Kazakhstan. HRSGs are installed inside a building.
This specification is applicable to the following items:
- HRSG-1 - HRSG-2 - HRSG-3 - HRSG-4
GENERAL It is not the purpose of this specification and enclosed or referred documents to describe all design and construction details. It shall be responsibility of the Supplier to select and supply all cables & wires that have been designed and fabricated for the required service conditions in compliance to all applicable codes and current standards of engineering suitable for the intended service of cables system.
 Here below some general requirements: o Cables will be laid in safe area. o Multicores cables & wires must be IEC code or applicable local authority stamped.  Wire and cable design shall provide the following : o Accurate and reliable transmission of measurement, status, and control signals. o The cables shall be delivered on non-returnable cable drums, which shall be designed (e.g., cover or planking) to protect the cable against damage during transportation. o All cable ends must be sealed to prevent entrance of moisture during shipment or outdoor storage on site. o Final lengths of cable on a drum shall be with tolerance -0/+2% based on the Bill of Quantities.
AMBIENT CONDITIONS
[9 empty] | Environmental | [16 empty] | Minimum | [14 empty] | Maximum
[9 empty] | Temperature (°C) (Outside) | [16 empty] | -30.3 °C | [14 empty] | +44.2 °C
[9 empty] | Temperature (°C) (Inside) | [16 empty] | +10 °C | [14 empty] | +50.2 °C
[9 empty] | Relative Humidity | [16 empty] | 57%
[9 empty] | Site Elevation (m) | [16 empty] | 695 m above m.s.l
LANGUAGE The official language for general correspondence, technical information data, drawings, test data, literature, and any other document to be supplied shall be English & Russian.
Document Number: 234249-00-CAB001
[34 empty] | Revision 01 | [6 empty] | Date: 02/07/2024 | [15 empty] | Page 5 of 14
[34 empty] | Document Type: | [14 empty] | SPECIFICATION
POWER & CONTROL CABLE TECHNICAL SPECIFICATION
CODES, REGULATIONS AND STANDARDS Design shall conform to the related IEC standards, to applicable local rules and the last issue of the standards and codes issued by the following associations (issue that was applicable at the time of award of contract): Where any conflict exists between the referenced codes or standards, the most stringent of the codes or standards shall prevail.
[6 empty] | CODE | [15 empty] | CODE SUBJECT
[6 empty] | IEC 60228 | [15 empty] | Conductors for Insulated Cables
[6 empty] | IEC 60502 | [15 empty] | Power cable with Extruded Insulation and Their Accessories for Rated Voltages from 1kV up to 30kV
[6 empty] | IEC 60331-21 | [15 empty] | Tests for electric cables under fire conditions - Circuit integrity - Part 21: Procedures and requirements - Cables of rated voltage up to and including 0,6/1,0 kV
[6 empty] | IEC 60332-1-2 | [15 empty] | Test on Electric and Optical fibre cables under fire conditions – Part 1-2: Test for vertical flame propagation for a single insulated wire or cable
[6 empty] | IEC 60332-3 | [15 empty] | Test on Electric and Optical fibre cables under fire conditions – Part 3- 10: Test for vertical flame spread of vertically mounted bunched wires or cables - Apparatus
[6 empty] | BS EN 50288-7 | [15 empty] | Multi-element metallic cables used in analogue and digital communication and control. Sectional specification for instrumentation and control cables
[6 empty] | IEC 60304 | [15 empty] | Standard colours for Insulation of Low Frequency Cables and Wires
[6 empty] | ANSI/ICEA S-73-532 | [15 empty] | Standard for Control, Thermocouple Extension, and Instrumentation Cables
[6 empty] | IEC 60364-4-44 | [15 empty] | Protection for safety – Protection against voltage disturbances and electromagnetic disturbances
[6 empty] | IEEE 43 | [15 empty] | Methodical recommendations for testing the insulation strength of electrical equipment.
[6 empty] | IEEE 118 | [15 empty] | Standard Test Code for Resistance Measurement
[6 empty] | IEC 17050-1 | [15 empty] | Supplier’s Declaration of Conformity
[6 empty] | IEC 61034 | [15 empty] | Measurement of smoke density of cables burning under defined conditions
[6 empty] | IEC 60092-376 | [15 empty] | Applicable Standard for Screened and Unscreened cables for Control and Instrumentation Circuits.
[6 empty] | IEC 60227-1 | [15 empty] | Polyvinyl chloride insulated cables of rated voltage up to and including 450/750V
[6 empty] | IEC 60344 | [15 empty] | Calculation of D.C. resistance of plain and coated copper conductors of Low-Frequency cables and wires
[6 empty] | IEC 60584-3 | [15 empty] | Thermocouples - Part 3: Extension and compensating cables - Tolerances and identification system
[6 empty] | IEC 61156-1 | [15 empty] | Multicore and symmetrical pair/quad cables for digital communication – Part 1: Generic Specification
Document Number: 234249-00-CAB001
[34 empty] | Revision 01 | [6 empty] | Date: 02/07/2024 | [15 empty] | Page 6 of 14
[34 empty] | Document Type: | [14 empty] | SPECIFICATION
POWER & CONTROL CABLE TECHNICAL SPECIFICATION
[6 empty] | IEC 61156-7 | [15 empty] | Multicore and symmetrical pair/quad cables for digital communication – Part 7: Symmetrical pair cables with transmission characteristics up to 1200 MHz – Sectional specification for digital and analogue communication cables
[6 empty] | IEC 62305 | [15 empty] | Protection against Lightning
All cables shall comply with the following:  Maximum temperature rating of power cable conductors does not exceed 90ºC under normal operation & 250ºC under short-circuit conditions.  Conductor material shall be annealed copper complying with IEC 60228. Each conductor shall have at least seven strands.  All cables shall be suitable for correct and safe operation in the environmental conditions in which they will be installed.  Cables shall not be jointed except in long runs where production lengths cannot be manufactured to the desired length.  Cables which are run underground shall be installed in conduits.  Cables carry the manufacturer’s identification, number of conductors, conductor material, year of manufacturer, and size printed on the outer jacket for the entire length of the cable.  Cable splices are prohibited unless protected by junction boxes specifically intended for that purpose.
MARKING 1.1 Cables marking
The outer sheath of cable shall be indelibly marked as follows below information:  Manufacturer's name and Year of manufacture  Voltage of Rating  Temperature Rating  Core/Pair Numbering  Size and Type of cable  Numbers of Cores/Pairs/Triads  Cable Length, starting at zero, marked every 1m cable length.
Each cable shall have a ripcord, and the outer sheath of cable shall be embossed and/or printed with the minimum information along the cable length at 1 Meter interval.
1.2 Cables drums marking, numbering and colour painting
Cable drums shall be indelibly marked as follows below information: 1) Number : AA-A-NNNN (AA: V/C Code, A: Cable Type Code, NNNN : Serial Number)
2) V/C Code (AA) - PE : Electrical - PI : Instrumentation & Control - PH : HVAC
Document Number: 234249-00-CAB001
[34 empty] | Revision 01 | [6 empty] | Date: 02/07/2024 | [15 empty] | Page 7 of 14
[34 empty] | Document Type: | [14 empty] | SPECIFICATION
POWER & CONTROL CABLE TECHNICAL SPECIFICATION
- PF : Fire Fighting - PW : Water Treatment - BB : Boiler - TB : Turbine/Generator - PA : Other packages
3) Cable Type Code (A) - M : MV Power Cable - L : LV Power Cable - C : Control Cable - I : Instrumentation Cable - F : Fire Resisting LV Power Cable
4) Drum Colour - Yellow : Electrical - Blue : Instrumentation & Control - Purple : HVAC - Pink : Fire Fighting - Orange : Water Treatment - Red : Boiler - Black : Turbine/Generator - No colour : Other Package
5) Manufacturer’s Name and Year of Manufacture 6) Project No. 7) Requisition Number and Project Name 8) Requisition Item Number 9) Total Weight of Drum Including Cable 10) Length of Cable on the drum (in Meters) 11) Drum Overall Sizes 12) Overall, Weight of Cable and Drum (kgs). 13) Rated Voltage 14) Minimum Bend Radius 15) Maximum Pulling Tension 16) Number and Cross Section of Cores/Pairs/Triads
Document Number: 234249-00-CAB001
[34 empty] | Revision 01 | [6 empty] | Date: 02/07/2024 | [15 empty] | Page 8 of 14
[34 empty] | Document Type: | [14 empty] | SPECIFICATION
POWER & CONTROL CABLE TECHNICAL SPECIFICATION
I&C MULTICORE / SINGLE & MULTI PAIRS CABLE TYPES Single-pair - I&C Cables for NOT I.S. circuits
[6 empty] | GENERAL | [11 empty] | 1 |  |  | Cable code | [16 empty] | After P.O.
[18 empty] | 2 |  |  | Cable description | [16 empty] | Single-pair cable-Twisted-Overall Shield-Flame Retardant-Zero Halogen-Low Smoke-No fire propagation
[6 empty] | CONDUCTOR | [11 empty] | 3 |  |  | Reference Standard | [16 empty] | IEC 60228
[18 empty] | 4 |  |  | Type | [16 empty] | Stranded annealed high conductivity Copper conductor
[18 empty] | 5 |  |  | Formation | [16 empty] | 1x(1Px1.5) mm² (OSH)
[6 empty] | CONDUCTOR INSULATION | [11 empty] | 6 |  |  | Reference Standard | [16 empty] | IEC 60227-1 & IEC 60502-1
[18 empty] | 7 |  |  | Type | [16 empty] | Zero Halogen Polymer
[18 empty] | 8 |  |  | Colours | [16 empty] | Black (+) / White (-)
[18 empty] | 9 |  |  | Number Coded | [16 empty] | Yes
[6 empty] | FILLER | [11 empty] | 10 |  |  | Type | [16 empty] | Polypropylene yarn
[6 empty] | BINDER/WRAPPING | [11 empty] | 11 |  |  | Type | [16 empty] | Polyester Tape
[6 empty] | SHIELDS | [11 empty] | 12 |  |  | Pair/triple/quads shield | [16 empty] | Not Applicable
[18 empty] | 13 |  |  | Overall shield | [16 empty] | Yes
[18 empty] | 14 |  |  | Shield type | [16 empty] | Al/Polyester tape overlapped approx. 25% (1/4 cycle) with 100% coverage, with a minimum 7/0.25mm tinned copper drain wire.
[18 empty] | 15 |  |  | Ground PE yellow/green | [16 empty] | Not Required
[18 empty] | 16 |  |  | Drain wire | [16 empty] | Yes, 0.50 mm²
[6 empty] | INNER SHEATHS | [11 empty] | 17 |  |  | Reference Standard | [16 empty] | Not Applicable
[18 empty] | 18 |  |  | Inner sheath | [16 empty] | Not Required
[18 empty] | 19 |  |  | Inner sheath colour | [16 empty] | Not Applicable
[18 empty] | 20 |  |  | Lead sheath | [16 empty] | Not Applicable
[18 empty] | 21 |  |  | Bedding | [16 empty] | Not Applicable
[18 empty] | 22 |  |  | Bedding colour | [16 empty] | Not Applicable
[6 empty] | ARMOUR | [11 empty] | 23 |  |  | Armour / Type | [16 empty] | Un-Armoured
[6 empty] | OUTER SHEATH | [11 empty] | 24 |  |  | Outer sheath | [16 empty] | Zero Halogen Polymer
[18 empty] | 25 |  |  | Outer sheath colour | [16 empty] | Black
[18 empty] | 26 |  |  | Marking | [16 empty] | See 1.1
[6 empty] | OTHERS CABLE INFORMATION | [11 empty] | 27 |  |  | Bending radius | [16 empty] | 12 times the OD
[18 empty] | 28 |  |  | Voltage rating | [16 empty] | 0.6/1 kV
[18 empty] | 29 |  |  | Voltage Test | [16 empty] | 3500 V AC
[18 empty] | 30 |  |  | Mutual Capacitance | [16 empty] | /
[18 empty] | 31 |  |  | Inductance - Resistance - L/R Ratio | [16 empty] | /
[18 empty] | 32 |  |  | Sunlight resistance (UV Resistant) | [16 empty] | Yes
[18 empty] | 33 |  |  | Oil resistance | [16 empty] | Yes
[18 empty] | 34 |  |  | Protection against rodents | [16 empty] | Yes
[18 empty] | 35 |  |  | Flame retardant | [16 empty] | Yes, as per IEC 60332-1-2
[18 empty] | 36 |  |  | No fire propagation | [16 empty] | Yes, as per IEC 60332-3
[18 empty] | 37 |  |  | Fire Resistant | [16 empty] | Not Applicable
[18 empty] | 38 |  |  | Moisture barrier | [16 empty] | Not Applicable
[6 empty] | REFERENCE STD | [11 empty] | 39 |  |  | Main Applicable Standards | [16 empty] | IEC 60502
[6 empty] | TYPE OF CIRCUITS | [11 empty] | 40 |  |  | Intrinsically safe or non-intrinsically safe | [16 empty] | Non intrinsically safe
[6 empty] | NOTES | [11 empty] | 41
Document Number: 234249-00-CAB001
[34 empty] | Revision 01 | [6 empty] | Date: 02/07/2024 | [15 empty] | Page 9 of 14
[34 empty] | Document Type: | [14 empty] | SPECIFICATION
POWER & CONTROL CABLE TECHNICAL SPECIFICATION
Multicore I&C Cables for NOT I.S. circuits
[6 empty] | GENERAL | [12 empty] | 1 |  |  | Cable code | [19 empty] | After P.O.
[19 empty] | 2 |  |  | Cable description | [19 empty] | Multi-core cable – Overall Shield-Flame retardant - Low Smoke – Zero Halogen - Low Smoke - No fire propagation
[6 empty] | CONDUCTOR | [12 empty] | 3 |  |  | Reference Standard | [19 empty] | IEC 60228
[19 empty] | 4 |  |  | Type | [19 empty] | Stranded annealed high conductivity Copper conductor (Class 2)
[19 empty] | 5 |  |  | Formation | [19 empty] | 2C/4C/12C/15C/20C/30C x 1.5 mm² (OSH)
[6 empty] | CONDUCTOR INSULATION | [12 empty] | 6 |  |  | Reference Standard | [19 empty] | IEC 60227-1 & IEC 60502-1
[19 empty] | 7 |  |  | Type | [19 empty] | Zero Halogen Polymer
[19 empty] | 8 |  |  | Colours | [19 empty] | Core Insulation: White with Black Numbers
[6 empty] | FILLER | [12 empty] | 9 |  |  | Type | [19 empty] | Polypropylene yarn
[6 empty] | BINDER/WRAPPING | [12 empty] | 10 |  |  | Type | [19 empty] | Polyester Tape
[6 empty] | SHIELDS | [12 empty] | 11 |  |  | Overall shield | [19 empty] | Yes
[19 empty] | 12 |  |  | Shield type | [19 empty] | Al/Mylar (Polyester) tape overlapped approx. 25% with 100% coverage, with a minimum 7/0.25mm tinned copper drain wire.
[19 empty] | 13 |  |  | Ground PE yellow/green | [19 empty] | Not Required
[19 empty] | 14 |  |  | Drain wire | [19 empty] | Yes, 0.50 mm²
[6 empty] | INNER SHEATHS | [12 empty] | 15 |  |  | Reference Standard | [19 empty] | Not Applicable
[19 empty] | 16 |  |  | Inner sheath | [19 empty] | Not Required
[19 empty] | 17 |  |  | Inner sheath colour | [19 empty] | Not Applicable
[19 empty] | 18 |  |  | Lead sheath | [19 empty] | Not Applicable
[19 empty] | 19 |  |  | Bedding | [19 empty] | Not Applicable
[19 empty] | 20 |  |  | Bedding colour | [19 empty] | Not Applicable
[6 empty] | ARMOUR | [12 empty] | 21 |  |  | Armour / Type | [19 empty] | Un-Armoured
[6 empty] | OUTER SHEATH | [12 empty] | 22 |  |  | Outer sheath | [19 empty] | Zero Halogen Polymer
[19 empty] | 23 |  |  | Outer sheath colour | [19 empty] | Black
[19 empty] | 24 |  |  | Marking | [19 empty] | See 1.1
[6 empty] | OTHERS CABLE INFORMATION | [12 empty] | 25 |  |  | Bending radius | [19 empty] | 12 times the OD
[19 empty] | 26 |  |  | Voltage rating | [19 empty] | 0.6/1 kV
[19 empty] | 27 |  |  | Voltage Test | [19 empty] | 3500 V AC
[19 empty] | 28 |  |  | Mutual Capacitance | [19 empty] | /
[19 empty] | 29 |  |  | Inductance - Resistance - L/R Ratio | [19 empty] | /
[19 empty] | 30 |  |  | Sunlight resistance (UV Resistant) | [19 empty] | Yes
[19 empty] | 31 |  |  | Oil resistance | [19 empty] | Yes
[19 empty] | 32 |  |  | Protection against rodents | [19 empty] | Yes
[19 empty] | 33 |  |  | Flame retardant | [19 empty] | Yes, as per IEC 60332-1-2
[19 empty] | 34 |  |  | No fire propagation | [19 empty] | Yes, as per IEC 60332-3
[19 empty] | 35 |  |  | Fire Resistant | [19 empty] | Not Applicable
[19 empty] | 36 |  |  | Moisture barrier | [19 empty] | Not Applicable
[6 empty] | REFERENCE STD | [12 empty] | 37 |  |  | Main Applicable Standards | [19 empty] | IEC 60502
[6 empty] | TYPE OF CIRCUITS | [12 empty] | 38 |  |  | Intrinsically safe or non-intrinsically safe | [19 empty] | Non intrinsically safe
[6 empty] | NOTES | [12 empty] | 39
Document Number: 234249-00-CAB001
[34 empty] | Revision 01 | [6 empty] | Date: 02/07/2024 | [15 empty] | Page 10 of 14
[34 empty] | Document Type: | [14 empty] | SPECIFICATION
POWER & CONTROL CABLE TECHNICAL SPECIFICATION
Multicore cables - LV Power Cables (0.4kV and below) Without Ground (PE) Conductor
[7 empty] | GENERAL | [12 empty] | 1 |  |  | Cable code | [15 empty] | After P.O.
[20 empty] | 2 |  |  | Cable description | [15 empty] | Multicore cable - Flame retardant - Low Smoke – Zero Halogen - No fire propagation - Outdoor
[7 empty] | CONDUCTOR | [12 empty] | 3 |  |  | Reference Standard | [15 empty] | IEC 60228
[20 empty] | 4 |  |  | Type | [15 empty] | Stranded annealed high conductivity Copper conductor (Class 2).
[20 empty] | 5 |  |  | Size | [15 empty] | 2C / 3C / 4C / 2C (DC) x 2.5 / 4 / 6 / 10 mm²
[7 empty] | CONDUCTOR INSULATION | [12 empty] | 6 |  |  | Reference Standard | [15 empty] | IEC 60227-1 & IEC 60502-1
[20 empty] | 7 |  |  | Type | [15 empty] | XLPE
[20 empty] | 8 |  |  | Colours | [5 empty] | Two cores | [9 empty] | L: Yellow, N: Blue
[29 empty] | Three cores | [9 empty] | L1: Yellow, L2: Green, L3: Red
[29 empty] | Four cores | [9 empty] | L1: Yellow, L2: Green, L3: Red, N: Blue
[7 empty] | SHIELDS | [12 empty] | 9 |  |  | Overall shield | [15 empty] | Not Required
[20 empty] | 10 |  |  | Shield type | [15 empty] | Not Applicable
[20 empty] | 11 |  |  | Drain wire | [15 empty] | Not Applicable
[7 empty] | INNER SHEATHS | [12 empty] | 12 |  |  | Reference Standard | [15 empty] | Not Applicable
[20 empty] | 13 |  |  | Inner sheath | [15 empty] | Not Required
[20 empty] | 14 |  |  | Inner sheath colour | [15 empty] | Not Applicable
[20 empty] | 15 |  |  | Lead sheath | [15 empty] | Not Applicable
[20 empty] | 16 |  |  | Bedding | [15 empty] | Not Applicable
[20 empty] | 17 |  |  | Bedding colour | [15 empty] | Not Applicable
[7 empty] | ARMOUR | [12 empty] | 18 |  |  | Armour / Type | [15 empty] | Un-Armoured
[7 empty] | OUTER SHEATH | [12 empty] | 19 |  |  | Outer sheath | [15 empty] | Zero Halogen Polymer
[20 empty] | 20 |  |  | Outer sheath colour | [15 empty] | Black
[20 empty] | 21 |  |  | Marking | [15 empty] | See 1.1
[7 empty] | OTHERS CABLE INFORMATION | [12 empty] | 22 |  |  | Bending radius | [15 empty] | 12 times the OD
[20 empty] | 23 |  |  | Voltage rating | [15 empty] | 0.6/1 kV
[20 empty] | 24 |  |  | Voltage Test | [15 empty] | 3500 V AC
[20 empty] | 25 |  |  | Mutual Capacitance | [15 empty] | /
[20 empty] | 26 |  |  | Inductance - Resistance - L/R Ratio | [15 empty] | /
[20 empty] | 27 |  |  | Sunlight resistance (UV Resistant) | [15 empty] | Yes
[20 empty] | 28 |  |  | Oil resistance | [15 empty] | Yes
[20 empty] | 29 |  |  | Protection against rodents | [15 empty] | Yes
[20 empty] | 30 |  |  | Flame retardant | [15 empty] | Yes, as per IEC 60332-1-2
[20 empty] | 31 |  |  | No fire propagation | [15 empty] | Yes, as per IEC 60332-3
[20 empty] | 32 |  |  | Fire Resistant | [15 empty] | Not Applicable
[20 empty] | 33 |  |  | Moisture barrier | [15 empty] | Not Applicable
[7 empty] | REFERENCE STD | [12 empty] | 34 |  |  | Main Applicable Standards | [15 empty] | IEC 60502
[7 empty] | TYPE OF CIRCUITS | [12 empty] | 35 |  |  | Intrinsically safe or non-intrinsically safe | [15 empty] | Non intrinsically safe
[7 empty] | NOTES | [12 empty] | 36
Document Number: 234249-00-CAB001
[34 empty] | Revision 01 | [6 empty] | Date: 02/07/2024 | [15 empty] | Page 11 of 14
[34 empty] | Document Type: | [14 empty] | SPECIFICATION
POWER & CONTROL CABLE TECHNICAL SPECIFICATION
With Ground (PE) Conductor
[7 empty] | GENERAL | [12 empty] | 1 |  |  | Cable code | [15 empty] | After P.O.
[20 empty] | 2 |  |  | Cable description | [15 empty] | Multicore cable - Flame retardant - Low Smoke – Zero Halogen - No fire propagation - Outdoor
[7 empty] | CONDUCTOR | [12 empty] | 3 |  |  | Reference Standard | [15 empty] | IEC 60228
[20 empty] | 4 |  |  | Type | [15 empty] | Stranded annealed high conductivity Copper conductor (Class 2).
[20 empty] | 5 |  |  | Size | [15 empty] | 3G / 4G / 5G x 2.5 / 4 / 6 / 10 mm²
[7 empty] | CONDUCTOR INSULATION | [12 empty] | 6 |  |  | Reference Standard | [15 empty] | IEC 60227-1 & IEC 60502-1
[20 empty] | 7 |  |  | Type | [15 empty] | XLPE
[20 empty] | 8 | [11 empty] | Three cores | [6 empty] | L1: Yellow, N: Blue, Ground: Green/Yellow
[32 empty] | Four cores | [6 empty] | L1: Yellow, L2: Green, L3: Red Ground: Green/Yellow
[32 empty] | Five cores | [6 empty] | L1: Yellow, L2: Green, L3: Red, N: Blue, Ground: Green/Yellow
[7 empty] | SHIELDS | [12 empty] | 9 |  |  | Overall shield | [15 empty] | Not Required
[20 empty] | 10 |  |  | Shield type | [15 empty] | Not Applicable
[20 empty] | 11 |  |  | Drain wire | [15 empty] | Not Applicable
[7 empty] | INNER SHEATHS | [12 empty] | 12 |  |  | Reference Standard | [15 empty] | Not Applicable
[20 empty] | 13 |  |  | Inner sheath | [15 empty] | Not Required
[20 empty] | 14 |  |  | Inner sheath colour | [15 empty] | Not Applicable
[20 empty] | 15 |  |  | Lead sheath | [15 empty] | Not Applicable
[20 empty] | 16 |  |  | Bedding | [15 empty] | Not Applicable
[20 empty] | 17 |  |  | Bedding colour | [15 empty] | Not Applicable
[7 empty] | ARMOUR | [12 empty] | 18 |  |  | Armour / Type | [15 empty] | Un-Armoured
[7 empty] | OUTER SHEATH | [12 empty] | 19 |  |  | Outer sheath | [15 empty] | Zero Halogen Polymer
[20 empty] | 20 |  |  | Outer sheath colour | [15 empty] | Black
[20 empty] | 21 |  |  | Marking | [15 empty] | See 1.1
[7 empty] | OTHERS CABLE INFORMATION | [12 empty] | 22 |  |  | Bending radius | [15 empty] | 12 times the OD
[20 empty] | 23 |  |  | Voltage rating | [15 empty] | 0.6/1 kV
[20 empty] | 24 |  |  | Voltage Test | [15 empty] | 3500 V AC
[20 empty] | 25 |  |  | Mutual Capacitance | [15 empty] | /
[20 empty] | 26 |  |  | Inductance - Resistance - L/R Ratio | [15 empty] | /
[20 empty] | 27 |  |  | Sunlight resistance (UV Resistant) | [15 empty] | Yes
[20 empty] | 28 |  |  | Oil resistance | [15 empty] | Yes
[20 empty] | 29 |  |  | Protection against rodents | [15 empty] | Yes
[20 empty] | 30 |  |  | Flame retardant | [15 empty] | Yes, as per IEC 60332-1-2
[20 empty] | 31 |  |  | No fire propagation | [15 empty] | Yes, as per IEC 60332-3
[20 empty] | 32 |  |  | Fire Resistant | [15 empty] | Not Applicable
[20 empty] | 33 |  |  | Moisture barrier | [15 empty] | Not Applicable
[7 empty] | REFERENCE STD | [12 empty] | 34 |  |  | Main Applicable Standards | [15 empty] | IEC 60502
[7 empty] | TYPE OF CIRCUITS | [12 empty] | 35 |  |  | Intrinsically safe or non-intrinsically safe | [15 empty] | Non intrinsically safe
[7 empty] | NOTES | [12 empty] | 36
Document Number: 234249-00-CAB001
[34 empty] | Revision 01 | [6 empty] | Date: 02/07/2024 | [15 empty] | Page 12 of 14
[34 empty] | Document Type: | [14 empty] | SPECIFICATION
POWER & CONTROL CABLE TECHNICAL SPECIFICATION
Special Cables For AWL
[7 empty] | GENERAL | [12 empty] | 1 |  |  | Cable code | [15 empty] | After P.O.
[20 empty] | 2 |  |  | Cable description | [15 empty] | Multicore cable - Flame retardant - Low Smoke – Zero Halogen - No fire propagation - Outdoor
[7 empty] | CONDUCTOR | [12 empty] | 3 |  |  | Reference Standard | [15 empty] | IEC 60228
[20 empty] | 4 |  |  | Type | [15 empty] | Stranded annealed high conductivity Copper conductor (Class 2).
[20 empty] | 5 |  |  | Size | [15 empty] | 5C+PE x 2.5 mm²
[7 empty] | CONDUCTOR INSULATION | [12 empty] | 6 |  |  | Reference Standard | [15 empty] | IEC 60227-1 & IEC 60502-1
[20 empty] | 7 |  |  | Type | [15 empty] | Zero Halogen Polymer
[20 empty] | 8 |  |  | Colours | [15 empty] | Core Insulation: White with Black Numbers
[7 empty] | SHIELDS | [12 empty] | 9 |  |  | Overall shield | [15 empty] | Not Required
[20 empty] | 10 |  |  | Shield type | [15 empty] | Not Applicable
[20 empty] | 11 |  |  | Drain wire | [15 empty] | Not Applicable
[7 empty] | INNER SHEATHS | [12 empty] | 12 |  |  | Reference Standard | [15 empty] | Not Applicable
[20 empty] | 13 |  |  | Inner sheath | [15 empty] | Not Required
[20 empty] | 14 |  |  | Inner sheath colour | [15 empty] | Not Applicable
[20 empty] | 15 |  |  | Lead sheath | [15 empty] | Not Applicable
[20 empty] | 16 |  |  | Bedding | [15 empty] | Not Applicable
[20 empty] | 17 |  |  | Bedding colour | [15 empty] | Not Applicable
[7 empty] | ARMOUR | [12 empty] | 18 |  |  | Armour / Type | [15 empty] | Un-Armoured
[7 empty] | OUTER SHEATH | [12 empty] | 19 |  |  | Outer sheath | [15 empty] | Zero Halogen Polymer
[20 empty] | 20 |  |  | Outer sheath colour | [15 empty] | Black
[20 empty] | 21 |  |  | Marking | [15 empty] | See 1.1
[7 empty] | OTHERS CABLE INFORMATION | [12 empty] | 22 |  |  | Bending radius | [15 empty] | 12 times the OD
[20 empty] | 23 |  |  | Voltage rating | [15 empty] | 0.6/1 kV
[20 empty] | 24 |  |  | Voltage Test | [15 empty] | 3500 V AC
[20 empty] | 25 |  |  | Mutual Capacitance | [15 empty] | /
[20 empty] | 26 |  |  | Inductance - Resistance - L/R Ratio | [15 empty] | /
[20 empty] | 27 |  |  | Sunlight resistance (UV Resistant) | [15 empty] | Yes
[20 empty] | 28 |  |  | Oil resistance | [15 empty] | Yes
[20 empty] | 29 |  |  | Protection against rodents | [15 empty] | Yes
[20 empty] | 30 |  |  | Flame retardant | [15 empty] | Yes, as per IEC 60332-1-2
[20 empty] | 31 |  |  | No fire propagation | [15 empty] | Yes, as per IEC 60332-3
[20 empty] | 32 |  |  | Fire Resistant | [15 empty] | Not Applicable
[20 empty] | 33 |  |  | Moisture barrier | [15 empty] | Not Applicable
[7 empty] | REFERENCE STD | [12 empty] | 34 |  |  | Main Applicable Standards | [15 empty] | IEC 60502
[7 empty] | TYPE OF CIRCUITS | [12 empty] | 35 |  |  | Intrinsically safe or non-intrinsically safe | [15 empty] | Non intrinsically safe
[7 empty] | NOTES | [12 empty] | 36
Document Number: 234249-00-CAB001
[34 empty] | Revision 01 | [6 empty] | Date: 02/07/2024 | [15 empty] | Page 13 of 14
[34 empty] | Document Type: | [14 empty] | SPECIFICATION
POWER & CONTROL CABLE TECHNICAL SPECIFICATION
For CEMS
[6 empty] | GENERAL | [11 empty] | 1 |  |  | Cable code | [16 empty] | After P.O.
[18 empty] | 2 |  |  | Cable description | [16 empty] | Eight-pair cable-Twisted-Overall Shield-Flame Retardant-Zero Halogen-Low Smoke-No fire propagation
[6 empty] | CONDUCTOR | [11 empty] | 3 |  |  | Reference Standard | [16 empty] | IEC 60228
[18 empty] | 4 |  |  | Type | [16 empty] | Stranded annealed high conductivity Copper conductor
[18 empty] | 5 |  |  | Formation | [16 empty] | 8x(1Px0.75) mm²
[6 empty] | CONDUCTOR INSULATION | [11 empty] | 6 |  |  | Reference Standard | [16 empty] | IEC 60227-1 & IEC 60502-1
[18 empty] | 7 |  |  | Type | [16 empty] | Zero Halogen Polymer
[18 empty] | 8 |  |  | Colours | [16 empty] | Color coded ring marking e.g., as for LiHCH
[18 empty] | 9 |  |  | Number Coded | [16 empty] | Yes
[6 empty] | FILLER | [11 empty] | 10 |  |  | Type | [16 empty] | Polypropylene yarn
[6 empty] | BINDER/WRAPPING | [11 empty] | 11 |  |  | Type | [16 empty] | Polyester Tape
[6 empty] | SCREEN | [11 empty] | 12 |  |  | Type | [16 empty] | Braided Screen of Tinned Copper Wires
[6 empty] | SHIELDS | [11 empty] | 13 |  |  | Pair/triple/quads shield | [16 empty] | Not Required
[18 empty] | 14 |  |  | Overall shield | [16 empty] | Not Applicable
[18 empty] | 15 |  |  | Shield type | [16 empty] | Not Applicable
[18 empty] | 16 |  |  | Ground PE yellow/green | [16 empty] | Not Required
[18 empty] | 17 |  |  | Drain wire | [16 empty] | Not Applicable
[6 empty] | INNER SHEATHS | [11 empty] | 18 |  |  | Reference Standard | [16 empty] | Not Applicable
[18 empty] | 19 |  |  | Inner sheath | [16 empty] | Not Required
[18 empty] | 20 |  |  | Inner sheath colour | [16 empty] | Not Applicable
[18 empty] | 21 |  |  | Lead sheath | [16 empty] | Not Applicable
[18 empty] | 22 |  |  | Bedding | [16 empty] | Not Applicable
[18 empty] | 23 |  |  | Bedding colour | [16 empty] | Not Applicable
[6 empty] | ARMOUR | [11 empty] | 24 |  |  | Armour / Type | [16 empty] | Un-Armoured
[6 empty] | OUTER SHEATH | [11 empty] | 25 |  |  | Outer sheath | [16 empty] | Zero Halogen Polymer
[18 empty] | 26 |  |  | Outer sheath colour | [16 empty] | Black
[18 empty] | 27 |  |  | Marking | [16 empty] | See 1.1
[6 empty] | OTHERS CABLE INFORMATION | [11 empty] | 28 |  |  | Bending radius | [16 empty] | 12 times the OD
[18 empty] | 29 |  |  | Voltage rating | [16 empty] | 0.6/1 kV
[18 empty] | 30 |  |  | Voltage Test | [16 empty] | 3500 V AC
[18 empty] | 31 |  |  | Mutual Capacitance | [16 empty] | /
[18 empty] | 32 |  |  | Inductance - Resistance - L/R Ratio | [16 empty] | /
[18 empty] | 33 |  |  | Sunlight resistance (UV Resistant) | [16 empty] | Yes
[18 empty] | 34 |  |  | Oil resistance | [16 empty] | Yes
[18 empty] | 35 |  |  | Protection against rodents | [16 empty] | Yes
[18 empty] | 36 |  |  | Flame retardant | [16 empty] | Yes, as per IEC 60332-1-2
[18 empty] | 37 |  |  | No fire propagation | [16 empty] | Yes, as per IEC 60332-3
[18 empty] | 38 |  |  | Fire Resistant | [16 empty] | Not Applicable
[18 empty] | 39 |  |  | Moisture barrier | [16 empty] | Not Applicable
[6 empty] | REFERENCE STD | [11 empty] | 40 |  |  | Main Applicable Standards | [16 empty] | IEC 60502
[6 empty] | TYPE OF CIRCUITS | [11 empty] | 41 |  |  | Intrinsically safe or non-intrinsically safe | [16 empty] | Non intrinsically safe
[6 empty] | NOTES | [11 empty] | 42 |  |  | Operational capacitance approx. | [16 empty] | 80 nF/km
Document Number: 234249-00-CAB001
[34 empty] | Revision 01 | [6 empty] | Date: 02/07/2024 | [15 empty] | Page 14 of 14
[34 empty] | Document Type: | [14 empty] | SPECIFICATION
POWER & CONTROL CABLE TECHNICAL SPECIFICATION
CABLES USED FORMATIONS
Single-pair - I/C Cables for not I.S. circuits
[8 empty] | Formation | [12 empty] | Type of cable | [21 empty] | Overall – Intermediate Diameter
[8 empty] | 1x(1Px1.5) mm² (OSH) | [12 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [21 empty] | LATER
Multicore - I&C Cables for NOT I.S. circuits
[8 empty] | Formation | [15 empty] | Type of cable | [18 empty] | Overall – Intermediate Diameter
[8 empty] | 2C/4C/12C/15C/20C/30C x 1.5 mm² (OSH) | [15 empty] | CU/0H/OSH/FR/LS0H 0.6/1 kV | [18 empty] | LATER
Multicore cables - LV Power Cables (0.4kV and below)
[8 empty] | Formation (Without Ground (PE) Conductor) | [15 empty] | Type of cable | [18 empty] | Overall – Intermediate Diameter
[8 empty] | 2C / 3C / 4C / 2C (DC) x 2.5 / 4 / 6 / 10 mm² | [15 empty] | CU/XLPE/FR/0HLS 0.6/1 Kv | [18 empty] | LATER
[8 empty] | Formation (With Ground (PE) Conductor) | [15 empty] | Type of cable | [18 empty] | Overall – Intermediate Diameter
[8 empty] | 3G / 4G / 5G x 2.5 / 4 / 6 / 10 mm² | [15 empty] | CU/XLPE/FR/0HLS 0.6/1 kV | [18 empty] | LATER
Special Cables (AWL)
[8 empty] | Formation | [12 empty] | Type of cable | [21 empty] | Overall – Intermediate Diameter
[8 empty] | 5C+PE x 2.5 mm² | [12 empty] | CU/0H/FR/LS0H 0.6/1 kV | [21 empty] | LATER
Special Cables (CEMS)
[8 empty] | Formation | [12 empty] | Type of cable | [21 empty] | Overall – Intermediate Diameter
[8 empty] | 8x(1Px0.75) mm² | [12 empty] | CU/0H/FR/LS0H 0.6/1 kV | [21 empty] | LATER
Note: for lengths and types of conductors used please see document No. 234249-00-CAB531 POWER AND CONTROL CABLE LIST
Document Number: 234249-00-CAB502
[35 empty] | Revision 01 | [6 empty] | Date: 29/07/2024 | [15 empty] | Page 2 of 14
[35 empty] | Document Type: | [14 empty] | DATASHEET
POWER AND CONTROL CABLE - SUPP DATASHEET
POWER AND CONTROL CABLE - SUPP DATASHEET
REV |  |  |  |  | DATE | [9 empty] | DESCRIPTION | [29 empty] | SIGNATURES | [13 empty] | QAM
[45 empty] | Issued | [7 empty] | Approved | [5 empty] | Review
00 |  |  |  |  | 2024-07-29 | [9 empty] | FIRST ISSUE | [29 empty] | FLEI | [7 empty] | MB | [5 empty] | -
Data Sheet; Mod. 7.2.2 rev.2 del 14/03/18 Aggiornamento ISO 9001:2015
Cu Cl.2/XLPE/LSZH 0,6/1 kV 1G16 - GROUNDING CABLE - FRLS - Zero Halogen
Conductor
Insulation Outer sheath
TECHNICAL FEATURES
Conductor : Insulation : Cores colour code : Cores Assembling : Overall Wrapping: Drain wire : Overall Shield: RIPCORD : Bedding sheath : Bedding sheath color code: Armour : Outer sheath : Outer sheath color code: Outer printing (INKJET) : (EVERY 1000 mm) Outer diameter : Bending radius : Spark test : Conductors DC Resistance : Insulation Resistance : Applicable Standards Design Guidelines : ON COMPLETE CABLE Flame Retardant test : No fire propagation : Halogenidric Acid Emission : Smoke density : Temperature Range : ON INSULATION ON COMPLETE CABLE During Operation : During Installation : Note : | [14 empty] | STRANDED PLAIN high conductivity circular annealed copper wires IEC 60228 Class 2 XLPE, Nominal Thickness 0,7 mm Black Not Required Not required Not required Not required Not required Not required Not required Not required LSZH compound, ST8 quality to IEC 60502.1, Hydrocarbons/Oil/UV resistant with Rodent/Termite repellent, Nominal Thickness 1,4 mm Green/Yellow FLEI - Year of Manufacture - 0,6/1 kV - +90°C - 1G16 SQMM - CU/XLPE/LSZH - CE - Meter Marking (9,7 ± 10%) mm cable outer diameter x 8 (in fixed installation) 6,0 kV (on insulation) 10,0 kV (on sheath) IEC 60228 Class 2 ≥ 480 MW x Km (@ 20°C) IEC 60502.1 IEC 60332.1.2 IEC 60332.3 IEC 60754.1 (HCl ≤ 0,5%) IEC 61034.2 (LT ≥ 60%) (max +90°C) (max continuous operation temperature of conductors) (max +250°C) (max conductors temperature during short-circuit for maximum 5 seconds) (-35°C up to +90°C) (in fixed installation) (- 5°C up to +50°C) The cable is suitable for installation and use in Zone 1 & Zone 2 (IEC 60079-14) using only correct ATEX approved equipment or accessories
Office | [14 empty] | Date |  |  |  | Sign | [7 empty] | Rev. | [9 empty] | Date | [7 empty] | Sign
Drawn by : | [14 empty] | 2024-07-10 |  |  |  | Messa
Checked : | [14 empty] | 2024-07-10 |  |  |  | Spaccasassi
Approved : | [14 empty] | 2024-07-10 |  |  |  | Cucinotta
The data provided, lending assent for the treatment, will be used to the sense of the article 13 of of the Regulation (UE) 2016/679, also through outsiders, in order to allow the realization of the fulfilments informatives, administrative, commercial and accounting related to the contractual relationship. Integral copy of the informative could be requested at our offices.
All proprietary rights reserved according to law. This document shall be not reproduced without written permission. FLEI reserves the right to change characteristics and technical data of product shown at any time.
Data Sheet; Mod. 7.2.2 rev.2 del 14/03/18 Aggiornamento ISO 9001:2015
Cu Cl.2/XLPE/LSZH 0,6/1 kV 1G35 - GROUNDING CABLE - FRLS - Zero Halogen
Conductor
Insulation Outer sheath
TECHNICAL FEATURES
Conductor : Insulation : Cores colour code : Cores Assembling : Overall Wrapping: Drain wire : Overall Shield: RIPCORD : Bedding sheath : Bedding sheath color code: Armour : Outer sheath : Outer sheath color code: Outer printing (INKJET) : (EVERY 1000 mm) Outer diameter : Bending radius : Spark test : Conductors DC Resistance : Insulation Resistance : Applicable Standards Design Guidelines : ON COMPLETE CABLE Flame Retardant test : No fire propagation : Halogenidric Acid Emission : Smoke density : Temperature Range : ON INSULATION ON COMPLETE CABLE During Operation : During Installation : Note : | [14 empty] | STRANDED PLAIN COMPACTED high conductivity circular annealed copper wires IEC 60228 Class 2 XLPE, Nominal Thickness 0,9 mm Black Not Required Not required Not required Not required Not required Not required Not required Not required LSZH compound, ST8 quality to IEC 60502.1, Hydrocarbons/Oil/UV resistant with Rodent/Termite repellent, Nominal Thickness 1,4 mm Green/Yellow FLEI - Year of Manufacture - 0,6/1 kV - +90°C - 1G35 SQMM - CU/XLPE/LSZH - CE - Meter Marking (11,5 ± 10%) mm cable outer diameter x 8 (in fixed installation) 7,0 kV (on insulation) 10,0 kV (on sheath) IEC 60228 Class 2 ≥ 370 MW x Km (@ 20°C) IEC 60502.1 IEC 60332.1.2 IEC 60332.3 IEC 60754.1 (HCl ≤ 0,5%) IEC 61034.2 (LT ≥ 60%) (max +90°C) (max continuous operation temperature of conductors) (max +250°C) (max conductors temperature during short-circuit for maximum 5 seconds) (-35°C up to +90°C) (in fixed installation) (- 5°C up to +50°C) The cable is suitable for installation and use in Zone 1 & Zone 2 (IEC 60079-14) using only correct ATEX approved equipment or accessories
Office | [14 empty] | Date |  |  |  | Sign | [7 empty] | Rev. | [9 empty] | Date | [7 empty] | Sign
Drawn by : | [14 empty] | 2024-07-10 |  |  |  | Messa
Checked : | [14 empty] | 2024-07-10 |  |  |  | Spaccasassi
Approved : | [14 empty] | 2024-07-10 |  |  |  | Cucinotta
The data provided, lending assent for the treatment, will be used to the sense of the article 13 of of the Regulation (UE) 2016/679, also through outsiders, in order to allow the realization of the fulfilments informatives, administrative, commercial and accounting related to the contractual relationship. Integral copy of the informative could be requested at our offices.
All proprietary rights reserved according to law. This document shall be not reproduced without written permission. FLEI reserves the right to change characteristics and technical data of product shown at any time.
Data Sheet; Mod. 7.2.2 rev.2 del 14/03/18 Aggiornamento ISO 9001:2015
Cu Cl.2/XLPE/LSZH 0,6/1 kV 1G50 - GROUNDING CABLE - FRLS - Zero Halogen
Conductor
Insulation Outer sheath
TECHNICAL FEATURES
Conductor : Insulation : Cores colour code : Cores Assembling : Overall Wrapping: Drain wire : Overall Shield: RIPCORD : Bedding sheath : Bedding sheath color code: Armour : Outer sheath : Outer sheath color code: Outer printing (INKJET) : (EVERY 1000 mm) Outer diameter : Bending radius : Spark test : Conductors DC Resistance : Insulation Resistance : Applicable Standards Design Guidelines : ON COMPLETE CABLE Flame Retardant test : No fire propagation : Halogenidric Acid Emission : Smoke density : Temperature Range : ON INSULATION ON COMPLETE CABLE During Operation : During Installation : Note : | [14 empty] | STRANDED PLAIN COMPACTED high conductivity circular annealed copper wires IEC 60228 Class 2 XLPE, Nominal Thickness 1,0 mm Black Not Required Not required Not required Not required Not required Not required Not required Not required LSZH compound, ST8 quality to IEC 60502.1, Hydrocarbons/Oil/UV resistant with Rodent/Termite repellent, Nominal Thickness 1,4 mm Green/Yellow FLEI - Year of Manufacture - 0,6/1 kV - +90°C - 1G50 SQMM - CU/XLPE/LSZH - CE - Meter Marking (12,8 ± 10%) mm cable outer diameter x 8 (in fixed installation) 7,0 kV (on insulation) 10,0 kV (on sheath) IEC 60228 Class 2 ≥ 360 MW x Km (@ 20°C) IEC 60502.1 IEC 60332.1.2 IEC 60332.3 IEC 60754.1 (HCl ≤ 0,5%) IEC 61034.2 (LT ≥ 60%) (max +90°C) (max continuous operation temperature of conductors) (max +250°C) (max conductors temperature during short-circuit for maximum 5 seconds) (-35°C up to +90°C) (in fixed installation) (- 5°C up to +50°C) The cable is suitable for installation and use in Zone 1 & Zone 2 (IEC 60079-14) using only correct ATEX approved equipment or accessories
Office | [14 empty] | Date |  |  |  | Sign | [7 empty] | Rev. | [9 empty] | Date | [7 empty] | Sign
Drawn by : | [14 empty] | 2024-07-10 |  |  |  | Messa
Checked : | [14 empty] | 2024-07-10 |  |  |  | Spaccasassi
Approved : | [14 empty] | 2024-07-10 |  |  |  | Cucinotta
The data provided, lending assent for the treatment, will be used to the sense of the article 13 of of the Regulation (UE) 2016/679, also through outsiders, in order to allow the realization of the fulfilments informatives, administrative, commercial and accounting related to the contractual relationship. Integral copy of the informative could be requested at our offices.
All proprietary rights reserved according to law. This document shall be not reproduced without written permission. FLEI reserves the right to change characteristics and technical data of product shown at any time.
Data Sheet; Mod. 7.2.2 rev.2 del 14/03/18 Aggiornamento ISO 9001:2015
Cu Cl.2/XLPE/OSH/LSZH 0,6/1 kV 1X2X1,5 - I&C CABLE for NOT I.S. circuits - FRLS - Zero Halogen Ripcord Drain wire
Conductors Insulation Shield Wrapping Outer sheath
TECHNICAL FEATURES
Conductors : Insulation : Cores colour code : Pair Assembling : Overall Wrapping: Drain wire : Overall Shield: RIPCORD : Inner sheath : Inner sheath color code: Armour : Outer sheath : Outer sheath color code: Outer printing (INKJET) : (EVERY 1000 mm) Outer diameter : Bending radius : Voltage Test : Conductors DC Resistance : Insulation Resistance : Applicable Standards Design Guidelines : ON COMPLETE CABLE Flame Retardant test : No fire propagation : Halogenidric Acid Emission : Smoke density : Temperature Range : ON INSULATION ON COMPLETE CABLE During Operation : During Installation : Note : | [15 empty] | STRANDED PLAIN high conductivity circular annealed copper wires IEC 60228 Class 2 XLPE, Nominal Thickness 0,7 mm Black(+) / White(-) Cores twisted with optimal lay length with extruded or polypropylene yarns fillers by polyester tape helically wound STRANDED TINNED annealed copper drain wire, size 0,50 sqmm (7/0,30 mm), in continuous contact with the shield by Aluminium/polyester-mylar tape helically wound, minimum thickness 0,04mm (25% overlap, 100% coverage) Ripcord Not required Not required Not required LSZH compound, ST8 quality to IEC 60502.1, Hydrocarbons/Oil/UV resistant with Rodent/Termite repellent, Nominal Thickness 1,8 mm Black FLEI - Year of Manufacture - 0,6/1 kV - +90°C - 1X2X1,5 SQMM - CU/XLPE/OSH/LSZH - CE - Meter Marking (10,0 ± 10%) mm cable outer diameter x 12 (in fixed installation) 3500 V a.c. for 5' (Between Cores) / 2000 V a.c. for 1' (Between Cores - Shield) IEC 60228 Class 2 ≥ 1000 MΩ x Km (@ 20°C) Generally to IEC 60502.1 IEC 60332.1.2 IEC 60332.3 IEC 60754.1 (HCl ≤ 0,5%) IEC 61034.2 (LT ≥ 60%) (max +90°C) (max continuous operation temperature of conductors) (max +250°C) (max conductors temperature during short-circuit for maximum 5 seconds) (-35°C up to +90°C) (in fixed installation) (- 5°C up to +50°C) To meet the requirements of installation and use in Zone 1 & Zone 2 (IEC 60079-14) and "Gas & Vapour Tight" the cable must be provided with Penetrating Outer Sheath together with correct ATEX approved equipment or accessories.
Office | [15 empty] | Date |  |  |  |  | Sign | [8 empty] | Rev. | [7 empty] | Date | [9 empty] | Sign
Drawn by : | [15 empty] | 2024-07-10 |  |  |  |  | Messa
Checked : | [15 empty] | 2024-07-10 |  |  |  |  | Spaccasassi
Approved : | [15 empty] | 2024-07-10 |  |  |  |  | Cucinotta
The data provided, lending assent for the treatment, will be used to the sense of the article 13 of D.Lgs.196/03 (Privacy legislation), also through outsiders, in order to allow the realization of the fulfilments informatives, administrative, commercial and accounting related to the contractual relationship. Integral copy of the informative could be requested at our offices.
All proprietary rights reserved according to law. This document shall be not reproduced without written permission. FLEI reserves the right to change characteristics and technical data of product shown at any time.
Data Sheet; Mod. 7.2.2 rev.2 del 14/03/18 Aggiornamento ISO 9001:2015
GROUNDING BARE COPPER CONDUCTOR 1X50 Conductor
TECHNICAL FEATURES
Conductor : Insulation : Core colour code : Pair Assembling : Pair Wrapping: Drain wire : Pair Shield : Overall Wrapping: Drain wire : Overall Shield: Bedding sheath : Bedding sheath color code: Armour : Outer sheath : Outer sheath color code: Outer printing (Inkjet) : Outer diameter : Bending radius : | [17 empty] | STRANDED-COMPACTED plain/bare annealed copper wires Not Required Not Required Not Required Not Required Not Required Not Required Not Required Not Required Not Required Not Required Not Required Not Required Not Required Not Required Not required (8,0 ± 5%) mm cable outer diameter x 10 (in fixed installation) | [29 empty] | IEC 60228 Class 2
Conductor DC Resistance : | [17 empty] | IEC 60228 Class 2
Office | [17 empty] | Date | [6 empty] | Sign | [9 empty] | Rev. |  |  |  |  | Date | [7 empty] | Sign
Drawn by : | [17 empty] | 2024-07-10 | [6 empty] | Messa
Checked : | [17 empty] | 2024-07-10 | [6 empty] | Spaccasassi
Approved : | [17 empty] | 2024-07-10 | [6 empty] | Cucinotta
The data provided, lending assent for the treatment, will be used to the sense of the article 13 of of the Regulation (UE) 2016/679 (Privacy legislation), also through outsiders, in order to allow the realization of the fulfilments informatives, administrative, commercial and accounting related to the contractual relationship. Integral copy of the informative could be requested at our offices.
All proprietary rights reserved according to law. This document shall be not reproduced without written permission. FLEI reserves the right to change characteristics and technical data of product shown at any time.
Data Sheet; Mod. 7.2.2 rev.2 del 14/03/18 Aggiornamento ISO 9001:2015
Cu Cl.2/XLPE/LSZH 0,6/1 kV 3G2,5 - L.V. Power Cables (0.4kV and below) - FRLS - Zero Halogen Ripcord
Conductors Insulation Bedding Outer sheath
TECHNICAL FEATURES
Conductors : Insulation : Cores colour code : Cores Assembling : Overall Wrapping: Drain wire : Overall Shield: RIPCORD : Bedding sheath : Bedding sheath color code: Armour : Outer sheath : Outer sheath color code: Outer printing (INKJET) : (EVERY 1000 mm) Outer diameter : Bending radius : Voltage Test : Conductors DC Resistance : Insulation Resistance : Applicable Standards Design Guidelines : ON COMPLETE CABLE Flame Retardant test : No fire propagation : Halogenidric Acid Emission : Smoke density : Temperature Range : ON INSULATION ON COMPLETE CABLE During Operation : During Installation : Note : | [15 empty] | STRANDED PLAIN high conductivity circular annealed copper wires IEC 60228 Class 2 XLPE, Nominal Thickness 0,7 mm Yellow - Blue - Green/Yellow Cores twisted with optimal lay length Not required Not required Not required Ripcord LSZH commpound Black or Natural Not required LSZH compound, ST8 quality to IEC 60502.1, Hydrocarbons/Oil/UV resistant with Rodent/Termite repellent, Nominal Thickness 1,8 mm Black FLEI - Year of Manufacture - 0,6/1 kV - +90°C - 3G2,5 SQMM - CU/XLPE/LSZH - CE - Meter Marking (12,5 ± 10%) mm cable outer diameter x 12 (in fixed installation) 3500 V a.c. for 5' (Between Cores) IEC 60228 Class 2 ≥ 850 MΩ x Km (@ 20°C) IEC 60502.1 IEC 60332.1.2 IEC 60332.3 IEC 60754.1 (HCl ≤ 0,5%) IEC 61034.2 (LT ≥ 60%) (max +90°C) (max continuous operation temperature of conductors) (max +250°C) (max conductors temperature during short-circuit for maximum 5 seconds) (-35°C up to +90°C) (in fixed installation) (- 5°C up to +50°C) To meet the requirements of installation and use in Zone 1 & Zone 2 (IEC 60079-14) and "Gas & Vapour Tight" the cable must be provided with Penetrating Outer Sheath together with correct ATEX approved equipment or accessories.
Office | [15 empty] | Date |  |  |  |  | Sign | [8 empty] | Rev. | [7 empty] | Date | [9 empty] | Sign
Drawn by : | [15 empty] | 2024-07-10 |  |  |  |  | Messa
Checked : | [15 empty] | 2024-07-10 |  |  |  |  | Spaccasassi
Approved : | [15 empty] | 2024-07-10 |  |  |  |  | Cucinotta
The data provided, lending assent for the treatment, will be used to the sense of the article 13 of D.Lgs.196/03 (Privacy legislation), also through outsiders, in order to allow the realization of the fulfilments informatives, administrative, commercial and accounting related to the contractual relationship. Integral copy of the informative could be requested at our offices.
All proprietary rights reserved according to law. This document shall be not reproduced without written permission. FLEI reserves the right to change characteristics and technical data of product shown at any time.
Data Sheet; Mod. 7.2.2 rev.2 del 14/03/18 Aggiornamento ISO 9001:2015
Cu Cl.2/XLPE/LSZH 0,6/1 kV 3G4 - L.V. Power Cables (0.4kV and below) - FRLS - Zero Halogen Ripcord
Conductors Insulation Bedding Outer sheath
TECHNICAL FEATURES
Conductors : Insulation : Cores colour code : Cores Assembling : Overall Wrapping: Drain wire : Overall Shield: RIPCORD : Bedding sheath : Bedding sheath color code: Armour : Outer sheath : Outer sheath color code: Outer printing (INKJET) : (EVERY 1000 mm) Outer diameter : Bending radius : Voltage Test : Conductors DC Resistance : Insulation Resistance : Applicable Standards Design Guidelines : ON COMPLETE CABLE Flame Retardant test : No fire propagation : Halogenidric Acid Emission : Smoke density : Temperature Range : ON INSULATION ON COMPLETE CABLE During Operation : During Installation : Note : | [15 empty] | STRANDED PLAIN high conductivity circular annealed copper wires IEC 60228 Class 2 XLPE, Nominal Thickness 0,7 mm Yellow - Blue - Green/Yellow Cores twisted with optimal lay length Not required Not required Not required Ripcord LSZH commpound Black or Natural Not required LSZH compound, ST8 quality to IEC 60502.1, Hydrocarbons/Oil/UV resistant with Rodent/Termite repellent, Nominal Thickness 1,8 mm Black FLEI - Year of Manufacture - 0,6/1 kV - +90°C - 3G4 SQMM - CU/XLPE/LSZH - CE - Meter Marking (13,8 ± 10%) mm cable outer diameter x 12 (in fixed installation) 3500 V a.c. for 5' (Between Cores) IEC 60228 Class 2 ≥ 580 MΩ x Km (@ 20°C) IEC 60502.1 IEC 60332.1.2 IEC 60332.3 IEC 60754.1 (HCl ≤ 0,5%) IEC 61034.2 (LT ≥ 60%) (max +90°C) (max continuous operation temperature of conductors) (max +250°C) (max conductors temperature during short-circuit for maximum 5 seconds) (-35°C up to +90°C) (in fixed installation) (- 5°C up to +50°C) To meet the requirements of installation and use in Zone 1 & Zone 2 (IEC 60079-14) and "Gas & Vapour Tight" the cable must be provided with Penetrating Outer Sheath together with correct ATEX approved equipment or accessories.
Office | [15 empty] | Date |  |  |  |  | Sign | [8 empty] | Rev. | [7 empty] | Date | [9 empty] | Sign
Drawn by : | [15 empty] | 2024-07-10 |  |  |  |  | Messa
Checked : | [15 empty] | 2024-07-10 |  |  |  |  | Spaccasassi
Approved : | [15 empty] | 2024-07-10 |  |  |  |  | Cucinotta
The data provided, lending assent for the treatment, will be used to the sense of the article 13 of D.Lgs.196/03 (Privacy legislation), also through outsiders, in order to allow the realization of the fulfilments informatives, administrative, commercial and accounting related to the contractual relationship. Integral copy of the informative could be requested at our offices.
All proprietary rights reserved according to law. This document shall be not reproduced without written permission. FLEI reserves the right to change characteristics and technical data of product shown at any time.
Data Sheet; Mod. 7.2.2 rev.2 del 14/03/18 Aggiornamento ISO 9001:2015
Cu Cl.2/XLPE/LSZH 0,6/1 kV 4G4 - L.V. Power Cables (0.4kV and below) - FRLS - Zero Halogen Ripcord
Conductors Insulation Bedding Outer sheath
TECHNICAL FEATURES
Conductors : Insulation : Cores colour code : Cores Assembling : Overall Wrapping: Drain wire : Overall Shield: RIPCORD : Bedding sheath : Bedding sheath color code: Armour : Outer sheath : Outer sheath color code: Outer printing (INKJET) : (EVERY 1000 mm) Outer diameter : Bending radius : Voltage Test : Conductors DC Resistance : Insulation Resistance : Applicable Standards Design Guidelines : ON COMPLETE CABLE Flame Retardant test : No fire propagation : Halogenidric Acid Emission : Smoke density : Temperature Range : ON INSULATION ON COMPLETE CABLE During Operation : During Installation : Note : | [15 empty] | STRANDED PLAIN high conductivity circular annealed copper wires IEC 60228 Class 2 XLPE, Nominal Thickness 0,7 mm Yellow - Green - Red - Green/Yellow Cores twisted with optimal lay length with extruded filler Not required Not required Not required Ripcord LSZH commpound Black or Natural Not required LSZH compound, ST8 quality to IEC 60502.1, Hydrocarbons/Oil/UV resistant with Rodent/Termite repellent, Nominal Thickness 1,8 mm Black FLEI - Year of Manufacture - 0,6/1 kV - +90°C - 4G4 SQMM - CU/XLPE/LSZH - CE - Meter Marking (14,8 ± 10%) mm cable outer diameter x 12 (in fixed installation) 3500 V a.c. for 5' (Between Cores) IEC 60228 Class 2 ≥ 690 MΩ x Km (@ 20°C) IEC 60502.1 IEC 60332.1.2 IEC 60332.3 IEC 60754.1 (HCl ≤ 0,5%) IEC 61034.2 (LT ≥ 60%) (max +90°C) (max continuous operation temperature of conductors) (max +250°C) (max conductors temperature during short-circuit for maximum 5 seconds) (-35°C up to +90°C) (in fixed installation) (- 5°C up to +50°C) To meet the requirements of installation and use in Zone 1 & Zone 2 (IEC 60079-14) and "Gas & Vapour Tight" the cable must be provided with Penetrating Outer Sheath together with correct ATEX approved equipment or accessories.
Office | [15 empty] | Date |  |  |  |  | Sign | [8 empty] | Rev. | [7 empty] | Date | [9 empty] | Sign
Drawn by : | [15 empty] | 2024-07-10 |  |  |  |  | Messa
Checked : | [15 empty] | 2024-07-10 |  |  |  |  | Spaccasassi
Approved : | [15 empty] | 2024-07-10 |  |  |  |  | Cucinotta
The data provided, lending assent for the treatment, will be used to the sense of the article 13 of D.Lgs.196/03 (Privacy legislation), also through outsiders, in order to allow the realization of the fulfilments informatives, administrative, commercial and accounting related to the contractual relationship. Integral copy of the informative could be requested at our offices.
All proprietary rights reserved according to law. This document shall be not reproduced without written permission. FLEI reserves the right to change characteristics and technical data of product shown at any time.
Data Sheet; Mod. 7.2.2 rev.2 del 14/03/18 Aggiornamento ISO 9001:2015
Cu Cl.2/XLPE/LSZH 0,6/1 kV 5G6 - L.V. Power Cables (0.4kV and below) - FRLS - Zero Halogen Ripcord
Conductors Insulation Bedding Outer sheath
TECHNICAL FEATURES
Conductors : Insulation : Cores colour code : Cores Assembling : Overall Wrapping: Drain wire : Overall Shield: RIPCORD : Bedding sheath : Bedding sheath color code: Armour : Outer sheath : Outer sheath color code: Outer printing (INKJET) : (EVERY 1000 mm) Outer diameter : Bending radius : Voltage Test : Conductors DC Resistance : Insulation Resistance : Applicable Standards Design Guidelines : ON COMPLETE CABLE Flame Retardant test : No fire propagation : Halogenidric Acid Emission : Smoke density : Temperature Range : ON INSULATION ON COMPLETE CABLE During Operation : During Installation : Note : | [15 empty] | STRANDED PLAIN high conductivity circular annealed copper wires IEC 60228 Class 2 XLPE, Nominal Thickness 0,7 mm Yellow - Green - Red - Blue - Green/Yellow Cores twisted with optimal lay length with extruded filler Not required Not required Not required Ripcord LSZH commpound Black or Natural Not required LSZH compound, ST8 quality to IEC 60502.1, Hydrocarbons/Oil/UV resistant with Rodent/Termite repellent, Nominal Thickness 1,8 mm Black FLEI - Year of Manufacture - 0,6/1 kV - +90°C - 5G6 SQMM - CU/XLPE/LSZH - CE - Meter Marking (17,6 ± 10%) mm cable outer diameter x 12 (in fixed installation) 3500 V a.c. for 5' (Between Cores) IEC 60228 Class 2 ≥ 580 MΩ x Km (@ 20°C) IEC 60502.1 IEC 60332.1.2 IEC 60332.3 IEC 60754.1 (HCl ≤ 0,5%) IEC 61034.2 (LT ≥ 60%) (max +90°C) (max continuous operation temperature of conductors) (max +250°C) (max conductors temperature during short-circuit for maximum 5 seconds) (-35°C up to +90°C) (in fixed installation) (- 5°C up to +50°C) To meet the requirements of installation and use in Zone 1 & Zone 2 (IEC 60079-14) and "Gas & Vapour Tight" the cable must be provided with Penetrating Outer Sheath together with correct ATEX approved equipment or accessories.
Office | [15 empty] | Date |  |  |  |  | Sign | [8 empty] | Rev. | [7 empty] | Date | [9 empty] | Sign
Drawn by : | [15 empty] | 2024-07-10 |  |  |  |  | Messa
Checked : | [15 empty] | 2024-07-10 |  |  |  |  | Spaccasassi
Approved : | [15 empty] | 2024-07-10 |  |  |  |  | Cucinotta
The data provided, lending assent for the treatment, will be used to the sense of the article 13 of D.Lgs.196/03 (Privacy legislation), also through outsiders, in order to allow the realization of the fulfilments informatives, administrative, commercial and accounting related to the contractual relationship. Integral copy of the informative could be requested at our offices.
All proprietary rights reserved according to law. This document shall be not reproduced without written permission. FLEI reserves the right to change characteristics and technical data of product shown at any time.
Data Sheet; Mod. 7.2.2 rev.2 del 14/03/18 Aggiornamento ISO 9001:2015
Cu Cl.2/XLPE/LSZH 0,6/1 kV 5C+PE X 2,5 - FOR AWL - FRLS - Zero Halogen Ripcord
Conductors Insulation Bedding Wrapping Outer sheath
TECHNICAL FEATURES
Conductors : Insulation : Cores colour code : Cores Assembling : Overall Wrapping: Drain wire : Overall Shield: RIPCORD : Bedding sheath : Bedding sheath color code: Armour : Outer sheath : Outer sheath color code: Outer printing (INKJET) : (EVERY 1000 mm) Outer diameter : Bending radius : Voltage Test : Conductors DC Resistance : Insulation Resistance : Applicable Standards Design Guidelines : ON COMPLETE CABLE Flame Retardant test : No fire propagation : Halogenidric Acid Emission : Smoke density : Temperature Range : ON INSULATION ON COMPLETE CABLE During Operation : During Installation : Note : | [15 empty] | STRANDED PLAIN high conductivity circular annealed copper wires IEC 60228 Class 2 XLPE, Nominal Thickness 0,7 mm WHITE numbered (in Black) + Green/Yellow Cores twisted with optimal lay length with extruded filler by polyester tape helically wound Not required Not required Ripcord LSZH commpound Black or Natural Not required LSZH compound, ST8 quality to IEC 60502.1, Hydrocarbons/Oil/UV resistant with Rodent/Termite repellent, Nominal Thickness 1,8 mm Black FLEI - Year of Manufacture - 0,6/1 kV - +90°C - 5C+PEX2,5 SQMM - CU/XLPE/LSZH - CE - Meter Marking (15,5 ± 10%) mm cable outer diameter x 12 (in fixed installation) 3500 V a.c. for 5' (Between Cores) IEC 60228 Class 2 ≥ 850 MΩ x Km (@ 20°C) IEC 60502.1 IEC 60332.1.2 IEC 60332.3 IEC 60754.1 (HCl ≤ 0,5%) IEC 61034.2 (LT ≥ 60%) (max +90°C) (max continuous operation temperature of conductors) (max +250°C) (max conductors temperature during short-circuit for maximum 5 seconds) (-35°C up to +90°C) (in fixed installation) (- 5°C up to +50°C) To meet the requirements of installation and use in Zone 1 & Zone 2 (IEC 60079-14) and "Gas & Vapour Tight" the cable must be provided with Penetrating Outer Sheath together with correct ATEX approved equipment or accessories.
Office | [15 empty] | Date |  |  |  |  | Sign | [8 empty] | Rev. | [7 empty] | Date | [9 empty] | Sign
Drawn by : | [15 empty] | 2024-07-10 |  |  |  |  | Messa
Checked : | [15 empty] | 2024-07-10 |  |  |  |  | Spaccasassi
Approved : | [15 empty] | 2024-07-10 |  |  |  |  | Cucinotta
The data provided, lending assent for the treatment, will be used to the sense of the article 13 of D.Lgs.196/03 (Privacy legislation), also through outsiders, in order to allow the realization of the fulfilments informatives, administrative, commercial and accounting related to the contractual relationship. Integral copy of the informative could be requested at our offices.
All proprietary rights reserved according to law. This document shall be not reproduced without written permission. FLEI reserves the right to change characteristics and technical data of product shown at any time.
Data Sheet; Mod. 7.2.2 rev.2 del 14/03/18 Aggiornamento ISO 9001:2015
Cu Cl.2/XLPE/TCWB/LSZH 0,6/1 kV 8X2X0,75 - FOR CEMS - FRLS - Zero Halogen Ripcord
Conductors Insulation Shield Wrapping Outer sheath
TECHNICAL FEATURES
|  |  | Conductors : Insulation : Cores colour code : Pair Assembling : Pair Wrapping: Drain wire : Pair Shield: Cores Assembling : Overall Wrapping: Drain wire : Overall Shield: RIPCORD : Inner sheath : Inner sheath color code: Armour : Outer sheath : Outer sheath color code: Outer printing (INKJET) : (EVERY 1000 mm) Outer diameter : Bending radius : Voltage Test : Conductors DC Resistance : Insulation Resistance : Mutual Capacitance : Applicable Standards Design Guidelines : ON COMPLETE CABLE Flame Retardant test : No fire propagation : Halogenidric Acid Emission : Smoke density : Temperature Range : ON INSULATION ON COMPLETE CABLE During Operation : During Installation : Note : | [14 empty] | STRANDED PLAIN high conductivity circular annealed copper wires IEC 60228 Class 2 XLPE, Nominal Thickness 0,7 mm White / Black (each core NUMBERED for PAIR identification) Cores twisted in pairs Not required Not required Not required Pairs assembled together with optimal lay length with optional extruded or polypropylene yarns fillers by polyester tape helically wound Not required by Tinned copper Wire Braid (TCWB) Ripcord Not required Not required Not required LSZH compound, ST8 quality to IEC 60502.1, Hydrocarbons/Oil/UV resistant with Rodent/Termite repellent, Nominal Thickness 1,8 mm Black FLEI - Year of Manufacture - 0,6/1 kV - +90°C - 8X2X0,75 SQMM - CU/XLPE/TCWB/LSZH - CE - Meter Marking (18,0 ± 10%) mm cable outer diameter x 12 (in fixed installation) 3500 V a.c. for 5' (Between Cores) / 2000 V a.c. for 1' (Between Cores - Shield) IEC 60228 Class 2 ≥ 1000 MΩ x Km (@ 20°C) ≤ 80 nF/km (between cores) Generally to IEC 60502.1 IEC 60332.1.2 IEC 60332.3 IEC 60754.1 (HCl ≤ 0,5%) IEC 61034.2 (LT ≥ 60%) (max +90°C) (max continuous operation temperature of conductors) (max +250°C) (max conductors temperature during short-circuit for maximum 5 seconds) (-35°C up to +90°C) (in fixed installation) (- 5°C up to +50°C) To meet the requirements of installation and use in Zone 1 & Zone 2 (IEC 60079-14) and "Gas & Vapour Tight" the cable must be provided with Penetrating Outer Sheath together with correct ATEX approved equipment or accessories.
|  |  | Office | [14 empty] | Date | [5 empty] | Sign | [7 empty] | Rev. | [5 empty] | Date | [9 empty] | Sign
|  |  | Drawn by : | [14 empty] | 2024-06-10 | [5 empty] | Messa
|  |  | Checked : | [14 empty] | 2024-06-10 | [5 empty] | Spaccasassi
|  |  | Approved : | [14 empty] | 2024-06-10 | [5 empty] | Cucinotta
The data provided, lending assent for the treatment, will be used to the sense of the article 13 of D.Lgs.196/03 (Privacy legislation), also through outsiders, in order to allow the realization of the fulfilments informatives, administrative, commercial and accounting related to the contractual relationship. Integral copy of the informative could be requested at our offices.
All proprietary rights reserved according to law. This document shall be not reproduced without written permission. FLEI reserves the right to change characteristics and technical data of product shown at any time.
Data Sheet; Mod. 7.2.2 rev.2 del 14/03/18 Aggiornamento ISO 9001:2015
Cu Cl.2/XLPE/OSH/LSZH 0,6/1 kV 15X1,5 - I&C CABLE for NOT I.S. circuits - FRLS - Zero Halogen Ripcord Drain wire
Conductors Insulation Shield Wrapping Outer sheath
TECHNICAL FEATURES
Conductors : Insulation : Cores colour code : Cores Assembling : Overall Wrapping: Drain wire : Overall Shield: RIPCORD : Inner sheath : Inner sheath color code: Armour : Outer sheath : Outer sheath color code: Outer printing (INKJET) : (EVERY 1000 mm) Outer diameter : Bending radius : Voltage Test : Conductors DC Resistance : Insulation Resistance : Applicable Standards Design Guidelines : ON COMPLETE CABLE Flame Retardant test : No fire propagation : Halogenidric Acid Emission : Smoke density : Temperature Range : ON INSULATION ON COMPLETE CABLE During Operation : During Installation : Note : | [15 empty] | STRANDED PLAIN high conductivity circular annealed copper wires IEC 60228 Class 2 XLPE, Nominal Thickness 0,7 mm WHITE numbered (in Black) Cores twisted with optimal lay length with extruded or polypropylene yarns fillers by polyester tape helically wound STRANDED TINNED annealed copper drain wire, size 0,50 sqmm (7/0,30 mm), in continuous contact with the shield by Aluminium/polyester-mylar tape helically wound, minimum thickness 0,04mm (25% overlap, 100% coverage) Ripcord Not required Not required Not required LSZH compound, ST8 quality to IEC 60502.1, Hydrocarbons/Oil/UV resistant with Rodent/Termite repellent, Nominal Thickness 1,8 mm Black FLEI - Year of Manufacture - 0,6/1 kV - +90°C - 15X1,5 SQMM - CU/XLPE/OSH/LSZH - CE - Meter Marking (18,2 ± 10%) mm cable outer diameter x 12 (in fixed installation) 3500 V a.c. for 5' (Between Cores) / 2000 V a.c. for 1' (Between Cores - Shield) IEC 60228 Class 2 ≥ 1000 MΩ x Km (@ 20°C) Generally to IEC 60502.1 IEC 60332.1.2 IEC 60332.3 IEC 60754.1 (HCl ≤ 0,5%) IEC 61034.2 (LT ≥ 60%) (max +90°C) (max continuous operation temperature of conductors) (max +250°C) (max conductors temperature during short-circuit for maximum 5 seconds) (-35°C up to +90°C) (in fixed installation) (- 5°C up to +50°C) To meet the requirements of installation and use in Zone 1 & Zone 2 (IEC 60079-14) and "Gas & Vapour Tight" the cable must be provided with Penetrating Outer Sheath together with correct ATEX approved equipment or accessories.
Office | [15 empty] | Date |  |  |  |  | Sign | [8 empty] | Rev. | [7 empty] | Date | [9 empty] | Sign
Drawn by : | [15 empty] | 2024-07-10 |  |  |  |  | Messa
Checked : | [15 empty] | 2024-07-10 |  |  |  |  | Spaccasassi
Approved : | [15 empty] | 2024-07-10 |  |  |  |  | Cucinotta
The data provided, lending assent for the treatment, will be used to the sense of the article 13 of D.Lgs.196/03 (Privacy legislation), also through outsiders, in order to allow the realization of the fulfilments informatives, administrative, commercial and accounting related to the contractual relationship. Integral copy of the informative could be requested at our offices.
All proprietary rights reserved according to law. This document shall be not reproduced without written permission. FLEI reserves the right to change characteristics and technical data of product shown at any time.